Scope of Work for Dragging, transportation, unloading with in sub-station premises and erection of existing 500 MVA, 400/220 kV Toshiba make transformer as ICT-IV (S/N: 90654C01 M/Y:2022) at Prayagraj SS.

The scope of work includes the following:

- 400/220/33 kV, 500 MVA 3-Phase Transformer (ICT) is placed in Prayagraj SS on switchyard RCC road without wheels and oil. Radiator bank is in dismantled/ not erected state.

- The scope of work includes loading of 400/220/33 kV, 500 MVA Transformer with filled dry air pressure of 0.5-0.5 psi.

- The scope of work also includes transportation of Main Tank from RCC road to plinth location in switchyard and unloading at plinth.

- The Transport dimension of main tank is 11550 mm x 5000 mm x 4600 mm . Transport mass of ICT (without Oil & With Dry Air) 260000 KGS. (OGA drawing is attached for reference)

- Contractor shall arrange suitable material handling and transport equipment as may be necessary including labor, packing materials, cranes, trucks, trailers etc. and the T&P required for above works. The main tank shall be filled with dry air by POWERGRID before transportation however dry air cylinders which are available at site need to be top up before and during transportation to maintain the required pressure (shall be in the scope of party). The impact recorder (if required) shall be arranged by POWERGRID.

- Contractor shall make all arrangement of adequate size and capacity of cranes etc. for loading and unloading of materials and will ensure that overloading in vehicles in not done.

- The contractor shall carry out the route survey along with the transporter and finalize the detail methodology for transportation of autotransformer and based on route survey; any modification/ extension/ improvement to existing road, bridges, culverts etc. if required, shall be in the scope of the contractor.

- If any damages to drainage, culverts etc. occurred due to dragging of ICT at source point or destination, the same shall be repaired by the contractor.

- All the equipment and materials to be transported shall be kept insured by the contractor against any loss, damage, accident, pilferage, theft, fire etc. from the point of commencement of loading up to the time of taking over by the owner POWERGRID. The premium charges for above need to be quoted in BOQ. Approx value of ICT with oil and accessories: 14.96 Crore.

- The Contractor shall take the policy in the joint names of Employer and the Contractor. The policy shall indicate the Employer as the beneficiary. However, if the Contractor is having an open policy for its line of business, it should obtain an endorsement of the open cover policy from the insurance company indicating that the dispatches against this Contract are duly covered under its open policy and include the name of the Employer as jointly Insured in the endorsements to the open policy.

- The Contractor shall arrange necessary surveys and loading/settling of insurance claims for consignments landed in damaged conditions. Necessary surveys for the damaged materials/packing before repacking and dispatch.

- Proper coordination for smooth transportation and dispatch of ICT is essential.

- Contractor shall be fully responsible for the safe handling of materials and shall indemnify and absolve owner of any consequences thereof by way of damage/loss of cargo, accidents, damages to vehicles and handling equipment either owned or hired by the contractor, public property as well as injuries or otherwise to the personnel under the contractor’s command or the public.

- Contractor shall properly maintain all registers and records in the prescribed manner as required by the regulations of the various authorities concerned and shall indemnify the consignee and the owner from any consequences due to any inaccurate and faulty documentation on contractor part.

- All the statutory requirement such as electrical license, Workman compensation policy, Erection all risk policy, Transit/Marine Cargo insurance (as applicable) etc. shall be in the scope of contractor/Bidder.

- The other related works which are not specifically mentioned above and required for completion of the works shall be in the scope of contractor.

- Contractor shall take proper supervision of entire operation till final dispatch/receipt of materials.

- Oil filtration plant, Dry air plant and temporary electrical connection shall be arranged by POWERGRID, free of cost.

- Erection of ICT at Prayagraj S/s: The erection of ICT at Prayagraj S/s is also in the scope of vendor. The main activities to be carried out for erection shall be as below:

- Removal of impact recorder under the supervision of OEM representative, followed by erection of accessories including HV, IV, LV & Neutral bushings, Conservator, Tank to conservator pipes, Buchholz & PNRV Relay, equalizer pipes, PRV, Turret, Radiator along with support structures and other accessories etc.

- Erection of the ICT BPI, 400 KV Connection with Jumper/Aluminum with Bushings & LA and Neutral Jumper/Aluminum Tube is in the scope of contactor.

- The scope of work also includes commissioning of the ICT as per POWERGRID norms such as activities related to dry-out with Vacuum Cycles, leakage identification and arresting, processing and filling of insulating oil in main tank and carrying out the Hot Oil Circulation (HOC) of the insulating oil inside Main Tank. Total quantity of Insulating oil is 114 KL in main tank.

- T&P such as dew point meter, online ppm kit, McLeod Guage, appropriate sling for lifting of bushing etc. shall be in the scope of contractor.

- Testing of the processed oil before filling & after HOC shall be in the scope of POWERGRID.

- Erection of all the auxiliary items such as IMB, ODS, FOTS, DGA etc. is in the scope of contactor. Cable termination at IMB, CMB, mechanical protection devices etc. will be in the scope of M/s POWERGRID.

- Contractor shall arrange suitable material for handling of equipment as may be necessary including labor, cranes, hydra etc. and the T&P required for above works.

- Contractor shall make all arrangement of adequate size and capacity of cranes/ hydra etc. for erection of the bushings and accessories such as conservator, radiator etc.

- Electrical Testing of the ICT (after the final settling of the Main tank post HOC) along with the Kits required for the same shall be in the scope of POWERGRID.