## Indicative BoQ
Indicative BOQ for reference purpose only- Dismantling, Dragging & Commissioning of Spare 160MVA ICT in place of ICT-3 (by carrying out the dismantling & shifting of ICT-3 to Spare ICT Location) at Sitarganj Substation NR-III for making the provision of auxiliary supply from ICT tertiary.
Sr. No. | Description | Unit | Qty
1 | Draining out of approx 50kL Insulating Oil from 220/132kV Bharat Bijlee Make ICT-3 and storage of the Insulating Oil in Oil Storage Tank at Site and carrying out the filtration and processing of the Oil to achieve required oil parameters. Note:- Oil Storage Tank and Oil Filtration machine shall be in the scope of the contractor. | Lot | 1
2 | Dismantling of HV, IV, Neutral Bushings and Conservator etc. of 220/132kV 100MVA Bharat Bijlee Make ICT-3 including dismantling of the jumper connections and Surge arresters and all ICT accessories such as the radiators, cooling fans, cooler pipes, firefighting system & pipes, ICT MB etc. (As ICT-3 is currently in service at its location) and further fixing of dummy plates on all required points after dismantling of accessories followed by the flling of Positive dry air upto 0.2-0.5 psi. Note:- Crane/Hydra or any other T&P and Manpower required for the dismantling shall be in the scope of the contractor. | Lot | 1
3 | Dragging & Shifting of 100MVA ICT-3 main tank from existing plinth to temporary holding location near Spare ICT foundation and storage of the same on Wooden Slipper platform for tentative duration of 02 months (during which ICT-3 foudation modification work shall be carried out under seperate contract) Note:- Material (such as wooden Slippers required for the dragging & temporary holding), T&P and Manpower shall be in the Scope of the contractor. | Mtr | 90
4 | Draining out of approx 62kL Insulating Oil from 220/132/33kV TOSHIBA Make 160MVA Spare ICT and storage of the Insulating Oil in Oil Storage Tank at Site and carrying out the filtration and processing of the Oil to achieve required oil parameters. Note:- Oil Storage Tank and Oil Filtration machine shall be in the scope of the contractor. | Lot | 1
5 | Dismantling of HV, IV, Tertiary Bushing, Neutral Bushings and Conservator etc. of 220/132/33kV TOSHIBA Make 160MVA Spare ICT including dismantling all its accessories such cooling fans, cooler pipes, ICT MB etc. (As Spare 160MVA ICT is in completely erected condition at Spare ICT foundation) and further fixing of dummy plates on all required points after dismantling of accessories followed by the flling of Positive dry air upto 0.2-0.5 psi. Note:- Crane/Hydra or any other T&P and Manpower required for the dismantling shall be in the scope of the contractor. | Lot | 1
6 | Dragging & Shifting of TOSHIBA Make 160MVA Spare ICT from Spare foundation to ICT-3 location for Its commissioning as ICT-3. Note:- This dragging and shifting is to be carried out after the removal of existing ICT-3 and its shifting to temporary hoding location as per BoQ Line Item 03 & further modification of the ICT-3 foundation in line with the 160MVA ICT dimensions, civil works for which shall be under POWERGRID Scope. Material (such as Wooden Slippers), T&P and Manpower required for the dragging and shifting shall be in the Scope of the contractor. | Mtr | 65
7 | Erection and Commissioning of 160MVA TOSHIBA Make ICT as 220/132/33kV ICT-3 with the erection of HV, IV, Tertiary Bushing, Neutral Bushings, Surge Arresters and Conservator etc. along with installation of all its accessories such radiators, cooling fans, fire fighting system and pipes, cooler pipes, ICT MB etc. (after the removal of the dummy plates and under positive dry air supply into the main tank to avoid moisture ingress during erection). Note:- Crane/Hydra or any other T&P and Manpower required for the erection and commissioning shall be in the scope of the contractor. New Gaskets required for the erection & commissioning of ICT shall be in the scope of POWERGRID | Lot | 1
8 | Filling and Hot Oil Circulation of approx 62kL Insulating Oil of 220/132/33kV TOSHIBA Make 160MVA ICT in main tank (after the carrying out the post erection Vaccuum & Dry out Cycle of the ICT) to achieve the required oil parameters and carrying out the jumper connections of the ICT. Note:- Dry Air Plant, Vacuum Plant & Oil Filtration machine shall be in the scope of the contractor. | Lot | 1
9 | Dragging & Shifting of ICT-3 main tank from temporary holding location to Spare ICT Foundation for its final commissioning as Cold RPC Spare. Note:- Material (such as wooden Slippers required for the dragging & temporary holding), T&P and Manpower shall be in the Scope of the contractor. | Mtr | 45
10 | Erection and Commissioning of 100MVA Bharat Bijlee Make ICT as Cold RPC Spare at Spare ICT foundation with the erection of HV, IV, Neutral Bushings and Conservator etc. along with installation of all its accessories (after the removal of the dummy plates and under positive dry air supply into the main tank to avoid moisture ingress during erection). Note:- Crane/Hydra or any other T&P and Manpower required for the erection and commissioning shall be in the scope of the contractor. New Gaskets required for the erection & commissioning of ICT shall be in the scope of POWERGRID | Lot | 1
11 | Filling and Hot Oil Circulation of approx 50kL Insulating Oil of 220/132kV Bharat Bijlee Make 100MVA ICT in main tank (after the carrying out the post erection Vaccuum & Dry out Cycle of the ICT) to achieve the required oil parameters. Note:- Dry Air Plant, Vacuum Plant & Oil Filtration machine shall be in the scope of the contractor. | Lot | 1
12 | Sub Total for the Services (Item 01 to 11)
Execution Schedule | Shall be executed in 04 Months from the date of issuance of LOA (02 Months time required for the modification works of existing foundation of ICT-3 after the dismantling and dragging of Bharat Bijlee Make ICT