Amendment – II to the Bidding Documents for Supply, Installation & Commissioning of Spring-Spring Operated 3-Ph, 145kV, Circuit Breakers with SF6 free alternative medium including dismantling of existing 145kV CBs at Imphal S/s.

Spec. No. CC/NT/W-MISC/DOM/A06/24/10523

| Sl. No. | Clause Reference | Existing Provision | Amended Provision |
| --- | --- | --- | --- |
| 1. | Section- Switchgear GCB (for 145kV) Rev.00, Clause 4.1.1 | The gap between the open contacts shall be such that it can withstand at least the rated phase to ground voltage for 8 hours at zero gauge pressure of SF6 free alternative medium due to the leakage. The breaker should be able to withstand all dielectric stresses imposed on it in open condition at lock out pressure continuously (i.e. 2 p.u. across the breaker continuously, for validation of which a power frequency dielectric with stand test conducted for a duration of at least 15 minutes is acceptable). | Deleted |
| 2. | Section- Switchgear GCB (for 145kV) Rev.00, Clause 15.2 (iv) | Test to demonstrate the Power Frequency withstand capability of breaker in open condition at Zero Gauge pressure and at lockout pressure (Ref. Clause 4.1.1). | Deleted |