SECTION-V

Technical Specification and Special Conditions of Contract

Supply, installation, Testing and Commissioning of street light on the side of defence road in front of PAL Complex, Manesar, Gurugram

SPEC. NO.: CC/NT/W-MISC/DOM/A15/24/17276

(RFX No : 5002004161)

|  | पावर ग्रिड कार्पोरेशन आफ इन्डिया लिमिटेड (भारत सरकार का उद्यम) Power Grid Corporation of India Limited (A Government of India Enterprises) |
| --- | --- |

(These documents are meant for the exclusive purpose of bidding against this Specification and shall not be transferred, reproduced or otherwise used for purposes other than that for which it is specifically issued.)

- SCOPE OF WORK:

The scope involves, Supply, installation, Testing and Commissioning of streetlight on the side of defence road in front of PAL Complex, Manesar, Gurugram” The above scope of work is indicative, and the detailed scope of work is given in the Technical Specification & Scope of work of the Bidding Documents.

- Technical Specification:

- Technical Specifications for  Street light

- The work is to be carried out strictly as per Bill of Quantity.

- The contract price includes the cost of materials, manpower, loading, unloading, transportation to the sites and tools, plants etc. including cost of site arrangements, overheads etc. and exclusive of all applicable taxes and duties.

- Water shall be provided free of cost however, its distribution, as per work requirement shall be arranged by contractor at their own cost. POWERGRID will not entertain any claim, nor does it relieve the contractor of their responsibilities regarding work quality whatsoever in this regard.

- The contractor/agency must do all the job, required materials, tools and tackles, which is not specifically mentioned or specified in the detailed BOQ items, but is required for proper completion of BOQ items, then same shall be provided/carried out by the contractor without any additional cost to POWERGRID.

- The contractor/agency shall make all necessary arrangement for proper safety of his workmen during execution of work including deployment of proper tools & tackles and personnel protective equipment (PPE). Contractors shall ensure the safety of their personnel during execution of the work. Power Grid shall not entertain any type of claim regarding injury or accident with the staff of the contractor.

- Normally the offer should be as per Technical Specification without any deviation. But any deviation felt necessary to improve performance, efficiency and utility of equipment must be mentioned with reasons duly supported by documentary evidence and advantages of such deviation.

- Any defects pointed out during the work by the POWERGRID, shall be corrected or attended by the contractor at his own cost.

- If any damage is caused inadvertently to any other utility shall be the sole responsibility of Contractor and no any extra claim shall be raised by him.

- Street Light Pole:-

- Height of Pole: - 07 meter

- Single arm length: - 1.5 meter

- Poles made up material: - Galvanized steel with mass of zinc coating 360Gms per Sq. meter.

- Shape of pole – Octagonal tubular shape

- Wall thickness of pole structure shall be in between 4.5mm to 3.3mm.

- Pole structure shall have finials, base plates, taper plug, GI arm (length 1.5 meter) for holding LED fixture, foundation bolt etc

- The inbuilt junction box at suitable height from the base shall be provided. The junction box shall have SS rail, Single pole 10A MCB, terminal block - suitable for 4 core 10 Sq mm Aluminium armoured cable connection, suitable size lugs etc. required for completion of this work.

- The pole has suitable point for cable entry and exist.

- The pole shall be designated 410SP-5 as per IS 2713/80 Part 2 with amdt. no 1

- Tubes for manufacturing poles shall conform to Grade YST 240 as per IS:1161/1998

- Pole shall be Swaged (SP) with departmental logo as prescribed by POWERGRID on each pole

- Vendor shall submit manufacture test report.

- 60 W LED light fixture: -

| Sl. No | Specification | Required parameters |
| --- | --- | --- |
| 1 | Power Rating | 60 Watt |
| 2 | Luminaire System Efficacy (Lumen/watt) | >/= 100 Lm/Watt (6000 Lumen) |
| 3 | Ingress Protection (IP Rating) as per IS:10322 (Part 1):1982 latest | IP66 |
| 4 | Input operating Voltage range and frequency | 90 to 300 Volts AC at 50 Hz+/-2 |
| 5 | Operating temperature range | -10 deg C to +50 deg C |
| 6 | The luminaire shall be protected against surges and transients (Internal) | >/=4KV(Kilo Volt) |
| 7 | Number of electronic control gear (power supplies) | 01 no’s |
| 8 | Rated voltage | 240 V AC 50 Hz |
| 9 | Automatic Higher Cut off voltage | Above 300 volt |
| 10 | LED chip Efficacy | ≥130 Lm/Watt |
| 11 | Color temperature | 6500K |
| 12 | Working life for LED | Minimum 50,000 burning hours as per LM-80 and LM 21 |
| 13 | Colour Rendering Index(CRI | ≥70 |
| 14 | LED Beam Angle | 120 |
| 15 | Optic lens material (UV stabilized) | Poly carbonate lens |
| 16 | Heat sink | Die-cast aluminum along with sufficient heat sink fins to dissipate heat effectively |
| 17 | Junction / Soldering point temperature | shall not exceed 85 deg. Celsius |
| 18 | Capacitor rated temperature | 105 deg. celsius or better |
| 19 | Operating Humidity Range | 10 % to 95% RH |
| 20 | Insulation resistance | >100 M Ohm |
| 21 | Gasket | Extruded silicon provided in the lantern body to ensure a weatherproof seal between the UV Glass cover and the metal housing to exclude the entry of the dust, water, insects etc., |
| 22 | Toughened transparent glass cover thickness | >/=4 mm |
| 23 | Light Source | Surface mounted device (SMD) LED Chip as per LM 80/IS16106 |
| 24 | PCB | FR4 grade minimum thickness 0.8 mm to 1.0 mm thick or more |
| 25 | Warranty | 2 years |

ii)  The LED fixture shall comply IS 10322 / part 5/section3/2012latest, IS: 16107 (Part 2/Sec 1):2012 latest and Photo biological safety of LEDs used shall be as per IS:16108/2012.

ii)  Types of LED Luminaire as per the IS: 16107(Part-2/ Sec.-1)/2012 and Types of LED Modules as per the IS:IS: 16103(Part2)/2012.

iii)The LED fixture shall comply with short circuit Protection, overload protection, overvoltage protection, reverse polarity.

iv) The Luminaires casing/housing (single piece housing) shall be   pressure die cast aluminum alloy with higher thermal conductivity and luminaire body must be corrosion resistant powder coated.

v) The Manufactures Name, model number, serial number, date of manufacture (month-year), and lot number on the aluminum die cast body " Engraved/Embossed. The operation characteristics voltage and power are marked inside of each LED luminaire unit.

vi) The LED Luminaire for road and street lighting shall comply with Compulsory Registration (CRS) of BIS for safety as per IS 10322 (Part 5/Section 3): 2012 as applicable on date.

vii) Vendor shall submit documentation for meeting above mention specifications.

4 core 10 Sq.mm LT Cable: -

| Sl. No | Specification | Required parameters |
| --- | --- | --- |
| 1 | Cable | 4 core 10 Sq. mm XLPE armored aluminum cable C2-FR-LSH. Identification on cable as per IS7098 part 1 latest |
| 2 | Conductor | Aluminum stranded & shaped as per IS 8130 2013 latest |
| 3 | Armour | GI steel formed wire |
| 4 | Outer Sheath | PVC – ST2 conforming to IS 5831 1984 latest |
| 5 | Inner sheath | Thermoplastic |

ii) The 1100 V 3 Core XLPE cable shall be buried at a depth of not less than 900mm below the ground level and shall be protected by means of layers of sand to a depth of 100mm throughout the entire route with protective brick covering.

iii) Wherever the U.G. cable must cross the existing cable, sewerage or water supply line the U.G. cable has to be maintained adequate clearance.

iv) The cables shall be laid in HDPE pipe wherever it crosses roads etc. and to be maintained safe adequate clearance.

v) The excavated trench shall be back filled, compacted and surface properly redone to restore that of original condition.

vi) Whenever a cable raised from the trench to end in termination, to be finally connected to the junction box of street light pole shall provide steel grip conduit.

vii) The lugs on the termination shall be compressed with a suitable compression tool.

vii) The armor should be efficiently bonded and earthed at all terminals to earth plates / points provided.

vii) All cables after laying and jointing works are completed should be tested systematically as below: -

a) Continuity

b) Absence of cross phasing

c) Insulation resistance to earth, insulation resistance between conductors by 1 kV Megger.

d) The internal bending radius of power cable shall not be less than 8 D

e)  All the cable joints / termination done by the contractor shall be guaranteed for 12 months from the date of energization of the complete cable. In the event of failure during the guarantee period, the restoration work shall be done free of cost by the contractor within 24 hours of notice.

SPECIFIC REQUIREMENTS:

CPWD specification/Manufacturer specifications of items are to be followed for the above work as per requirement.

Health & Safety :

The contractor shall take requisite step to prevent accidents and injury to health of its workmen , arising out of ,associated with or incurring in the course of work , by minimizing the cause of hazard inherent in the working environment . All the Personal Protective Equipment’s required as per the nature of activity such as Safety Helmets , Safety belt , appropriate Gloves etc , shall be issued to all their workmen.

Drawing for Pole