## Combined
Clarification (Technical) -II dated 01/02/2022 to the Bidding Document for Substation Package-SS01 for (i) Augmentation of 400kV bays at Kolhapur (MSETCL) and Augmentation of 400kV bays at Kolhapur (PG) S/s associated with Transmission System Strengthening beyond Kolhapur for export of power from Solar & wind Energy Zones in Southern region; (ii) Extension of 400/220kV Bhatapara (PG) S/s associated with Augmentation of 1x500 MVA, 400/220kV ICT (3rd) at Bhatapara; (iii) Extension of 400/220kV Sohawal S/s associated with Augmentation of 1x500 MVA, 400/220kV ICT (3rd) at Sohawal (PG) under system strengthening; (iv) Extension of 220kV Chamera GIS S/s associated with One No of 220kV bay at Chamera Pooling for 2nd Circuit stringing of 220kV Karain-Chamera pool Line under implementation by HPPTCL; (v) Extension of 220kV Khatkar (Jind) S/s, and Extension of 220kV Naggal (Panchkula) S/s associated with 220kV and 400kV Substation PGCIL Khatkar (Jind) & Naggal (Panchkula) Substation. Specification No.: 5002002050/SUB-STATION (EXCLUDIN/DOM/A00 - CC CS -1
Sr. No. | Tender Clause No. | Tender Clause | Bidder Query | POWERGRID REPLY
I | 400KV KOLHAPUR (MSETCL)
1 | SECTION-PROJECT & Price schedule | Scope | As seen from tender SLD & price schedule, 400kV WT, CT, Pentograph Isolators & CB are to be supplied & erected in 2 nos 400kV Line bays at Kolhapur substation. We presume that Line side LA & CVT are existing or shall be supplied by PGCIL & are not in our scope. | Please note that line side LA and CVT are already exising and same shall be used. Further, all other requirement / scope shall be as per bidding document.
2 | ANNEXURE-VIII, Volume-II | Cl. No. (c) & (d) | As per cl. No. (c) existing equipment support structures to be used & as per cl. No. (d)Dismantling of existing 400kV equipments along with support structures are covered under present scope as mentioned in BPS. Aforesaid statements are contradictory. Please confirm if supply of support structures for new 400kV equipments (WT, CT, Pentagraph Iso) are in scope of work | The dismantled support structure may be used along with new supplied equipment with suitable modification if required.
3 | ANNEXURE-VIII | (f) Existing cables are envisaged to be reused. However, additional cable if any required shall be provided by bidder and the price of same shall deemed to be included in the equipment cost. | LT Power & Control Cables, Glands, lugs are not mentioned in price schedule. Please confirm whether the additional cables required to be quoted under erection hardware item? | The specification is ample clear about cables. Please comply.
4 | ANNEXURE-VIII | (b) Erection Hardware: For 2 X 400kV Bays under present scope. • 4.5” IPS Aluminium Tube shall be used in place of existing 4.0” IPS Aluminium tube for equipment interconnections. • Twin HTLS conductor shall be used in place of existing ACSR Moose conductors for interconnections. • Clamps & Connectors for equipments (as per requirement). • Earthing materials and risers for equipments (as per requirement). | Please provide following drawings for estimation, Electrical Lauout Plan & Section, Earthmat layout/spcing of earthmat | Electrical Layout Plan & Section, Earthmat layout/spacing of earthmat drawing for Kolhapur (MSETCL) shall be provided to successful bidder if required. Further, bidder is requested to visit site regarding the above inputs.
5 | Price schedule | Fabrication, galvanising and supply of Lattice Structures (MS Steel),to be designed during detailed engineering, for towers, beams andequipment support structure including pack plates / packwashers andgusset plates excluding fasteners and foundation bolts | Please provide the electrical layout plan & section of existing substation to understand the details of towers & beams to be designed under subject package. | Tower & Beams are not envisaged in the present scope. Electrical Layout Plan & Section, drawing for Kolhapur (MSETCL) shall be provided to successful bidder if required. Further, bidder is requested to visit site regarding the above inputs.
6 | Sec_Project_Ss01_Final |  | We understand from price schedule that there is no requirement of supply/integration work of CRP, Busbar augmentation & SAS as these items are not listed in price schedule. Please confirm. | As the present scope is involves upgradation of equipment rating only, modification of CRP/SAS is not envisaged under prsent scope.
7 | General |  | As the work extension to be carries out at 400kV MSETCL substation, please confirm whether Technical specification of MSETCL or PGCIL to be followed. | Bidder shall follow the technical specification of bidding documents.
II | 400kV KOLHAPUR (PG)
8 | SLD Price Schedule | - | As per SLD & price schedule, our understanding is that we need to supply & erect 4 nos 400kV WT along with terminal connectors & need to dismantle existing wavetraps & store them. Please mention the approximate location to store the dismatled equipments. | Dismantle and storage of existing WTs alongwith terminal connectors shall be handed over to Kolhapur (PG) subsustation stores.
9 | ANNEXURE-VIII | Cl. No. 1.1 (b) Erection Hardware: For 2 X 400kV Bays under present scope. • Twin HTLS conductor shall be used in place of existing ACSR Moose conductors for Interconnections of Dead End gantry to of SF6 to Air bushing. | Please provide the electrical layout plan & section of existing substation for working of erecetion Hardwares. | Electrical Layout Plan & Section of existing substation shall be provided to successful bidder if required. Further, bidder is requested to visit site regarding the above inputs.
10 | ANNEXURE-VIII | Cl. No. 1.1 (e) Main Earthmat is existing for present scope of work. Old earth connection for the Wave Traps shall be dismantled and all the new Wave Traps, structures, etc. shall be earthed by connecting them to the main Earthmat through new earth riser by the contractor | Please provide the existing earthmat layout/earthmat spacing. | GA drawing and Earthmat drawing for Kolhapur (PG) is attached.
11 | Sec_Project_Ss01_Final |  | We understand from price schedule that there is no requirement of supply/integration work of CRP, Busbar augmentation & SAS as these items are not listed in price schedule. Please confirm. | As the present scope is involves upgradation of equipment rating only, modification of CRP/SAS is not envisaged under prsent scope.
III | BHATAPARA TR AUGMENTATION
12 | EARTHMAT_BHATAPARA |  | Drawing provided with tender is not legible. Please provide legible copy of drawing. Also the area under scope of work not marked in the drawing. Please provide earthmat spacing in existing switchyard. | The document available already attached in tender documents. Bidder to quote as per BPS/TS Further, for more clarity bidder is requested to visit site regarding the above inputs.
13 | - | - | Please provide the electrical layout plan & section of existing substation. | SLD and Electrical layout plan with present scope marked is already attached with tender document. Bidder to quote as per BPS/TS. Further, for more clarity bidder is requested to visit site regarding the above inputs.
14 | Sec_Project_Ss01_Final | - | Existing SAS Architecture required for the SAS augumentation/integration. Please provide the same. | Existing SAS Architecture drawing shall be provided to the successful bidder during detailed engineering
15 | Sec_Project_Ss01_Final | A) a. Digital RTCC panel with 4 numbers of Digital RTCC relays (As per BPS) | Please confirm the location of existing RTCC panels for existing transformers. Also new RTCC panel being supplied shall accommodate 4 nos of digital relays in single panel only. Hence, please confirm whether new RTCC panel to be placed in existing Control Room building or SPR. Please provide details/drawings of existing RTCC panels. | Bidder is requested to visit site for verifying exising location of RTCC panels. The new digital RTCC panel shall be placed in new SPR. Drawing of existing RTCC panel shall be povided to successful bidder if required. Further, bidder is requested to visit site regarding the above inputs.
III | SOHAWAL TR AUGMENTATION
16 | Sec_Project_Ss01_Final | - | Existing SAS Architecture required for the SAS augumentation/integration. Please provide the same. | Existing SAS Architecture drawing shall be provided to the successful bidder during detailed engineering
17 | Sec_Project_Ss01_Final | A) a. Digital RTCC panel with 4 numbers of Digital RTCC relays (As per BPS) | Please confirm the location of existing RTCC panels for existing transformers. Also new RTCC panel being supplied shall accommodate 4 nos of digital relays in single panel only. Hence, please confirm whether new RTCC panel to be placed in existing Control Room building or SPR. Please provide details/drawings of existing RTCC panels. | Bidder is requested to visit site for verifying exising location of RTCC panels. The new digital RTCC panel shall be placed in new SPR. Drawing of existing RTCC panel shall be povided to successful bidder if required. Further, bidder is requested to visit site regarding the above inputs.
V | 220KV CHAMERA GIS
18 | Price schedule | Fabrication, galvanising and supply of Lattice Structures (MS Steel),to be designed during detailed engineering, for towers, beams andequipment support structure including pack plates / packwashers andgusset plates excluding fasteners and foundation bolts | Please provide the electrical layout section of existing substation to understand the details of towers & beams to be designed under subject package. | Bidder to quote as per BPS/TS.
19 | Sec_Project_Ss01_Final | - | As line length is not mentioned in tender documents, hence we are considering Distance protection relay as Main protection. Please confirm | Confirmed
20 | Sec_Project_Ss01_Final | - | Existing SAS Architecture required for the SAS augumentation/integration. Please provide the same. | Existing SAS Architecture drawing shall be provided to the successful bidder during detailed engineering
VI | KHATKAR (JIND) SS
21 | Sec_Project_Ss01_Final | - | As line length is not mentioned in tender documents, hence we are considering Distance protection relay as Main protection. Please confirm | Confirmed
22 | Sec_Project_Ss01_Final | - | Existing SAS Architecture required for the SAS augumentation/integration. Please provide the same. | Existing SAS Architecture drawing shall be provided to the successful bidder during detailed engineering
VI | 220KV NAGGAL SS
23 | Sec_Project_Ss01_Final | - | As line length is not mentioned in tender documents, hence we are considering Distance protection relay as Main protection. Please confirm | Confirmed
24 | Sec_Project_Ss01_Final | - | Existing SAS Architecture required for the SAS augumentation/integration. Please provide the same. | Existing SAS Architecture drawing shall be provided to the successful bidder during detailed engineering
Civil Work queries
25 | VI - KHATKAR (JIND) SS BOQ Sr. no. 323- Civil works | Earthwork in excavation & filling in all types of soil and soft/disintegrated rock in open areas/ nallas/ channels, to the requiredslopes, shapes, levels, elevations and profile, including trimming of bottom and slopes of excavation, bailing out rain(dewatering), pumping, removal of slush, preparing embankments/marginal banks, loosening, dressing, spreading material in layers notexceeding 200mm, as per direction of Engineer-in-Charge | Earthwork quantities mentioned in price schedule for Naggal & Jind SS seem to be on higher side. Please confirm if the quantities mentioned may reduce during execution or same are fixed. | Site Levelling is requried to be done at Khatkar (Jind) S/s and not at Naggal (Panchkula) S/s. Please refer to the Bid Price Shcedule under Amendment II. Bidder to qoute as per BPS.
26 | V-220 kV Chamera GIS |  | Please provide Drawing of existing GIS buildings for Bay extensions. | Necessary drawings shall be provided to the successful bidder. Bidder to qoute as per BPS.
27 |  |  | Please provide GPS Co-ordinates for all locations. | Please refer clarification I for address and contact details of site. Bidder to quote as per BPS/TS
28 |  |  | Please provide Soil Investigation report & contour if available for any site | The Soil Investigation Reports shall be provided to the successful bidder. Bidder to qoute as per BPS.
29 |  |  | Please confirm if the the concrete items mentioned in price schedule covers qunatities for the Fire wall & boundary wall. If yes please provide break up of concreate quantities required for Fire wall & boundry wall | Construction of firewall and boundary wall is not in the scope of the contractor.
30 | Spare-400kV T/F | Sl. No. 102 & 177, Sch-1 & Sch 2 Price schedule | Please provide the detailed list of items corresponding to subject spares. Further also confirm whether supply of these items are included in subject project scope. | Bidder to Quote as per BPS
31 | Pre - bid site visit /survey Permission | -- | We wish to conduct pre-bid site visit / survey to understand the local conditions of each substation. Kindly provide the contact details of location wise site officials. Also provide the permission to visit the sites. | Already provided in Clarification -I
32 | Layout drawings and Earth mat Drawings | Vol II Part 12 & 13. | Please provide the GA drawing and earth mat drawing for following substations as we need to estimate the the quantities of earthing flats (raisers) for equipment connection. 1. 400 kV MSETCL S/s at Kolhapur. 2. 400 kV Kolhapur substation (PG). | GA drawing and Earthmat drawing for Kolhapur (PG) are attached. Please refer detailed earthing scope mentioned in the TS and comply accordingly. For Kolhapur (MSETCL), bidder is requested to visist site to aquaint themselves the site conditions for collecting required inputs.
33 | Twin HTLS conductor shall be used in place of existing ACSR Moose conductors for Interconnections of Dead End gantry to of SF6 to Air bushing. | ANNEXURE-VIII : Scope of work, Kolhapur PG | Please provide GA drawing & section layout drawings to estimate the quantities of the following: 1. Distance between the Dead End gantry to of SF6 to Air bushing for calculation of HTLS conductor length. 2. The dropper from Dead end Gantry to Wave trap shall be of which conductor (i.e. existing Moose or HTLS) Please confirm the cross section and/or provide specification of HTLS conductor. | GA drawing and Earthmat drawing for Kolhapur (PG) are attached. Further, bidder is requested to visit site to aquaint themselves the site conditions for collecting required inputs.
34 | Substation wise existing bus conductor configurations | Sec_Project_Ss 01_Final | As per tender GA drawing and Earth mat layout drawings are provided. Please provide the sectional drawings for all substations or provide substation wise existing bus conductor configuration, Equipment interconnection conductor/IPS tube details for existing bays for calculation of clamps and connectors. | Bidder to quote as per BPS/TS. Bidder is requested to visist site to aquaint themselves the site conditions for collecting required inputs.
35 | Details of Existing equipments | Sec_Project_Ss 01_Final | Kindly let us know the Existing make and model of Control and Protection scheme & Substation automation System at 400 kV MSETCL S/s | Kindly note the details of Existing make and model of following at 400 kV Kolhapur MSETCL S/s: 1) Substation Automation System - SIEMENS make RTU SCADA 2) Bus bar protection - GE make B90 Bidder is requested to visist site to aquaint themselves the site conditions for collecting required inputs.
36 | Land development & Site Levelling work | Sec_Project_Ss 01_Final | The scope of work of Land development & Site levelling is mentioned only for Khatkar(Jind) substation. We presume that for rest of the locations available land for extension work is levelled land. Please confirm. | Confirmed that Site Levelling is requried at Khatkar (Jind) S/s only and that Site Levelling is not requried at Sohawal S/s, Chamera S/s, Naggal (Panchkula) S/s, Kolhapur (PG) S/s, Kolhapur (MSETCL) & Bhatapara S/s. The same can also be refferred at Section Project and it's Amendment.
37 | Soil Investigation Work & Contour Survey | Sec_Project_Ss 01_Final | As per scope of work soil investigation & Contour survey are not applicable for Naggal, Chamera & Khatkar substations. We presume that the same is not applicable for remaining substations also. Kindly confirm. | Refer Section Project for detailed scope of work for each sub station. Site Levelling is requried at Khatkar (Jind) S/s only and Site Levelling is not requried at Sohawal S/s, Chamera S/s, Naggal (Panchkula) S/s, Kolhapur (PG) S/s, Kolhapur (MSETCL) & Bhatapara S/s. Soil investigation is not required at any S/s.
38 | General - Civil Works | Soil Investigation Report | Since all the substations are existing substations Please share existing Soil Investigation Report to understand the soil strata. | The Soil Investigation Reports shall be provided to the successful bidder. Bidder to qoute as per BPS.
39 | CIVIL WORKS : BASED ON DESIGNS, ARCHITECTURAL, STRUCTURAL, FOUNDATION DRAWINGS TO BE DEVELOPED BY THE CONTRACTOR : Standard Structure and foundations for Equipment supports, Gantries, LM, LT Transformers, double pole structure, DG set etc. | C.2. Sec_Project_Ss 01_Final , VII Name of Substation : Extension of 400/220kV Chamera GIS Substation. | We presume that the drawing for Standard Structure and foundations for Equipment supports, Gantries, LM, LT Transformers, double pole structure, DG set etc shall be provided by Power Grid to the successful bidder. Please confirm. | 1. Standard Structure and foundation drawings for Towers/ Beams/ Equipment Support Structure shall be provided by POWERGRID. 2. Non Standard Structure and foundation drawings for Towers/ Beams/ Equipment Support Structure shall be developed by the contractor and approved by POWERGRID. 3. Foundation drawings for LT Transformer, Double Pole Structure, DG Set shall be provided by POWERGRID if required. 4. For further clarificaiton in scope of drawings to be developed by contractor refer Section Project.
40 | Clause no 24.19 of Annexure-I of GTR (Rev.15) | Technical Requirement of Communication Equipment: The SDH equipment shall be offered from a manufacturer(s) who is a “Local Supplier” as per DPIIT PP notification & has been Manufacturing SDH equipments for the last three (3) years and SDH equipment Manufactured by such manufacturer(s) shall have been satisfactory operation in 110kV or higher voltage Power Substations for at least two (2) years as on the date of NOA | As per the GTR only “Local suppliers” for communication equipment is approved and as per our knowledge only Tejas make is fulfil this criteria. We request you to approved “foreign suppliers” also for competitive price. | Bidder to meet as per requirement of Technical specification
41 | Sch -1 of Price Schedule | Spare-400kV T/F at Bhatapara & Sohawal location. | We understood this line item is for spares of 400kV Power transformer. As discussed with vendors Quotation for Spare only will not provide by any vendor, so we request you to kindly delete this line item from this package. | Bidder to quote as per BPS