| Sl. No. | Clause/ Drg. No. | Existing provision | Amended provision |
| --- | --- | --- | --- |
| 1 | Vol III BPS, Schedule I, II and III Part III 765/400KV Maheshwaram GIS S/s Extn. | New Item | 624kV Surge Arrester (1-Phase); EA; 3. |
| 2 | Vol III BPS, Schedule I, II and III Part III 765/400KV Maheshwaram GIS S/s Extn. | New Item | 765 kV, 1 phase Bus Post Insulator (except for Line Traps); EA; 12. |
| 3 | Vol III BPS, Schedule I, II and III Part III 765/400KV Maheshwaram GIS S/s Extn. | New Item | 336kV Surge Arrester (1-phase); EA; 3. |
| 4 | Vol III BPS, Schedule I, II and III Part III 765/400KV Maheshwaram GIS S/s Extn. | New Item | 420 kV, 1 phase Bus Post Insulator (except for Line Traps); EA; 18. |
| 5 | Vol III BPS, Schedule I, II and III Part-II: Aug of ICT at KPS3 S.No 7 | 800kV, 3000/3150 A, 50kA, Single phase, SF6 Gas Insulated Bus Duct (GIB) outside GIS Hall along with associated support structure.; M; 1250. | 800kV, 3000/3150 A, 50kA, Single phase, SF6 Gas Insulated Bus Duct (GIB) outside GIS Hall along with associated support structure.; M; 750. |
| 6 | Vol III BPS, Schedule I, II and III Part-II: Aug of ICT at KPS3 | New Item | Supply Items: 1000006163 Service Items: 100003632 800kV, 4000A, 50kA, Single phase, SF6 Gas Insulated Bus Duct (GIB) outside GIS Hall along with associated support structure; M; 500. |
| 7 | Vol III BPS, Schedule I, II and III Part-II: Aug of ICT at KPS3 S.No 19 | 420kV, 3000A, 63kA, Single phase, SF6Gas Insulated Bus Duct (GIB) outside GIS Hall along with associated support structure; M; 1850. | 420kV, 3000A, 63kA, Single phase, SF6Gas Insulated Bus Duct (GIB) outside GIS Hall along with associated support structure; M; 550. |
| 8 | Vol III BPS, Schedule I, II and III Part-II: Aug of ICT at KPS3 | New Item | Supply Item: 1000004295 Service Item: 100002142 420kV, 4000A,63kA, Single phase SF6 Gas Insulated Bus Duct (GIB) outside GIS Hall along with associated support Structure; M; 1300. |
| 9 | Vol III BPS, Schedule I, II and III Part-II: Aug of ICT at KPS3 | New Item | Supply Item: 1000059091 Service Item: 100023078 800 KV, 3150A, 50KA, SF6 GIS AUXILIARY BUS MODULE EXTN FOR SPARE REACTOR AS PER SECTION-PROJECT, TECHNICAL SPECIFICATION; SET; 1. |
| 10 | Vol III BPS, Schedule I, II and III Part-II: Aug of ICT at KPS3 | New Item | Supply Item: 1000012039 Service Item: 100001867 Hydrant system, complete U/G piping and accessories etc. outside the Pump House for Fire Protection of 765/400/220kV (Ext) Substation; SET; 1. |
| 11 | Cl. no.: 2.2.2.B.v (Fire protection System) of Section project, Rev-00 of Vol. II of Bidding Documents | 2.2.2 Extension of 765/400kV KPS-3 GIS Substation B. Air insulated switchgear (AIS) and Other Main Equipments - FIRE PROTECTION SYSTEM: Fire protection system including HVWS & Hydrant system for 3nos 765/400kV, 1-Phase Autotransformers. The piping for fire protection system shall be extended from nearest autotransformer. | 2.2.2 Extension of 765/400kV KPS-3 GIS Substation B. Air insulated switchgear (AIS) and Other Main Equipments - FIRE PROTECTION SYSTEM: - Fire protection system (HVW spray system & hydrant system) for Owner supplied 3 nos. of 765/400kV, 1 Phase Auto-transformers. The existing piping (for Fire protection system) shall be suitably extended from nearest existing autotransformer for this purpose. Under the present scope, contractor shall integrate the annunciation/alarm signals of 765/400kV Transformers with the existing Annunciation panels placed in the FFPH building & Control room Building. The existing drawing of Hydrant piping Layout shall be provided during detailed engineering. - Outdoor Hydrant system for present scope 765kV & 400kV GIS Building. This will include new hydrant piping, dismantling, modification, shifting of existing piping required for new 765kV & 400kV GIS Buildings. - Fire detection & alarm system for 765kV GIS hall & 400kV GIS Hall shall be under present scope of work. Fire detection and alarm system for AHU Rooms & relay panel rooms under present scope are deemed to be included in respective GIS hall. Under the present scope, contractor shall integrate the Fire alarm signals with the existing Annunciation panels placed in the Control room Building. |
| 12 | Cl. no.: 2.2.2.B.xii (LIGHTNING PROTECTION (DSLP): of Section project, Rev-00 of Vol. II of Bidding Documents | The lightning protection (DSLP) for complete switchyard is to be provided by the contractor. The contractor shall design the lightning protection by utilizing the structures being provided under present scope. In case, additional structures (Lightning Masts) are required to meet the lightning protection, the contractor shall provide the same without any additional cost to POWERGRID. The cost for provision of lightning masts, including associated earthing materials, hardware etc. shall deemed to be included under the respective switchyard bay structures. The civil works shall be payable as per relevant item of BPS | The lightning protection (DSLP) for area under present scope including 765kV Transformer area is to be provided by the contractor based on employer provided drawings. In case LM’s are required the same shall be provided by contractor under relevant items of Structures (in MT). The cost for associated earthing materials, hardware etc. shall deemed to be included under the respective switchyard bay erection hardware |
| 13 | Vol III BPS, Schedule I & II, Sl. No. III) 4 of 765/400KV Maheshwaram GIS S/s Extn. Schedule III Sl. No. III) 5 of 765/400KV Maheshwaram GIS S/s Extn. | 420kV, 3150 A, 63 kA, SF6 GIS Auxiliary Bus module for Spare Transformer as per Section-Project, Technical specification; SET; 1. | Item deleted |
| 14 | Vol III BPS, Schedule I, II and III Part III 765/400KV Maheshwaram GIS S/s Extn. | New Item | EXTENSION OF 420 KV, 3150A, 63KA, SF6 GIS AUXILIARY BUS MODULE FOR SPARE TRANSFORMER AS PER SECTION-PROJECT, TECHNICAL SPECIFICATION; SET; 1. |