| S. No. | Volume/ Section/ Clause No. | Description | Bidder’s Query | Bidder’s Recommendations | POWERGRID Reply |
| --- | --- | --- | --- | --- | --- |
| 01 | Clause No. 1.0.6.4 of Technical Specifications | No. of Sides for the design/manufacture/testing/supply | Drag Coefficient is provided up to 16 sided | Can we have liberty to consider 20 sided polygon structure as it is very common in Pole industry. | Bid document shall prevail |
| 02 | Clause No. 1.4.9 of technical Specifications | Max. Permissible Segment / Seams | Max. 4 Seams are allowed if D>=1800 | Do we have liberty to consider more than 4 seams as 765 kV Pole diameter is so high and procurement of raw material with larger width is difficult for one or two poles. | Bid document shall prevail |
| 03 | Clause No. 1.5.1.3 © & S. No. 5 of BOQ | Full scale prototype testing | Proto Type Testing of Pole structure for design load cases & up to destruction | 1. How many load cases to be considered, can we consider 10 cases as per CEA guide lines? 2. Performing destruction of Pole during type testing is very difficult and dangerous. It may lead to damage to the testing centre/causality. So, request you to consider max 120% of design loads during type testing. Test shall be declared as successful if 120% loads are achieved even though it can take more loads. | Pole shall be tested by contractor as per POWERGRID approved testing procedure. |
| 04 | Clause No. 1.5.1.3 © & S. No. 5 of BOQ | Full scale prototype testing | Proto Type Testing of Pole structure for design load cases & up to destruction | Request you to consider third party testing facility or Independent Test Center i.e. CPRI in order have transparency in test results as this is the first 765 kV D/C Pole to be type tested in the world | Bidder may refer clause 1.7 of TS |
| 05 | Volume-I, Section-I IFB Clause 3.1 Scope of Work | The scope of work covered under the subject packages shall include the following: • PA i. Design of pole structure for +0, +3, +6 & +9m extensions. ii. Development of design/drawing of Pole & its foundation (both Cassion & Open), development of structural drawing, BOM & shop drawings. iii. Fabrication and Galvanizing of Pole structure. iv. Horizontal proto assembly (PA+0). v. Transportation to test bed. vi. Full scale proto-type testing of PA+0. vii. Submission of final set of documents (Pole Design/ Clearance drawing/ Structural drawing/ BOM/ shop drawing of Pole with its extensions and foundation designs). | It is not clear from the scope of the PA Type Pole what is required to be done with the pole after the successful completion of the Full-Scale Prototype Testing of PA+0. Specifically, it is unclear whether the PA Type Pole is also required to be supplied to the PGCIL store along with the PD/PE Type Poles ? as this requirement has not been mentioned in the scope for the PA Type Pole. | We recommend to consider light angle (0-5deg) pole structure in the place of suspension or tangent pole as this design can be used in multiple places as all tension poles are to be checked with Anti-Cascading load case or it can be used as cut-point pole. | Bidder to design pole as per provisions of Technical Specification. Bidder may refer TS for scope of work where it is clearly mentioned that only PD/PE type pole is to be supplied to PGCIL Store. |