| Sl. No. | Clause ref. | Existing Provision of the Bidding Document | Bidder’s Query/Comments | POWERGRID’s Clarification |
| --- | --- | --- | --- | --- |
| 1 | Volume II, Section II, Clause 1.9.2 – Core, point 1.9.2.1 | The core wire strand(s) shall be of………………………...........................................Bidder shall furnish properties and composition of the core wire strand(s) in the schedule GTP of BPS. The properties & composition of core wires guaranteed by the bidder shall be based on the relevant Indian/International Standards. However, the material offered for Steel/ Invar core shall meet following minimum requirements regarding torsion & elongation of core wires: Minimum No. of twists in guage length equal to 100 times the dia. of wire which the strand can withstand in the torsion test (before stranding)*; 16. Minimum elongation (%) of the core strand (after stranding) for a gauge length of 250 mm (at break); 1.5. *A reduction of 2 number of twists is permitted for after stranding values.. | Kindly modify/ remove as mentioned and struck off (In red) below, Bidder shall furnish properties and composition of the core wire strand(s) in the schedule GTP of BPS. The properties & composition of core wires guaranteed by the bidder shall be based on the relevant Indian/International Standards. However, the material offered for Steel/ Invar core shall meet following minimum requirements regarding torsion & elongation of core wires: Minimum No. of twists in guage length equal to 100 times the dia. of wire which the strand can withstand in the torsion test (before stranding) * - 16 Nos Minimum elongation (%) of the steel strand (after stranding) for a gauge length of 250 mm (after break) – 1.5% | Provisions of the bidding documents remain unchanged. |