| Sl. No. | Clause ref. | Existing Provision of the Bidding Document | Bidder’s Query/Comments | POWERGRID’s Clarification |
| --- | --- | --- | --- | --- |
| 1 | Volume II, Section I, Clause 3 | ………………….. C; Sag Tension Requirements. 1; Ruling Span (m); 350. 2; Maximum sag for ruling span at designed maximum continuous operating temperature corresponding to required ampacity per conductor/ sub-conductor as specified at sl. no. (A) (1) above (m); 8.84. 3; Minimum Sag for ruling span at minimum temp (0 deg C) and no wind condition (m); 6.11. 4; ……………; …….. 5; Tensions under Condition-I. a); Tension at 32°C and full wind condition (45 kg/m2 wind pressure); ≤ 3953 kg & not exceeding 50% of UTS of proposed conductor. b); Tension at 0°C and 2/3 wind condition (30 kg/m2 wind pressure); ≤ 4362 kg & not exc eding 50% of UTS of proposed conductor. 6; Tensions under Condition-II. a); Tension at 32°C and full wind condition (156 kg/m2 wind pressure); ≤ 6596 kg & not exceeding 70% of UTS of proposed conductor. b); Tension at 0°C and 36% of full wind condition (56 kg/m2 wind pressure); ≤ 4389 kg & not exceeding 70% of UTS of proposed conductor. …………………….. | Kindly amend/add the sag requirements for condition-II based on tower feasibility, Max. Sag - 10.18 mtr Min. Sag at Zero deg. C – 7.15 mtr | Please refer Amendment No. 4 in this regard. |