| Sl. No. | Ref Section | Provision in bidding document | Bidders Queries | POWERGRID Reply |
| --- | --- | --- | --- | --- |
| 1. | Section Project Cl. No. 2.2.d.ii) Pg No: 3 of 6 & Price Schedule- Sch 1- IV, PR Line No.1030 | Existing 400KV Class Transformers are equipped with Conventional RTCC system. 01 no. Conventional RTCC panel for remote control of Tap changing of 01 no. Transformer (being supplied) under present scope of contract. Technical specification of the same is attached as ANNEXURE-II. | a) As per Section project & Annexure-II we understand that bidder to supply the Conventional RTCC Panel for Nalagarh S/s. and no requirement of Digital RTCC Relays for parallel operation with Existing transformer. b) But as per the BPS we understand that along with the Panel there is a requirement of Digital RTCC relays as per Specification (i.e., One Relay for 3-ph Transformer + One Spare Relay). | Digital RTCC relay is not envisaged in the scope of Nalagarh S/s (Extn) . |
| 2. | Price Schedule (BPS) PR Line item No. 190, 2230 & 1060 | 245KV 2000A RIP BUSHING MAKE MASSA LLC | As specified in the subjected PR Lines, the 245kV Class RIP bushing shall be of only Massa LLC make as Spare & also for Offered Transformers (or) Bidders can consider any PGCIL approved Vendor for the Offered Transformers as well as for spare. | Please refer Amendment-I. |
| 3. | 08-Sample Forms and Procedures_Vol-I_Appendix-2-Cl. No. 2.1.ii) | Subscript ‘1’ refers to indices as on sixty (60) days prior to date of shipment, for Copper, Electrical Lamination Steel, Insulating material and Insulating oil. Thirty (30) days prior to date of shipment, for Construction Steel & ninety (90) days prior to date of shipment, for labour. | As per the Latest IEEMA Formula the Indicies for Construction Steel is considered 60 days prior to Dispatch and we request for the correction of the same in the present Tender as follows : Subscript ‘1’ refers to indices as on sixty (60) days prior to date of shipment, for Copper, Electrical Lamination Steel, Insulating material Construction Steel and Insulating oil. & ninety (90) days prior to date of shipment, for labour. | Provisions of Bidding Documents shall prevail. |