| S N | Clause |  | Provision of Bidding Documents |  | Bidder’s Query | POWERGRID's Reply |
| --- | --- | --- | --- | --- | --- | --- |
| Volume-I (Conditions of Contract) |  |  |  |  |  |  |
|  |  | Vol. II Part-A Section-1 Point 1.7. e) |  | Import and Adaption of database & displays made by Employer/Owner for existing NMS system including import of historical data stored in existing servers for integration in new system. | ## We request to kindly confirm and share below details: ## 1.Whether the required database and access to schemas etc. of existing NMS/EMS/NES is available with PGCIL so that the same can be considered for import & integration. ## 2. Size of data to be imported. ## 3. Retention period for data to be imported, whether 7 years or 12 months. | Bidder to Comply TS |
|  |  | Volume II Part A Section-1, 1.9.2 xxv |  | After successful deployment of UNMS system, all data from Excel sheets and disparate sources shall be migrated to proposed UNMS system so that operations team can work efficiently. |  |  |
|  |  | Vol. II Part-A Section-1, Point 1.7. g) |  | Integration & Testing with new EMS/NMS/NEs coming up during implementation and AMC period of this Contract. | We request to kindly confirm and share below details: 1. The details provided in the TS Appendix for upcoming NMSs/EMS/NEs are final and shall be considered for integration 2. Any further NMS/EMS/NEs etc. other than these shall be considered with separate CRs, commercials and the required licensing shall be procured by PGCIL 3. We understand that that New/upcoming national U-NMS/NMS/EMS/NEs will be excluded from the project delivery period of 20 Months and shall be integrated as and when ready and will not effect the project completion and signoff | 1. The sizing of the UNMS system shall be done as per Appendix G. The details provided in Appendix A is not exhaustive and shall be finalized during detail engineering. 2. The sizing shall be done as per Appendix G i.e. for 2000 NEs with expansion capability of 200%. Any upcoming NE/NMS during implementation and AMC period shall be integrated with the UNMS in present scope. 3. Confirmed |
|  |  | Vol. II Part-A Section-1, 1.9.2 xviii |  | Integration of existing equipment and with other planned equipment being procured by Employer/Owner in future. Contractor is responsible for integrating the complete system i.e. upcoming/future network equipment also. |  |  |
|  |  | Vol. II Part-A Section-1, Point 1.7. s) |  | Comprehensive Maintenance of the supplied system for seven (7) years including one (1) year defect liability period as per specification including future UNMS/NMS/EMS & NE Integrations, Database configurations, Maintaining Spare inventory etc. | We request to kindly confirm and share below details: 1. The details provided in TS Appendix A for upcoming NMEs/EMS/NEs are final and shall be considered for integration 2. Any further NMS/EMS/NEs etc. other than these shall be considered with separate CRs, Commercials and the required licensing shall be procured by PGCIL. 3. We understand that that New/upcoming national U-NMS/NMS/EMS/NEs will be excluded from the project delivery period of 20 Months and shall be integrated as and when ready and will not effect the project completion and signoff | 1. The sizing of the UNMS system shall be done as per Appendix G. The details provided in Appendix A is not exhaustive and shall be finalized during detail engineering. 2. The sizing shall be done as per Appendix G i.e. for 2000 NEs with expansion capability of 200%. Any upcoming NE/NMS during implementation and AMC period shall be integrated with the UNMS in present scope. 3. Bidder to Comply TS |
|  |  | Vol. II Part-A Section-1, 1.9.2 xxvi |  | Tie up with existing communication system provider for providing necessary system information of existing OEMs of Communication system for getting required information for seamless integration with U-NMS system as per requirements mentioned in different sections of Technical Specification. | Since the existing NMS/EMS/Nes OEM AMC is taken care by PGCIL and required contracts may be in place for the same, we hereby request PGCIL to facilitate in establishing the communication with the existing OEM's for initiating the necessary discussion. | Bidder to Tie up with existing communication system provider for seamless integration with UNMS System. |
|  |  | Vol. II Part-A Section-1, Point 1.7. l) |  | Integration of all the supplied equipments and existing system | Kindly confirm below details: 1. We understand that any kind of configuration at existing NMSs/EMS/NE's will be taken care by existing service provider of PGCIL and required support for NBI/API/Adapter development shall be facilitated by PGCIL. 2. The required database and access to schemas etc. of existing NMS/EMS/NE's are available with PGCIL for successfull integration with proposed U-NMS | 1. Bidder to comply TS w.r.t to seamless integration of supplied systems and existing system. |
|  |  | Vol. II Part-A Section-1 ,Point 1.7. m) |  | The contractor’s scope shall include customization of its database, such as configuration of database, scan period and all other database parameters required to integrate existing system successfully. |  | 2. Bidder to Comply TS |
|  |  | Vol. II Part-A Section-2, 2.2 |  | Project Schedule Completion schedule of the project is 20 months from the date award of contract agreement. Based upon this the bidder shall submit a preliminary project implementation schedule along with the bid. The detail project implementation schedule shall be submitted by the Contractor after award for Employer’s/Owner’s approval, which shall include at least the following activities: | We understand that that integration of New/upcoming national U-NMs/NMS/EMS/NEs will be excluded from the project delivery period of 20 Months and will not effect the project completion and signoff, kindly confirm. | Bidder to Comply TS |
|  |  | Vol. II Part 3 Appendix-B |  | Project Implementation Schedule |  |  |
|  |  | Volume II PART-A Technical Specification, Section 1.4.1, B |  | ISTS Communication provided by Private Transmission Agencies | We request to kindly provide the details of private transmission agencies/systems to ascertain the integration efforts and necessary arrangemnts can be done for the same. | Bidder to comply TS. If needed, Details in addition to TS may be collected by the Bidder on their own. |
|  |  | Vol. II Part-A Section-1 Point 1.7. n) |  | Shifting of existing system workstations and Installation of new system workstations at temporary location in parallel for intervening period. | We understand that there will be no temporary implementation at any of the sites, kindly confirm and share below information: 1.Shifting of the systems from temporary location to permanent should not be considered under the project timelines as dismantling and re-deployments of the systems as per the ask can be momentous task. We further request that functional testing and commissioning should be considered even if systems are up and running at the Temporary Location. 2. Kindly confirm whether any shifting will be involved or not. And if yes, pls share the details of shifting location to ascertain the efforts. | Bidder to comply TS. |
|  |  | Vol. II Part-A Section-1 Point 1.7. o) |  | Shifting and Installation of new system in UNMS Centre. This shall include all the services including cabling, interface modification and shifting or re-shifting of system required for intervening period and for final shifting to main UNMS Centre. Re-cabling for some or all equipments as required for final shifting shall also be in the scope of supplier |  |  |
|  |  | Volume II PART-A Technical Specification, Section 1.8.1 |  | Teaming Agreement of bidder with OEM | Kindly confirm that teaming agreement is required between the bidder and NMS OEM only and not for rest of the Hardware OEM's etc. | Confirmed. |
|  |  | Volume II Part A Section-3 3.4.9.3 |  | Less than 99.9% Deduction of 2% of the apportioned price of the apportioned quarterly AMC for every 0.5% or part there of decrease in availability under 99.9%. (Maximum amount of deduction is limited to 100% of AMC charges) | We request to kindly cap the maximum penalty within 05% to 15% of the AMC Charges as per standards followed. | Bidder to comply TS. |
|  |  | Volume II Part B Section-4 4.1.2 |  | Operating System The operating system of all the equipments of U-NMS system including network equipments shall be latest version. The operating system shall be hardened to provide robust security. In order to facilitate cyber security requirements including patch management, common operating system is preferable to be used by all server nodes within the U-NMS System. | Operating system, database details are not mentioned in the TS, so we would request that the bidder can propose open-source operating system, virtualization and databases that meet the requirements. Kindly confirm. | Bidder to Comply TS |
|  |  | Vol. II, Part-2 of 3 5.5.2 LAN Switches, part-B, section 5 page 10 |  | Dual LAN is envisaged for the System at Main UNMS Centre and Single LAN for the backup UNMS Centre. | It is understood that, the quantity of L2 switches mentioned in BOQ (Appendix-C) are considered based on the dual LAN at main UNMS and single LAN at back-up UNMS. Please confirm if the understanding is correct | Bidder to comply TS. |
|  |  | Vol.II, Appendix-D, S. No 14 - point 13 (WAN Router, page 16) |  | There shall be 50% spare ports in every router over above the BOQ specified quantity of ports Router should support 1 GB, 10 GB, STM 64 & serial interface. As a minimum 1-G.703 and 10 no. - 1 GB Ethernet ports, 4x10 Gbps Fibre optic ports | Please specify the fiber optic interface type i.e single mode (LR/ER) or multimode | Single Mode |
|  |  | Vol.II, Appendix-D, S. No 15 - point 7 (LAN Switch, page 17) |  | 10 Gbps Fibre Optic Ports for Connecting dual Fibre Optic LAN at Server location and State Minimum 8x10 Gbps Fibre Optic Ports and 16x1 Gbps Ethernet ports at Server location Minimum 4x10 Gbps Fibre Optic Ports and 8x1 Gbps Ethernet ports at state | Please specify the fiber optic interface type i.e single mode (LR/ER) or multimode | Single Mode |
|  |  | Appenzix-D, Clause14, DRS for WAN router-S. No. 13 Interface support, page 16 of Page 21 |  | There shall be 50% spare ports in every router over above the BOQ specified quantity of ports. Router should support 1 GB, 10 GB, STM 64 & serial interface. As a minimum 1-G.703 and 10 no. - 1 GB Ethernet ports, 4x10 Gbps Fibre optic ports | As per the solution requirement 1/10G ethenet interfaces shall be required for connecting the EMS and UNMS. For unmanaged NE, E1 (G.703) connectivity is also provisioned in the solution for carrying management traffic as DCN over E1. The STM64 requirement is not required and is not feasible for the current set-up of EMS and NMS. We request to kindly remove the STM64 support feature from the router as it is not required and is a restrictive clause in favour of particular OEM. | Bidder to comply TS. |
|  |  | General (WAN Router cum Firewall) |  | Minimum Inbuilt software firewall features….. | The Firewall appliance is also provisioned at each ingress and egress network locations to protect the traffic; thus, there is no requirement of Firewall features in router including IPsec. We request you to kindly remove the firwall functionality and IPSec from the router as separate firewall is provided already to meet the solution requirements. | Bidder to comply TS. |
|  |  | Vol.II, Appendix-C, S. BoQ Switches |  | 24 Port L-3 LAN SWITCH for Server location | We recoomended to include additional 5 TOR Switch in the BoQ to achieve different Security Zones- External Zone , Internal Zone and DMZ Zone. | Bidder to comply TS. |
|  |  | VOL-II Part 3 of 3 Appendix -C: BoQ of UNMS, Page No. 2 of 2 & VOL-II Part 3 of 3 APPENDIX-H: AUXILIARY POWER SUPPLY CALCULATION Page No. 1 of 1 |  | 2. VRLA TYPE BATTERY BANKS & Criteria for selection of rating of UPS Battery bank: | As per our understanding, the mentioned battery VAH is 76800 VAH according to appendix-H, Kindly confirm that bidder needs to consider the same. | Bidder to comply TS. |
|  |  | VOL-II, Part 2 of 3, PART-C Page No. 19-20 of 30 |  | (a) The rating shall be of minimum as stated in relevant appendices of the technical specification. (b) It shall be provided with 4 nos. of Four (4) Pole type MCCBs which shall conform to IS 13947-2/IEC 60947-2 as indicated in figure 2-1. All the MCCBs shall provide overcurrent, short circuit protection and the co-ordination for the overload and short-circuit tripping of the MCCBs/MCBs with upstream and downstream switchgear shall be provided for the satisfactory discrimination. (c) It shall be provided with Class ‘B’ & ‘C’ type surge protection. The surge protection shall be in compliance with IEC 61312, IEC 61024, VDE 0100-534 for following i) Low Voltage Surges (Class C): Between Requirement R-N, Y-N, B-N In≥10kA, 8/20 μS for each phase N - PE In≥20kA, 8/20 μS In = Value of Nominal Discharge Current (ii)Lightning Electromagnetic impulse and other High surges (Class B): Between Requirement R-N,Y-N, B -N Iimp≥50kA, 10/350 μS for each phase N - PE Iimp≥100kA, 10/350 μS Iimp = Value of Lightning Impulse Current The blind spots shall be avoided as per IEC 61312-3. | The latest standard is IEC - 61643 hence request to consider IEC 61643 instead of IEC 61312. Kindly Confirm | Latest Industry standards meeting our technical specifications are acceptable. |
|  |  | Vol. II, Appendix -C: BoQ of UNMS, Page 1 of 2 & Appendix-D Page No. 2 of 3 & 7 of 21 |  | Video Projection system- Unit (LOT) Qty-1 & 9. Video Projection System (VPS) - Offered by the Contractor & Appendix - K (Typical Network Architecture MAIN CONTROL CENTRE) | Bidder is considering VPS 4X3 MODULE, kindly confirm our understanding. | Bidder to comply TS. |
|  |  | VOL-II, Part 3 of 3, Appendix D Page No. 19 of 21 |  | 19. Server Panels Sr No -8 : 230V AC, 15/5 A Internal power socket with switch General- Material for rack & Thickness of rack's material | Kindly confirm the following 1. Each rack should have 2 PDU for redundancy at rack end hence requesting to add the following specifications for PDU: " 32A MCB with indicator, SPD, IEC C13 X 16 Nos, IEC C19-6 Nos, 5/15A 5 pin socket X 5 Nos with industrial sockets." 2. Material for rack- CRCA & Thickness of rack's side panel 1.2mm, door 1.6 mm and main structure should be minimum 2 mm. Perforated door will be provided. | Bidder to comply TS. |
|  |  | VOL-II, Appendix C: BoQ of UNMS Page No. 1 of 2 |  | 44U SERVER RACK WITH KVM SWITCH &MONITOR (LOT)- Qty: 1 | Kindy provide total qty of rack/server panels | Bidder to comply TS. |
|  |  | General |  | General | A) Space for Rack, Power, Cooling, UPS, incoming & outgoing ups panel & DBs will be provided by purchaser. Please confirm B) It is understand that the AHU, PAC required for the rooms, rack area respectively alogn with Ducting for cooling distribution will be provided by purchaser. Please confirm C) Earth pit shall be provided by PGCIL. Kindly Confirm | Bidder to comply TS. |
|  |  | VOL-II, Part 2 of 3, PART-C: Sec-1 Page No. 10 of 30 |  | 1.2.9 Enclosures/ Earthing: The connection to the nearest available earthing grid shall be made by the Contractor through 50X6 sq. mm. GI strip with proper protection | As per our understanding, bidder needs to extend earth strip from nearest available earth box/strip for termination of earthing system. Bidder need not to prepare earthing pit. Kindly confirm. | Confirmed. Bidder to Comply TS |
|  |  | VOL-II PART-A, Sec-1 Page No. 8 of 22 |  | 1.11 Main and Backup UNMS Centre Operational Philosophy: This specification document states the requirements for the UNMS systems, which the Contractor shall install at RTAMCs of POWERGRID at Kolkata, Patna and Bhubaneswar and SLDCs of BSPTCL, JBVNL, WBSETCL, DVC, OPTCL, and Sikkim SLDC of Eastern Region. Apart from the number of workstations/servers associated with each system, the UNMS configurations shall be identical at main & back-up UNMS centres. | We understood that, bidder needs to prepare supporting infra for UNMS system at all 6 SLDC's also. The SOR items mentioned at ER1 & ER2 will be distributed accordingly. Requesting to Segregate the SOR qty in all locations (SLDC & RTAMCs) and provide additional qty of item list in SOR if required. | Bidder to comply TS. |
|  |  | Volume II, Part 3 of 3, Appendix-D: DRS OF HARDWARE, Workstation consoles with dual/ single monitor , Page No. 3 of 21 |  | 5. Processor: Min 1x4 Core, Clock Speed >3.2 GHz | As these specifications are not available w.r.t leading OEMs, Kindly change the specifications as follows : Intel Core Processor i5, 4 Cores, 8MB Cache, >3.2Ghz Turbo | Minimum CPU frequency with Turbo Boost option is already mentioned in TS. Bidder to comply TS. |
|  |  | Volume II, Part 3 of 3, Appendix-D: DRS OF HARDWARE, 4. Remote Console, Page No. 3 of 21 |  | 9.Speakers: Inbuilt | As the inbuilt speakers are not available with leading OEMs hence requesting to allow external speakers of 4W. | Bidder to comply TS. |
|  |  | Volume II, Part 3 of 3, Appendix-D: DRS OF HARDWARE, Workstation consoles with dual/ single monitor , Page No. 3 of 21 |  | 10.Interfaces Ports: 10 Gbps dual Fibre Optic Ports (Minimum) for connecting on dual Fibre optic LAN in each erver at Main & Backup Control Centre and SLDCs, USB Ports, HDMI Ports | As these specifications are not available w.r.t leading laptop OEMs, Kindly change the specifications as follows : 1 Gb Ethernet port 3x USB 3.0 Gen 1 & 1x Thunderbolt Type C, 1 HDMI Port Or allow the use of the external convertor to meet the required interface ports. | Bidder to comply TS. |
|  |  | Volume II, Part 3 of 3, Appendix-D: DRS OF HARDWARE, Workstation consoles with dual/ single monitor , Page No. 3 of 21 |  | 8. Internal Optical Drive : DVD+RW | As DVD+RW is obsoleted from the major OEMs, Kindly allows for the external DVD +RW drive | Bidder to comply TS. |
|  |  | Volume II, Part 3 of 3, Appendix-D: DRS OF HARDWARE, 4. Remote Console, Page No. 3 of 21 |  | 7. Processor: Min 1x4 Core, Clock Speed >3.2 GHz | Kindly change the specifications as follows as these specifications are not available with OEMs : Intel Core Processor i5, 4 Cores, 8MB Cache, >3.2Ghz, 4.2Ghz Turbo | Minimum CPU frequency with Turbo Boost option is already mentioned in TS. Bidder to comply TS. |
|  |  | Volume II, Part 3 of 3, Appendix-D: DRS OF HARDWARE, 4. Remote Console, Page No. 3 of 21 |  | 8.Speakers: Inbuilt speakers | As the inbuilt speakers are not provided by OEMs hence requesting to allow external speakers of 4W. | Bidder to comply TS. |
|  |  | VOL-II, Part 2 of 3, Part B ; Section 5 ; 5.11 Furniture Page 13 of 15; 5.11 (a) ; Point 9 |  | Monitor tilts variation with motorized height/tilt/depth adjustment. | This is not required as Worktop and Monitors are on different platforms and both platforms are having Independent Height adjustment Mechanism, also Monitors are mounted on Double extension Arms which gives User the flexibility to adjust the Monitors as per there Comfort. | Bidder to comply TS. |
|  |  | VOL-II, Part 2 of 3, Part B ; Section 5 ; 5.11 Furniture Page 13 of 15; 5.11 (a) ; Point 10 |  | Programmable touch screen controls for operator desk management with automatic save PRESET options related to desk movements/position. | Programmable Touch screen is just a technical enhancement without any Ergonomic impact and thus adding extra cost to the Delivery, this feature is already available manually and also through OEM Mobile APP like LINAK. Etc. So kindly remove it. | Bidder to comply TS. |
|  |  | Volume II Appendices Technical Specification for Unified Network Management System (U-NMS) : Appendix-D DRS OF HARDWARE, Remote Console , Page No. 3 of 21 |  | 2.Model No. The compute platform (CPU) shall be inbuilt into display | The specifications of the remote console is not possible with inbuilt option of CPU to all across the OEMS as specs of remote console is of high end server which comes with 4U form factor which also does not get in built attached with 55 DISPLAY so kindly delete the clause. | 55 inch Display with inbuilt or External CPU is already Mention in TS. Bidder to Comply TS. |
|  |  | Volume II, Part 3 of 3, Appendix-D: DRS OF HARDWARE, Processor terminal (Laptop) , Page No. 5 of 21 |  | 3. Processor Min 1x4 Core, Clock Speed >3.2 GHz | Kindly change the specifications as follows as these specifications are not available to leading laptop OEMs : Intel Core Processor i5-10210U, 4 Cores, 6MB Cache, 1.6Ghz, 4.2Ghz Turbo | Minimum CPU frequency with Turbo Boost option is already mentioned in TS. Bidder to comply TS. |
|  |  | Volume II, Appendix-D: DRS OF HARDWARE, Processor Terminal (Laptop) , Page No. 5 of 21 |  | 10.Interfaces 1 Gb dual Ethernet ports Minimum 4 USB3.0 Ports 1 HDMI Port | Kindly change the specifications as follows as these specifications are not available to leading laptop OEMs : 1 Gb Ethernet port 3x USB 3.0 Gen 1 & 1x Thunderbolt Type C, 1 HDMI Port | Kindly refer clause of Volume II, Appendix-D: DRS OF HARDWARE, Processor Terminal (Laptop), Page No. 5 of 21. Bidder to comply TS. |
|  |  | VOL-II, Part 2 of 3, Part C , Page 16 of 30, 1.3.1.6: Connectors, Nuts & Bolts, Heat Shrinkable Sleeves |  | All inter cell connectors shall be protected with heat shrinkable silicon sleeves for reducing the environmental impact including a corrosive environment. | The asked silicon sleeves are not being manufactured by any battery OEM and hence they are proposing to amend this clause as " All inter cell connectors shall be protected with heat shrinkable PVC sleeves for reducing the environmental impact including a corrosive environment." | Heat shrinkable PVC sleeves are already mentioned in TS. Bidder to comply TS. |
|  |  | Volume II (2/3), Part B, 4.5.3 Intrusion Detection & Prevention System (IDPS)--(A) Intrusion Detection and Prevention System (Host Based)-- PDF Pg-87 |  | A) Intrusion Detection and Prevention System (Host Based): Host based Intrusion Detection and Prevention System module shall be provided for all machines on DMZ LANs. IDS shall be able to perform following actions: „X Capability for Detecting the intrusion attempt that may take place, intrusion in progress and the intrusion that has taken place. „X Flag and check unauthorized access | Please be referred that all type of unauthorized access can be met with access management / IDAM solutions and won't be available in many HIPS solutions globally. So we request the clause Should read as: " A) Intrusion Detection and Prevention System (Host Based): Host based Intrusion Detection and Prevention System module shall be provided for all machines on DMZ LANs. IDS shall be able to perform following actions: „X Capability for Detecting the intrusion attempt that may take place, intrusion in progress and the intrusion that has taken place. „X Flag and check all malicious activities and command & control access". | Bidder to comply TS. |
|  |  | Volume II (2/3),Part B, 4.5.3 Intrusion Detection & Prevention System (IDPS)--(A) Intrusion Detection and Prevention System (Host Based)-- PDF Pg-88 |  | In an event where user accounts are added, deleted, or modified, changes to key system files and executables is done in by unauthorized account or there is unauthorized attempt to overwrite vital system files, to install Trojan horses or backdoors suitable action should be taken such as: Terminate User (intruder) Login Disable User (intruder) Account Forge a TCP FIN packet to force intruder connection to terminate | HIPS can block the traffic once the attack has been detected. In case of TCP FIN, most of HIPS agent detects packet with only the SYN and FIN flags set. Since HIPS works on connection/session basis, for Activities like Terminate User Login & Disable User Account are user level activities and is not available with many HIPS solutions globally. Clause Should Read as: In an event where user accounts are added, deleted, or modified, changes to key system files and executables is done in by unauthorized account or there is unauthorized attempt to overwrite vital system files, to install Trojan horses or backdoors suitable action should be taken such as: Forge a TCP FIN packet to force intruder connection to terminate | Bidder to comply TS. |
|  |  | Volume II (2/3),Part B, 5.9 Centralized Management Console (CMC)-- PDF Pg -105 |  | 5.9 Centralized Management Console (CMC) | Kindly change to security CMC requirement as below. Centralised Management Console (CMC): A separate solution shall be supplied to be used as Centralized management console for the HIPS and firewall. The management console shall perform the following functions: (i).Create and deploys new policies (ii).For Centralized Logging of messages from all systems across the network as a Central Syslog server (inline with CERT-In Guidelines) (iii). Collect and archive audit log for post event analysis (iv).Maintain an Integrated Event Database (v)Getting Virus definition, signature, patches etc. update from internet and updating the system . (vi) Performance monitoring and log retention period of 1 months. | Bidder to comply TS. |
|  |  | Volume II(1/3),Part A, 1.15 Applicable Standards,Sec-1, PDF Page 25 & 26 |  | TEC GR no. GR/FWS-01/02 SEP 2006 for Firewall, Specifications and codes shall be the latest version, inclusive of revisions, which are in force. | TEC GR for FW is not available with some OEMs. We request to remove the same. | Bidder to comply TS. |
|  |  | Volume II (2/3),Part B, 5.5.4 (Intrusion Detection and Prevention System (IDPS),PDF Page 103 |  | The contractor shall provide an intrusion detection and prevention system, to have a dedicated NIPS (Network Intrusion Protection System) appliance and the IPS (Intrusion Protection System) functionality shall not be coupled with the Firewall solutions, which shall be integrated to detect and prevent intrusion, worm, virus etc. | Please remove this clause, With respect to RFP requirement, both internal & external firewalls are asked with built in IPS functionality. No need for dedicated NIPS & hence its TEC GR. | Bidder to comply TS. |
|  |  | Volume II(1/3),Part A, 1.15 Applicable Standards,Sec-1, PDF Page 25 & 26 |  | TEC GR no. GR/IPS-01/01 NOV 2006 for IPS | Please remove this clause, With respect to RFP requirement, both internal & external firewalls are asked with built in IPS functionality. No need for dedicated NIPS & hence its TEC GR. | Bidder to comply TS. |
|  |  | VOL-II (3/3) Appendix D, 10. Firewall Features/Characteristics required of internal Firewall: |  | IPv4 to IPv6 translations & Encapsulations. | Please revove this clause as some OEMs do not comply this clause. | Bidder to comply TS. |
|  |  | VOL-II (3/3) Appendix D, 10. Firewall Features/Characteristics required of internal Firewall: |  | Antivirus, Anti-worm, anti- spam and anti-spyware protection | Please revove this clause as some OEMs do not comply this clause. | Bidder to comply TS. |
|  |  | VOL-II (3/3) Appendix D, 12. Firewall Features/Characteristics required of External Firewall: |  | IPv4 to IPv6 translations & Encapsulations. | Please revove this clause as some OEMs do not comply this clause. | Bidder to comply TS. |
|  |  | VOL-II (3/3) Appendix D, 12. Firewall Features/Characteristics required of External Firewall: |  | Antivirus, Anti-worm, anti- spam and anti-spyware protection | Please revove this clause as some OEMs do not comply this clause. | Bidder to comply TS. |
|  |  | Volume II(1/3),Part A, 1.8 General Requirements, PDF Pg 15 |  | It should be noted that preliminary design information and bill of quantity are minimum and indicative only; the Contractor shall verify jointly (with Employer/Owner) the design data during the site surveys & detail engineering and finalize the BoQ as required for ultimate design & system performance. |  | All Items required to meet the requirement of TS shall be supplied by Bidder as part of present scope. Bidder to comply TS. |
|  |  | Volume II (2/3),Part B, 2.7.Development System as a Test Bench and as a Training Simulator system,PDF Page 58 |  | 2.7.Development System as a Test Bench and as a Training Simulator system The development systems shall include all functions required to support the generation and testing of the system software, database, displays and reports. The development system shall also include tools to acquire data from existing NMSs and independent Ness under test mode. Development system shall be able to provide testing facility for integration of new Patches, displays, integration with other NMS/UNMS/NEs or any other changes in the UNMS system before putting it online with Real-time system. · This system shall also be used as a Test bench for Cyber security and shall accordingly be equipped with firewall, antivirus and enable mode wherein threat scenarios can be tested with configured security elements before implementing on the main/production system. · This Test bench for Cyber security shall also be used for VAPT (Vulnerability Assessment & Penetration Tests) e.g. OS fingerprinting, Port scanning etc. | We assume that all the quantities mentioned in the SOR Items includes the training simulators and test bench also. In case there is a requirement of additional items apart from SOR Qty, based on the inputs recieved from the site survey or design engineering phase the same shall be procure seprately as a change management. | All Items required to meet the requirement of TS shall be supplied by Bidder as part of present scope. Bidder to comply TS. |
|  |  | Volume II (2/3),Part B,4.7 Monitoring and Compliance Manager of Critical Infrastructure Protection Standards, PDF Pg - 89 |  | Volume II (2/3),Part B,4.7 Monitoring and Compliance Manager of Critical Infrastructure Protection Standards, PDF Pg - 89 | We understand that the functionality of these components can be achived through the single console, kindly confirm. | Bidder to comply TS. |
|  |  | Volume II (2/3),Part B,5.9 Centralized Management Console (CMC),PDF Pg- 105 |  | Volume II (2/3),Part B,5.9 Centralized Management Console (CMC),PDF Pg- 105 |  |  |
|  |  | Volume II PART-A, Pg 13 |  | 1.7 Scope of Work | We understand that 1) New EMS/NMS/Nes coming up during implementation and AMC Period of this Contract shall be integrated with the proposed UNMS. Please Confirm 2) U-NMS at National level coming up during implementation and AMC period of this Contract shall be integrated with the proposed UNMS. Please Confirm 3) The tender scope of work for Integration with UNMS solution with the existing NMS/EMS/NEs only. Please confirm 4) Any Shifting is applicable to both main and backup UNMS center, also we understand that this refer to shifting of equipment within the same premises only. Please confirm 5) The term "Existing equipment" mentioned in this RFP is limited to existing NMS/EMS/NEs. Please confirm 6) The term additional NMS/EMS software may be required for integration of standalone NEs. The requirment shall be identified by the bidder during detailed engineering. Please confirm | 1. Confirmed 2. Confirmed 3. Bidder to comply TS 4. Bidder to comply TS. 5. Bidder to comply TS. If needed, Details in addition to TS may be collected by the Bidder on their own. 6. All details are given in relevant Annexure. Bidder to comply TS. If needed, Details in addition to TS may be collected by the Bidder on their own. |
|  |  | Volume II PART-A, Pg 16 |  | 1.9.2 Contractor’s Responsibilities and Obligations (xxix) Full system backup of all installed software for all machines. | Kindly confirm that backup solution is applicable for supply scope of this RFP | Bidder to comply TS. |
|  |  | General |  | RTO & RPO | Please specify the RTO and RPO of each solution | Bidder to comply TS. |
|  |  | Volume II PART-A, Sec-3, Page 6 of 16 |  | 3.4.4.1. Preventive Maintenance, Updates & Upgrades: | Lab Environment BoM is not mentioned in SOR. Please add the same in SOR | Bidder to comply TS. |
|  |  | General |  | Network/Communication channel | Our understanding is all network links, Bandwidth, communication channel shall be the scope of the purchaser, while monitoring of Nes over the provided network shall be scope of the bidder. Please confirm | Confirmed |
|  |  | VOL-II PART-B Sec-2 Page 6 of 38 |  | 2.3.Application Functions 2.3.1. Network Resource Management: a) Integration with other Existing Inventory Management Systems, if exists. | Our understanding is inventory Management system refer to existing NMS/EMS. Please clarify | Bidder to comply TS. |
|  |  | VOL-II PART-B Sec-2 Page 9 of 38 |  | 2.3.Application Functions 2.3.3. Network Configuration and Planning 9) The proposed system needs to interface with NMS/network elements belonging to different OEMs, supporting different interfaces in the future also. | Kindly confirm that this requirment refers the capability of proposed NMS only, any additional BoQ for new requirment shall be taken as variation order | Bidder to comply TS. |
|  |  | VOL-II PART-B Sec-2 Page 27 of 38 |  | 2.4.4. U-NMS Console on Mobile/Handheld | Kindly confirm the number of Users of mobile platform | Bidder to comply TS. |
|  |  | VOL-II PART-B Sec-2 Page 30 of 38 |  | 2.5.2. Future Readiness 1) UNMS will be able to integrate and assure a range of Network Function Virtualization (NFV) solutions from a range of vendors | Kindly confirm that this requirment refers the capability of proposed NMS only, any additional BoQ for new requirment shall be taken as variation order | Bidder to comply TS. |
|  |  | General |  | General | Our understanding is that bidder can propose Multi party UNMS System | Bidder to comply TS. |
|  |  | VOL-II Appendix Appendix E Page 1 of 5 |  | The auxiliary memory utilization of any of the server shall not exceed 25% of its delivered capacity. This memory utilization includes the memory used for storage of data for the defined duration as specified in the technical specification. | Our understanding for Auxilary memory is Server RAM. Please confirm | Bidder to comply TS. |
|  |  | General |  | General | Our understanding is that UNMS will not integrate and exchange data with existing systems like SCADA system. Please confirm | Bidder to comply TS. |
|  |  | General |  | General | Bidder can propose the mixture of multiple system/additional system from other OEM to complying the TS. Pease confirm | Bidder to comply TS. |
|  |  | General |  | General | Our understanding is there is no existing ERP, BSS, GIS solution so integration not required. Please confirm | Bidder to comply TS. |
|  |  | General |  | General | Our understanding is RFP scope for suppy, implementation, configuration & Mantainance of solution/Items mentioned in SOR only. Please confirm | Bidder to comply TS. |
|  |  | General |  | General | Our understanding Is bidder not need to provide SAN Switches. Please confirm. If Bidder need to supply the same then, is bidder need to comply TEC as well for SAN Switches mentioned in RFP?. Please Confirm | Bidder to comply TS. |
|  |  | General |  | General | Any feature, function not supported or available in any layer(NMS/EMS/NEs APIs, Comunnication System, etc) shall not be achived under UNMS. Please confirm | Bidder to comply TS. |
|  |  | General |  | General | CPU 2006 or latest equivalent is acceptable whereever required | CPU 2006 or latest is already mentioned in TS. Bidder to comply TS. |
|  |  | General |  | General | As the functional and technical requirement for PGCIL UNMS ER tender are similar to PGCIL UNMS NR & NER tender so we understood that the clarifications, corrigendum, addendum, Prebid queries released for PGCIL UNMS NR and NER Bid will be applicable for PGCIL UNMS ER Bid except the quantities mentioned in SOR/Price bid. Please Confirm | Bidder to comply TS. |
|  |  | General |  | General | CPU 2006 or latest equivalent is acceptable whereever required | CPU 2006 or latest is already mentioned in TS. Bidder to comply TS. |
|  |  | General |  | General | Processor frequency/Clock speed is mentioned in RFP is acceptable with turbo Frequency/Clock | Minimum CPU frequency with Turbo Boost option is already mentioned in TS. Bidder to comply TS. |
|  |  | II, Part 1, 1.7.t Page No.: 14 |  | Integration with third party Applications: The new UNMS Systems being supplied shall have provision to exchange data with the existing and or to be purchased third party applications of Employer/Owner in standard formats like ODBC, OPC & XML etc. | This is understood that any integration of the future procured softaware with the proposed UNMS will be handled through Change Management. The bidder will be only responsible for the data exchange in standard formats like ODBC, OPC & XML etc. Kindly confirm the same. | Bidder to comply TS. |
|  |  | II, Part 1, 1.8.1.b Page No.: 16 |  | OEM(s) shall also provide all the requisite assistance to the Contractor for project completion, warranty & AMC. | This is understood that in case of any obsolescence or non-compatibility to maintain SLAs with any of the existing parts (not the part of the proposed RFP) and in case of any requirement of replacement and procurement of new Product will be taken care through Change management process by the the purchaser. Kindly confirm the same. | Bidder to comply TS. |
|  |  | II,Part 2, 7.8.1. Page No:123 |  | Factory acceptance Test (FAT): The database, displays and the report formats developed by the contractor for the UNMS system under the scope shall be demonstrated and verified by the Employer/Owner before factory testing. | Please confirm if one of the Main UNMS Data Centre/Backup UNMS Centre be conidered for conducting FAT | Bidder to comply TS. |
|  |  | II, Part 2, 2.2 ,Page No:25 |  | 2.2.Design Requirements for UNMS Applications : d) Supplied U-NMS system application shall support north bound CORBA/XML/ Q3/SNMP or any other acceptable open standard interface for ensuring integration with other existing/upcoming U-NMS of similar nature. | Kindly confirm regarding the upcoming EMS/NMS ( Are these planned during the project duration of U-NMS implementation or later) | Bidder to comply TS. |
|  |  | II,Part 2, 7.8.1.2, Page No:125 |  | 7.8.1.2. Functional Performance Test: i) Verification of data link interfaces with other technology eg, MPLS, VSAT, Radio, Cellular etc. | We understanding that PGCIL will provide MPLS/VSAT/Radio/cellular for verfication of data link interface. Kindly confirm | Bidder to comply TS. |
|  |  | VOL-II PART-A Sec-3 Page 3 of 16 VOL-II PART-A Sec-3 Page 4 of 16 |  | 3.4 Philosophy of Maintenance Services The Contractor’s engineer shall carry out the first level of network management and maintenance. 3.4.2 Management of U-NMS Services iii. Contractor team shall be supporting the Employer/Owner for trouble shooting of issues/downtime of Application for bringing up the application with minimum down time. | As per these two clauses, the first level activities will be handled by Employer or owner and contractor team will assist them in trouble shooting or provide support for day to day basis activities. Please confirm. | Bidder to comply TS. |
|  |  | VOL-II PART-A Sec-3 Page 3 of 16 |  | 3.4.1 General Requirement for maintenance v. Technical assistance/support of the network including 24 x 7 remote assistance, On-line Assistance, On-site Support etc. | SI understands that monitoring of the network will be handled by Employer or owner. Contractor will handle/provide technical support remotely. Please confirm. | Bidder to comply TS. |
|  |  | VOL-II PART-A Sec-3 Page 4 of 16 |  | 3.4.1 General Requirement for maintenance ix. Integration of NEs/NMSs during the AMC period. x. Support for integrating system as mentioned in the scope. | All the new integration or adhering support to be handled by existing resources only. Please validate our understanding. | Bidder to comply TS. |
|  |  | VOL-II PART-A Sec-3 Page 4 of 16 |  | At UNMS Center: i. L1 Support: o The support personnel (1 no. in each shift) shall be available round the clock (in 3 shifts) at Employer’s/Owner’s Main UNMS Centre on 24X7 basis 365 Days. | SI understands that the manpower to be diputed at Main UNMS should be 24x7x365 days, which implies 4.5 or 5 resources to be deployed if SI will consider 40 hours per week working shift for single resource. In any case, any SI needs to cater 5 resources to adhere this clause. Please provide your concern. | Bidder to comply TS. |
|  |  | VOL-II PART-A Sec-3 Page 4 of 16 |  | At UNMS Center: i. L1 Support: o One person at all state control center 365 days from 9:00 am to 6:00 pm. o One person shall be deployed at Employer’s/Owner’s Backup UNMS center 365 days from 9:00 am to 6:00 pm. | SI understands that the manpower to be diputed at State Control Centre should be 9 to 6 (7 days week) x for all 365 days, which implies 2 resources to be deployed if SI will consider 40 hours per week working shift for single resource at site. In any case, any SI needs to cater 2 resources to adhere this clause. Please provide your concern. | Bidder to comply TS. |
|  |  | VOL-II PART-A Sec-3 Page 5 of 16 |  | The Contractor shall perform audit of the U-NMS system and Applications (preferably in the 3rd Quarter of every year) and the report shall be submitted to the Employer/Owner within fifteen (15) days. | We understand that the audit will be handled by all the existing resources of contractor being deployed in State control centre and main UNMS sites. No additional resource will be required for this activity Please confirm. | Bidder to comply TS. |
|  |  | VOL-II PART-A Sec-3 Page 6 of 16 |  | 3.4.4.1. Preventive Maintenance, Updates & Upgrades: i. The Contractor shall do the regular monitoring of U-NMS related issues on 24X7 basis | We understand that the monitoring of the network will be carried out by the existing resource/resources of contractor being deployed in State control centre in different shifts (one resource per shift). Please validate the understanding | Bidder to comply TS. |
|  |  | VOL-II PART-A Sec-3 Page 8 of 16 |  | 3.4.6 Spares Management Contractor shall undertake appropriate planning for the storage of spares at strategic locations/ store depots on its own to meet the performance criteria. | The space for spare storage will be provided by Customer/onwer/Employer and Contractor will able to use the employer's premises for the same. | Bidder to comply TS. |
|  |  | VOL-II PART-A Sec-3 Page 13 of 16 |  | Deduction of 2% of the apportioned price of the apportioned quarterly AMC for every 0.5% or part there of decrease in availability under 99.9%. (Maximum amount of deduction is limited to 100% of AMC charges) | The penalty Cap is defined hereby unlimited ( 100% upto the maximum level) which is not as per global and industry standard. Please make the penalty capping to 10% of the value pertained in any month. | Bidder to comply TS. |
|  |  | Vol-II APPENDIX A1 |  | EXISTING/ UPCOMING NMS INFRASTRUCTURE | NMS/EMS Software Versions are not provided for some Vendors (OEMs). Also, Equipement Type is not mentioned. Pl Clarify. | Bidder to comply TS. If needed, Details in addition to TS may be collected by the Bidder on their own. |
|  |  | Vol-II Hardware APPENDIX C1 Page-1 |  | Hardware | Database Server not mentioned in BoQ. Pl Clarify | Delivered System shall meet the functionalities as per requirement of TS. Bidder to comply TS |
|  |  | Vol-II Hardware APPENDIX C1 Page-1 |  | 1. WORK STATION Console dual 24'' for state | Is workstation with 2 Monitors? | Yes. Bidder to Comply TS |
|  |  | Vol-II Software APPENDIX C1 Page-1 |  | 9. BACKUP & RESTORE SOFTWARE | Software Specification for BACKUP & RESTORE SOFTWARE not provided. Pl Clarify | Bidder to comply TS. |
|  |  | Vol-II Software APPENDIX C1 Page-1 |  | 10. HOT BASED IDS FOR ALL MACHNIES | Software Specification for HOT BASED IDS FOR ALL MACHNIES SOFTWARE not provided. Pl Clarify. | Bidder to comply TS. |
|  |  | Vol-II Software APPENDIX C 1 Page-1 |  | 15. IDENTITY AND PATCH MANAGEMENT SOFTWARE | Software Specification for IDENTITY AND PATCH MANAGEMENT SOFTWARE not provided. Pl Clarify. | Bidder to comply TS. |
|  |  | Vol-II Software APPENDIX C1 Page-1 |  | 17. SOFTWARE ADAPTERS FOR NETWORK ELEMENT | Is this line item referring to Adapter to integrate directly with NE? Pl Clarify | yes. Bidder to Comply TS |
|  |  | Vol-II Software APPENDIX C 1 Page-1 |  | 20. SOFTWARE FOR SAN & NAS STORAGE | Appliance for SAN & NAS Storage already provided in Hardware Section. What this line item referring to ? Pl Clarify | Bidder to comply TS. |
|  |  | Vol-II Appendix- C Page 1 of 2 |  | Hardware Servers & accesorries SAN System | Qty mentioned is 2 for Main & 2 for Backup. As per indsustry practice, Qty 2 is NOT required. In our considered opinion, the Quantity should be 1. The redundant Servers & SAN Switches would be connected to the same SAN Storage. Please clarify. | Bidder to comply TS. |
|  |  | Vol-II Clause 18 Appendix C Page 1 of 2 |  | Software NMS & Element Manager-Software | Qty mentioned is 1 LOT in Manin DC only. Neither is the need for redundancy stated for the DC nor is it shown as a Requirement in DR. This would result in a Single Point of Failure Please clarify the approach when Main DC is down, as to how the DR would run, without NMS & Element Manager-Software. | Bidder to comply TS. |
|  |  | Vol-II Clause 18 Appendix C Page 1 of 2 |  | Hardware NMS & Element Manager-Hardware | Qty mentioned is 1 LOT in Manin DC only. Neither is the need for redundancy stated for the DC nor is it shown as a Requirement in DR. This would result in a Single Point of Failure Please clarify the approach when Main DC is down, as to how the DR would run, without NMS & Element Manager-Hardware. | Bidder to comply TS. |
|  |  | Vol-II Firewall Appendix C Page 2 of 2 |  | Firewall | Specification provided for Firewall is same is for Server Location and State Location. As traffic need will be far less in state location, lower specification can be used at state location. The Project Cost goes significantly up, without any gain on the investment. It would increase the OPEX cost, in terms of the Power required. PGCIL may like to reconsider the Capacity. | Bidder to comply TS. |
|  |  | Vol-II Clause 15 Appendix D Page 17 of 21 |  | 15. LAN Switch 6. Switching capability Layer-3 switching & VLAN | You may like modify the clause to read as "Layer-3 switching & VLAN, VOQ with minimum 2Gb buffer to eliminate HOL blocking". Virtual_Output_Queuing is industry standard technology in data center switches that helps eliminates head-of-line blocking issues minimizing congestion in critical network. https://en.wikipedia.org/wiki/Virtual_output_queueing | Bidder to comply TS. |
|  |  | Vol-II Clause 15 Appendix D Page 17 of 21 |  | 15. LAN Switch 6. Switching capability Layer-3 switching & VLAN | You may like modify the clause to read as "Rack mountable, redundant hot-swappable power supply and fans. Must be from Data Center portfolio supporting IEEE standards based EVPN VXLAN Type 1, 2, 5,6,7 route types". Data Center (DC) grade devices should have redundant fans and power supplies for resiliency and DC grade high availability. IEEE EVPN VXLAN is the defacto choice for all DC fabrics and is supported by all leading DC switching OEMs | Bidder to comply TS. |
|  |  | Vol-II Clause 16 Appendix D Page 17 of 21 |  | 16. SAN (Storage Area Network) based storage or any other specialized storage solution | 4. Capacity: Minimum usable capacity of 50 TB, in our considered opinion, is HIGH for the size of the Network under consideration. The Project Cost goes up significantly, without any gain on the investment. It would increase the OPEX cost, in terms of the Power required. PGCIL may like to reconsider the Capacity. In our assessment 40 TB would be more than sufficient. | Storage requirement is given in TS. Bidder to comply TS. |
|  |  | Vol-II Clause 16 Appendix D Page 18 of 21 |  | 16. SAN (Storage Area Network) based storage or any other specialized storage solution | 10. Hard Drive speed 10000 or more rpm if applicable based on Historian Solution: A combination of Highspeed a Low speed to the industry practice. You may like to modify the Clause to read as: "10. Hard Drive speed: 40 TB (16TB SAS 15K RPM and 24TB SAS 10K RPM for Data Archiving) | Bidder to comply TS. |
|  |  | Vol-II Clause 17 Appendix D Page 18 of 21 |  | 17. Network Attached Storage (NAS) | 4. Capacity Minimum usable capacity of 10 TB, in our considered opinion, is HIGH for the size of the Network under consideration. The Project Cost goes significantly up, without any gain on the investment. It would increase the OPEX cost, in terms of the Power required. PGCIL may like to reconsider the Capacity. In our assessment 4 TB would be sufficient. | Storage requirement is given in TS. Bidder to comply TS. |
|  |  | Vol-II Clause 18 Appendix D Page 18 of 21 |  | 18. Tape Library (NAS) | 7 Capacity: Minimum 18 TB, in our considered opinion, is HIGH for the size of the Network under consideration. PGCIL may like to reconsider the Capacity. In our assessment 10 TB would be sufficient. | Storage requirement is given in TS.Bidder to comply TS. |
|  |  | Vol-II Backup Control Center Appendix K page 2 |  | Typical Network Architecture: BACKUP CONTROL CENTRE | Router shown in figure is not redundant but Qty of two (2)mentioned in BoQ indicates redundancy is required. Pl clarify which one is correct? | Diagram in only indicative, redundancy is required. |
|  |  | Vol-II Backup Control Center Appendix K page 2 |  | Typical Network Architecture: BACKUP CONTROL CENTRE | Firewall shown in figure is not redundant but Qty of two (2)mentioned in BoQ indicates redundancy is required. Pl clarify which one is correct? | Diagram in only indicative, redundancy is required. |
|  |  | Vol-II Backup Control Center Appendix K page 2 |  | Typical Network Architecture: BACKUP CONTROL CENTRE | If the answer to query # 28 above on Firewall is two (2), then accordingly the LAN Switches should be six (6) in Backup Control Center also. 2 Nos of Layers 3 Switch and 4 Nos of Layer 2 Switch. Please confirm this requirement. | Bidder to quote as per Bid Price Schedule. |
|  |  | Vol-II Main Control Center Appendix K page 1 |  | Typical Network Architecture: MAIN CONTROL CENTRE | The Architecture shows 2 External Firewalls and 2 Internal Firewalls. TEC GR calls for demonstration "High Availability during Link Failure". Should compliance of this Feature be required then the number of LAN Switches required would be 6 (six). The BOQ in the Tender asks for 2 (two) LAN Switches only. In our considered opinion "High Availability during Link Failure", is an essential feature for High Availability in any Data Center. This is the Industry practice also. We, therefore, request you to increase the quantity of LAN Switches to 6 (six). Nos of Layers 3 Switch and 4 Nos of Layer 2 Switch. Please confirm this requirement. | Bidder to quote as per Bid Price Schedule. |
|  |  | Vol-II PART B clause 1.1 Section 1 page 4 |  | Network Element (Any device i.e. Communication Equipment such as SDH,MPLS, PDH, DC Power Supply etc. communicating with UNMS system on SNMP or any Industry standard protocol) Data Acquisition | Is direct integration with NEs required ? Are there any NEs which are not managed by any of the NMS/EMSs? | Yes. The details are provided at Appendix-A. Bidder to comply TS. |
|  |  | Vol II PART B clause 1.1 Section 1 page 4 |  | Network Status Processor | Need some samples use cases to understand this requirement | Bidder to comply TS. |
|  |  | Vol-II PART B clause 1.1 Section 1 page 4 |  | Sequence of Event Recording | Need some samples use cases to understand this requirement | Bidder to comply TS. |
|  |  | Vol II PART B clause 1.1 Section 1 page 4 |  | Manual data entry | Need some samples use cases to understand this requirement | Bidder to comply TS. |
|  |  | Vol II PART B clause 1.1 Section 1 page 4 |  | Remote configuration of NEs | Need some samples use cases to understand this requirement | Bidder to comply TS. |
|  |  | Vol-II PART B clause 1.3 Section 1 page 8 |  | (b) Calculation | Need some samples use cases to understand this requirement | Bidder to comply TS. |
|  |  | Vol-II PART B clause 1.3 Section 1 page 8 |  | (d) Sequence of events data from NEs and connected UNMS/NMS/EMS, (e) NMS applications | Is it the same as receiving the unsolicited events / traps from the network and processing them?. If so how is this different from (a) Real-time/ telemetered. Needs some sample use cases for both to understand the differences? | Sequence of events (SoE) data is the series of event in sequence occuring due to any event. |
|  |  | Vol-II PART B clause 1.3 Section 1 page 8 |  | (f) Stored data | Need some samples use cases to understand this requirement | Bidder to comply TS. |
|  |  | Vol-II PART B clause 1.6 Section 1 page 13 |  | The ISR System shall capture raw production data in real-time, at its original scan rate from system such as Network resource management, fault management, performance management, trouble ticketing etc. and the same shall be submitted for approval during detail engineering. The raw data can be captured either by exception or periodically. The ISR System shall be a COTS (Commercial off the Shelf) product and shall provide user-configurable graphical visualization, reporting and analysis. It shall display current and past operating conditions on desktops anywhere and anytime throughout the enterprise and beyond. It shall store the information online for all data for 1 years and 6 years offline at its original resolution making it instantly available for deep and broad analysis, trending and bench marking for continuous processes improvements. The ISR System shall provide operators, engineers, and management with direct access to one integrated source of information. ISR system shall provide provision of insertion of future values in Historian. | The mentioned ISR system requirements can be supported together with the manamagement functional and non-functional related requirements in the proposed UNMS solution. No separate ISR system is required as part of the proposed UNMS. Hence, suggest to remove requirement of ISR sytem. | Bidder to comply TS. |
|  |  | Vol-II PART B clause 1.7 Section 1 page 17 |  | The Programming Development System (PDS) shall be supplied at UNMS Centre. Many of the development system requirements are defined by reference to the corresponding system requirements in the Specification. When requirements are defined by reference, the development system shall meet relevant requirements of the referenced section and all subsections to that referenced section. | Usually in Test & Development system, Application software customized/developed, tested, integrated as per RFP requirement. Further, it is offereed for User Acceptance Test before software is deployed in Field/ Production. But PDS system asked here with basic UNMS hardware & Software supplied in advance with FAT befoe supplying system. Is our understanding correct? | Confirmed |
|  |  | Vol-II PART B clause 1.1.1.2 Section 1 page 5 |  | The entire system data shall be auto discovered periodically as per frequency provided at relevant Appendices of the specifications, by exception and on demand. | What is the expectation on discovery by exception? | This is provided at Appendix-E |
|  |  | Vol-II PART B clause 1.1.1.3 Section 1 page 5 |  | Status data shall be reported by exception from the NMS/EMS/NEs and shall be updated and displayed within 4 seconds at UNMS Centre in worst case. A complete scan of all status data from the NMS/EMS/NEs shall be made by exception. | Need clarity on "report by exception" and "scan of status data by exception". | Status data shall be reported whenever there is change in the status of underlying NMS/EMS/Nes. |
|  |  | Vol-II PART B clause 1.1.1.5 Section 1 page 6 |  | (c) Inhibit automatic failover of communications | Need some samples use cases to understand this requirement | Bidder to comply TS. |
|  |  | Vol-II PART B clause 1.1.1.5 Section 1 page 6 |  | (d) Inhibit automatic fail-back of communications. | Need some samples use cases to understand this requirement | Bidder to comply TS. |
|  |  | Vol-II PART B clause 2.2 Section 2 page 5 |  | d) Supplied U-NMS system application shall support north bound CORBA/XML/ Q3/SNMP or any other acceptable open standard interface for ensuring integration with other existing/upcoming U-NMS of similar nature. | What are existing systems currently available for integration? Also specify what information shall be exchanged ? | Bidder to comply TS. |
|  |  | Vol-II PART B Clause 2.2 Section 2 page 5 |  | f) The supplied UNMS system application shall be able to exchange data with the supplied Information Storage & Retrieval (ISR) system/Historian system for all type of data envisaged in the specifications. | What is the purpose of ISR System? Is it like a data lake where all data is exported from proposed UNMS system and shall be used by 3rd Party systems for analysis? | ISR system shall export data from proposed UNMS system and store it for the time period as specified in the TS . All analysis for past data shall be done in ISR system. |
|  |  | Vol-II PART B clause 2.2 Section 2 page 5 |  | g) The UNMS system application shall have capability for integration and open APIs shall be provided for the integration with Employers other systems such as Billing system, GIS system, ERP system and IT systems. | Which BSS, GIS & ERP Systems are currently deployed? | There is no BSS, GIS & ERP system currently to be integrated, However, The delivered system should have the capability to integrate BIS, GIS, ERP and IT system, if required. |
|  |  | Vol-II PART B clause 2.6 Section 2 page 35 |  | An IT infrastructure is envisaged at each UNMS server location to enable publishing various applications such as Web portal System, Trouble ticketing etc. to be used by while on site. Other applications like DNS, Email servers etc. are also to be placed within this setup. Different zones shall be created for hosting different applications within this setup for ensuring system security. | No servers are mentioned for DNS, Email Applications. Pl clarify | SMS/E-mail Escalation Software licence for all UNMS modules is part of BoQ. Bidder to comply the TS. |
|  |  | Vol-II PART B clause 2.3.1 Section 2 page 5 |  | System shall integrate with EMS (element management systems)/NMS (Network Management Systems)/ NE (Network Elements such as SDH, PDH, DCPS etc.) to capture network inventory. Redundant communication channels shall be provided between UNMS System (UNMS Centre) and NEs/underlying NMS/EMS. If valid data cannot be acquired from one of the NEs/NMS/EMS, the UNMS System shall automatically failover to the backup Communication channel. A communications failure shall not cause a server failover. The backup communications channel shall be tested periodically up to NE, without manual intervention, to determine its readiness to take over upon failure of the primary channel. | Is direct integration with NEs required ? Are there any NEs which are not managed by any of the NMS/EMSs | Yes. Bidder to Comply TS |
|  |  | Vol-II PART B clause 2.3.1 Section 2 page 6 |  | a) Integration with other Existing Inventory Management Systems, if exists. b) Importing from Excel files | Is there any existing inventory systems which are to be integrated, If yes, what is the system and what kind of data does it have at present | Bidder to Comply TS |
|  |  | Vol-II PART B clause 2.3.2 Section 2 page 6 |  | The communication system model to be used by the application shall reflect present conditions of network as reported by EMS/NMS/NEs, ICCP/ other system data Exchange from connected Control Centres and as entered by the users. The Communication System Model Update (CSMU) function shall also include the following features, e.g. communication network model of STM 4/16 topology comprising of various communication rings/ radial branches. This topology and the associated model parameters shall be based on: (1) Telemetered switching/ node/ NE device statuses, (2) manually entered device statuses, (3) manually entered in-service or out-of-service designations for modelled elements. (4) manually entered modelled elements, e.g. SDH/PDH/DCPS/NMS etc. | What does ICCP/other system data exchnage refer to ? | ICCP refer to data exchange protocol between Control Centres. |
|  |  | Vol-II PART B clause 2.3.2 Section 2 page 6 |  | 3) Execute state estimation & System analysis functions for the Communication system using the nominal value or the typical network save case scenario of the regional communication network, with the entire regions/ states node, traffic, latency etc. | Needs clarification to understand the requirement | This is same as trending and analysis |
|  |  | Vol-II PART B clause 2.3.4 Section 2 page 14 |  | 17) The system shall obtain the related equipment asset/inventory information and related operation personnel information, add the inventory information into the alarm information and display the contact information in the FMS window. Thus, the monitoring personnel can timely notify the related personnel of these faults and the operation personnel can perform troubleshooting rapidly. | Is there an existing source which needs to be integrated for getting operation personnel information? | No. Bidder to Comply TS |
|  |  | Vol-II PART B clause 2.3.4 Section 2 page 14 |  | 18) Working together with the related external network association model database, the system should be able to analyze and locate the cross-network alarm for intra-network and cross network faults. | What the does the word external network association model database here refer to?. Is it any existing system already in the operator in environment?, If yes, what is the system | External network is the inter-regional or cross border links connected with ER. |
|  |  | Vol-II PART B clause 2.3.4 Section 2 page 14 |  | 24) The system shall generate alarm for any synchronization issue. It should also report for services affected due to synchronization in network. | "It should also report for services affected due to synchronization in network." - This requirement is assumed as follows. Pl Clarify System shall report that the connectivity with a particular NMS/EMS is affected | System shall report for services affected due to any sync issue in the network. |
|  |  | Vol-II PART B clause 2.3.4 Section 2 page 15 |  | 30) The “terminated” alarms shall be exported to a database for further user-defined processing. | What does the term "terminated" alarm mean here?. Need a discussion or sample use case for understanding | The terminated alarms are alarms which have been closed. |
|  |  | Vol-II PART B clause 2.3.4 Section 2 page 17 |  | 52) The system shall be able to compute the RCA and related SLA within 3 minutes from receiving the alarms for at least 95% of alarms received. | Understanding the term SLA as SIA. Is that understanding right ? | SLA is Service level agreement which in turn refers to availability responsibilities. |
|  |  | Vol-II PART B clause 2.3.5 Section 2 page 18 |  | iv) Redundancy Requirement | Needs clarification or sample use case for understanding | Redundancy requirement here refers to predicting unprotected channels. |
|  |  | Vol-II PART B clause 2.5.3.1 Section 2 page 31 |  | iv. The System shall provide User account expiry date. It shall be set/modified to the required number of days, once the number of days set for the user account exceeds, the user will not be allowed to log in to system as the user status will be changed as "user Expired". Configuration for the user Expiry shall be enabled or disabled accordingly. | System shall have the capability to integrate with Employer LDAP to support this functionality. Is our understanding correct? | Bidder to comply TS. |
|  |  | Vol-II PART B clause 2.5.3.1 Section 2 page 32 |  | xiii. The contractor may require to integrate with existing LDAP/AAA of Employer within its network else may provide separate servers to install these (AAA & LDAP) functionalities. | Clause is contradictory with Vol II, PART B, 2.5.3.1 (xi). Pl clarify | Bidder to comply TS. |
|  |  | Vol-II Part B clause 2.5.3.1(xi) Section 2 Page 32 of 38 |  | The existing Communication nodes & EMS/NMS shall be integrated with AAA/RADIUS server being supplied under this contract. | AAA/Radius Server not in BoQ. Since these contribute significantly to the cost of the Project it should be a Line item in the Commercial Price schedule, for fair commercial evaluation of the Tender. | Bidder to comply TS. |
|  |  | Vol-II PART B clause 2.5.4 Section 2 page 33 |  | 1) The supplied system to be certified & tested as per relevant contemporary Indian or International Security Standards e.g. IT and IT related elements against ISO/IEC 15408 standards, for Information Security Management System against ISO 27000 series, Telecom and Telecom related elements against 3GPP security standards, 3GPP2 security standards etc. from any certified lab identified by the Government of India. | Any one certification against ISO/IEC 15408 or ISO 27000 series or 3GPP security standards, 3GPP2 security standards is enough? | It will be as applicable as per relevant standards of cyber security and GOI guidelines being issued time to time |
|  |  | Vol-II PART B clause 2.5.4 Section 2 page 34 |  | 9) The product's appliance is highly scalable, supporting (for example) 3000 concurrent SSH sessions, 1500 concurrent RDP sessions, or 2000 concurrent connections of mixed SSH and RDP regardless of which form factor (physical or virtual) is used. The product adds scale by simply adding new appliance to a cluster. | Current Network Count is 1800 and need to dimension for additional 200% capacity. Is there a need for such as high number concurrent sessions? Pl clarify | Bidder to Comply TS |
|  |  | Vol-II Part B clause 2.6.1 Section 2 Page 36 of 38 |  | Reverse proxy: To publish portal and applications on internet using reverse proxy server is to be supplied | Reverse Proxy not in BoQ. Since this contributes significantly to the cost of the Project it should be a Line item in the Commercial Price schedule, for fair commercial evaluation of the Tender. | Delivered System shall meet the functionalities as per requirement of TS. Bidder to comply TS |
|  |  | Vol-II PART B clause 3.2 Section 3 page 5 |  | Identity Manager | Requirement provided as part Identity Manager shall be supplied by line item IDENTITY AND PATCH MANAGEMENT SOFTWARE in Appendix C - BoQ of UNMS. Pl clarify | Confirmed. Bidder to comply TS. |
|  |  | Vol-II PART B clause 4.4.2 Section 4 page 6 |  | Image Backup and Restoration Utility | Backup / Restore utility is not in BoQ | Backup and Restore Software is part of BoQ. Bidder to comply the TS. |
|  |  | Vol-II PART B clause 4.4.3 Section 4 page 6 |  | Web based “Document Management System” (DMS) software shall be supplied and installed at the owner’s facility by the contractor along with minimum 100 number of client access licenses and minimum 50 concurrent users. | No mention of Document Management System in Appendix C - BoQ of UNMS. Pl clarify | Delivered System shall meet the functionalities as per requirement of TS. Bidder to comply TS |
|  |  | Vol-II Part B clause 4.4.3 Section 4 Page 6 of 14 |  | Document Management System | Document Management System not in the BoQ. Since this contributes significantly to the cost of the Project it should be a Line item in the Commercial Price schedule, for fair commercial evaluation of the Tender. | Delivered System shall meet the functionalities as per requirement of TS. Bidder to comply TS |
|  |  | Vol-II Part B clause 4.4.4 Section 4 Page 6 of 14 |  | Through OPC Server: A full OPC server compliant to the latest standard shall be provided in order to export real time data, alarms, historical data etc. to the external system. OPC clients for WINDOWS and Linux shall also be supplied. | OPC Server is not in the BoQ. Since this contributes significantly to the cost of the Project it should be a Line item in the Commercial Price schedule, for fair commercial evaluation of the Tender. | Servers compliant to OPC protocol to be supplied as per requirement of TS. |
|  |  | Vol-II PART B clause 5.3 Section 5 page 6 |  | a.The servers shall be sized such that its processing capacity utilization should not exceed 25% of total processing capacity at peak load. | With 25% utllization, server sizing will be more. Suggest to increase to 60-75% utilization to reduce overall hardware cost | Bidder to comply TS. |
|  |  | Vol-II PART B clause 5.3 Section 5 page 7 |  | d.Blade Servers: Servers shall be accommodated in (8/16) slot chassis of mounting in rack (panel) and a rack mountable TFT monitor, keyboard and mouse using IP Based KVM switch to access all servers & peripherals in the panel. | Do we need to propose rack mountable servers or Blade Servers? Pl clarify | Bidder to comply TS. |
|  |  | Vol-II Part B clause 5.3 Section 5 Page 6 of 15 |  | a. The servers shall be sized such that its processing capacity utilization should not exceed 25% of total processing capacity at peak load. | As per Industry Standards, sizing the Hardware Platform keeping the idle capacity at 75%, is a waste of Computing power. The Tender also asks for sizing the Hardware sizing for additional 200% Network Expansion; or total 300% Capcity. 200% Additional Network Expansion has the potential to call for atleast doubling the computing power. Which in other words mean that, with the ask of 25% utilization, the utilization in the initial years would be as low as 12.5%. You would appreciate that 12.5% Utilization is too low a capacity utlization by any standards. We, therefore, request you to change 25% Utlilization to 50% Utlilization. | Bidder to comply TS. |
|  |  | Vol-II PART B clause 5.5.4 Section 5 page 11 |  | Protection System) functionality shall not be coupled with the Firewall solutions, which shall be integrated to detect and prevent intrusion, worm, virus etc. Definition updates for virus, signatures, software patches etc. shall be done up to AMC period. It is required that the firewalls (Internal) and Unified Threat Management (UTM) (External) are supplied from two different manufacturers | Does this mean a separate NIPS is expected ? i.e. Firewall and NIP separate appliances. Prices of the same to be combined & provided as FIREWALL line item in Appendix C - BoQ of UNMS. Pl clarify | Dedicated NIPS appliance and IPS functionality shall be provided inbuilt in the Firewall as per requirement of TS. |
|  |  | Vol-II Part B clause 5.5.4 Section 5 Page 10 of 15 |  | Intrusion Detection and Prevention System (IDPS): The contractor shall provide an intrusion detection and prevention system, to have a dedicated NIPS (Network Intrusion Protection System) appliance and the IPS (Intrusion Protection System) functionality shall not be coupled with the Firewall solutions, which shall be integrated to detect and prevent intrusion, worm, virus etc. Definition updates for virus, signatures, software patches etc. shall be done up to AMC period. It is required that the firewalls (Internal) and Unified Threat Management (UTM) (External) are supplied from two different manufacturers | BoQ contains line item Firewall with IDPS & clause mentions IDPS not to be decoupled with Firewall solution. DRS contains Firewall with IDPS. Its contradictory. Pl clarify | Dedicated NIPS appliance and IPS functionality shall be provided inbuilt in the Firewall as per requirement of TS. |
|  |  | Vol-II PART B clause 5.6.1 Section 5 page 11 |  | The switch shall be provided with fibre cables/ cat 5e/6 cables of appropriate lengths for all active ports / switch ports as to connect to servers and SAN storage. | SAN Switches are not in Appendix C - BoQ of UNMS. Are SAN swithes part of SAN system line item in BoQ? Pl clarify | Confirmed. Bidder to comply TS. |
|  |  | Vol-II Part B clause 5.6.1 Section 5 Page 11 of 15 |  | SAN Switches: The switch shall be provided with fibre cables/ cat 5e/6 cables of appropriate lengths for all active ports / switch ports as to connect to servers and SAN storage | SAN switch is not in the BoQ. This is a commercially expensive item; has the potential to be as high as 4-5% of the overall Project Cost. However, it finds no mention neither in the BOQ nor in the DRS for Hardware. 1. Please provide the specification in the DRS. 2. Please provide a separate line item in BoQ/Price schedule | 1. Bidder to propose SAN as a system as per requirement of TS including SAN switch as required. 2. Bidder to comply TS. |
|  |  | Vol-II Part B clause 5.6.3 Section 5 Page 11 of 15 |  | Tape library shall be used for archiving of data available on SAN. It shall schedule the archiving activity. Based on the schedule, archiving activity shall be initiated automatically. | Tape Library is not in the BoQ. Since this contributes significantly to the cost of the Project it should be a Line item in the Commercial Price schedule, for fair commercial evaluation of the Tender. | Tape library to be proposed as part of storage requirement detailed in TS as required. Bidder to comply TS. |
|  |  | Vol-III Price Schedule Price.xls file row no.7,8,9 |  | Database software (DB) for all modules of SA & SF in both ER1 and ER2 | This is repeated for 3 rows, whereas it should be row 7 - DB row 8 - OS - row 9 Backup /restore software. Please provide us with revised price schedule. | Kindly refer Amendment-I |
|  |  | Vo-III Price Schedule |  | Color Lazer Printer | Most of these high end printers are manufactured out of restrictive region. Can the specifications be lowered in terms of reference to A3 specifcation. | Bidder to comply TS. |