## Clarification No. II
Clarification No.-II to the Bidding Documents for Substation Extension Package-SS69 for (i) 400/220 kV Muzaffarpur S/S extn including ICT, (ii) 400 kV Saharsa S/S extn, (iii) 400 kV Durgapur S/S extn and (iv) 400kV Kahalgaon S/S (NTPC) extn associated with Eastern Region Strengthening Scheme-XXIII. [Spec. No.: CC-CS/1010-ER1/SS-4083/3/G2]
Prebid Queries
Sr. No. | Reference | Clause | Description | Query | POWERGRID’s Reply/Clarification
400 (AIS) /220 kV (GIS) Muzaffarpur sub-station
1 | Section Project | Clause 3.1, V | One number 500MVA, 400/220/33kV 3-Phase Auto Transformers, | Please confirm whether parellel operation of 500MVA is envisaged. If yes, please provide the details of exisitng transformer. | Confirmed. ICT1 &2 : 400/220/33kV, 315 MVA ICT 3: 400/220/33kV, 500 MVA
2 | Section Project | Clause 3.1, X | Main Earthmat already exists in the switchyard area under present scope (existing Earthmat layout drawing is enclosed) | Existing Earthmat layout drawing is missing in tender documents. Please furnish the same. | Please refer clarification-I
3 | Section Project | Clause 3.1, XIV | ………….Augmentation of existing control panel (including meters, transducers, mimic etc. wherever required) is under present scope………. | Please provide the details of existing Control & Relay Panels s as to work out the augmentation requirement. | Make & model of existing panels are mentioned in section project. Detailed scheme shall be provided to successful bidder during detailed engg.
4 | Section Project | Clause 3.1, XV | Integration of Bays under present scope with NTAMC & RLDC:…. | Please provide details of existing SAS system (architecture drawings, BOM, etc) | As per section project clause 3.1 XV, Data to NTAMC shall be sent through RTU. Please refer annexure V of section project for details.
5 | Section Project | Clause 3.1, XVI | ..........Digital RTCC panel for ICT-IV is under present scope which also includes Digital RTCC relays for existing ICTs. These Digital RTCC relays are to be installed, commissioned for the existing 400/220kV ICT’s and their existing conventional RTCC is to be disintegrated/discarded........ | Please furnish details/drawings of existing RTCC Panels of Toshiba & BHEL make. | As per section project clause 3.1,XVI, "Digital RTCC panel for ICT-IV is under present scope which also includes Digital RTCC relays for existing ICTs. These Digital RTCC relays are to be installed, commissioned for the existing 400/220kV ICT’s and their existing conventional RTCC is to be disintegrated/discarded".
6 | Section Project | Clause 3.1, XVII | Extensions of HVW spray system and hydrant system for the transformer under present scope from the nearest hydrant point available for existing transformer (i.e ICT-I). | Please provide existing Hydrant sytem layout showing nearest hydrant point to tap. Or please provide approx. length of nearest hydrant point. | As per section project clause 3.1 XVII, nearest hydrant point available is for ICT-1 adjacent to ICT-IV under present scope. Please refer GA & bidder is advised to visit the substation site and acquaint themselves with the topography, infrastructure and also the design philosophy.
7 | Elec Drawings | GA Muzaffarpur Extn | GA Muzaffarpur Extn | Please provide section layout for Muzaffapur substation | GA & SLD drawing provided with tender. Section layout shall be developed & submitted by sucessful bidder during detailed engineering for approval. Bidder is advised to visit the substation site and acquaint themselves with the topography, infrastructure and also the design philosophy.
8 | Elec Drawings | SLD & GIS Layout | 400 220 kV Muzaffarpur SS Extn-SLD PGCIL-10032181-A02-01_R0_20150210_Layout | GIS bay arrangement in SLD & drawing PGCIL-10032181-A02-01_R0_20150210_Layout do not match. Please check & provide relevant drawings. | Drg no. PGCIL-10032181-A02-01_R0_20150210 of bidding document is layout of existing Hyosung GIS and same is to be referred only for GIS interconnection detail purpose.
400/220/132 kV AIS Saharsa sub-station
1 | Section Project | Clause 3.2.1, b) | ……………..necessary modification, wiring/cabling, shifting, installation and integration of same for completion of 400 Kv bus bar protections is under present scope. | Provide details of existing Bus Bar Protection | Make & model of existing panels are mentioned in section project. Detailed scheme shall be provided to successful bidder during detailed engg.
2 | Section Project | Clause 3.2.1, c) | …..contractor has to integrate and configure the control & protection system with existing Substation Automation System and update the system database for the 400kV bays under present scope…… …….present scope include augmentation of SAS including hardware and software for the bays under present scope as per Single line diagram...... | Provide details of existing Substation Automation Sytem | Make & model of existing SAS are mentioned in section project. Detailed scheme shall be provided to successful bidder during detailed engg.
3 | Section Project | Clause 3.2.1, e) | Dismantling & Shifting of PLCC system (carrier terminals, protection coupler (digital & analog), coupling device etc) from Kishanganj end and erection of same at Saharsa end for 400 kV D/C Saharsa –Darbhanga transmission line is under present scope of work. | Please confirm, Dismantling & Shifting of PLCC eqipments associted with both the circuits are included. Further, please provide details of existing PLCC equipments. | Confirmed. Bidder is advised to visit the substation site and acquaint themselves with the topography, infrastructure and also the design philosophy.
4 | Price Schedule | Sr. No. 89-94 | PLCC for Saharsa | As per Section Project, clause no., 3.2.1, e) Dismantling & Shifting of PLCC system (carrier terminals, protection coupler (digital & analog), coupling device etc) from Kishanganj end and erection of same at Saharsa end for 400 kV D/C Saharsa –Darbhanga transmission line is under present scope of work. Please confirm, the exact scope as PLCC equipments from Kishenganj existing ba to be shifted for Saharsa New Line Bays, aslo new equipments are included in BPS for Saharsa New Line Bays. | As clarified in section project, Kishanganj end PLCC shall be shifted and to be used for 400kV Saharsa-Darbhanga line and new PLCC equipments shall be utilised for 400kV D/C Saharsa-Kishenganj line after LILO.
5 | Section Project | Clause 3.2.3, a)-f) | Integration with the existing communication system | Existing communication details required | SDH Communication Equipment is still under implemantation at Saharsa S/s. Before Engineering, Site Survey may please be taken up for verifying site condition with respect to communication equipment as per contractual provision.
6 | Price Schedule | Sr. No. 73 | 420 kV, 4400 pF Capacitive Voltage Transformer (1-Phase)- 6 nos | SLD indicates CVT for each 400kV Line Bays. Accordingly quantity of 420 kV, 4400 pF Capacitive Voltage Transformer (1-Phase) shall be 12 nos instead of 6 nos. Please check & confirm. | Please refer amendment-II
7 | Elec Drawings | GA Layout Saharsa SS | 400-220-132kV GA-Saharsa | Please provide Electrical Layout Plan & section for Saharsa substation | GA & SLD drawing provided with tender. Section layout shall be developed & submitted by sucessful bidder during detailed engineering for approval. Bidder is advised to visit the substation site and acquaint themselves with the topography, infrastructure and also the design philosophy.
8 |  |  |  | Kindly provide the conductor details for incoming transmission line from Kishenganj & Darbhanga | Quad ACSR Moose
400 kV AIS Durgapur sub-station
1 | Section Project | Clause 3.3.4 | ……...Any other miscellaneous works like erection h/w, cables, wiring, integration etc arises due to replacement of circuit breaker & PLCC as mentioned above is also under present scope of work and deemed to be included under item “ERECTION H/W-MISC WORK”. | Please provide the layout drawings of existing Durgapura Substation to work out the misc. work included under scope. | Bidder is advised to visit the substation site and acquaint themselves with the topography, infrastructure and also the design philosophy.
2 | Section Project | Clause 3.3.5 | 3.3.5 Any modification in Control & Protection panel drawings (addition / modifications of CB signals) associated with Circuit Breakers under present scope. However, supply of new Protection IED/ BCU etc. are not envisaged under present scope. | Please provide the list of signal to be included for work under scope. Also details of existing CRP's required. | Make and model of existing panels are mentioned detailed augmentation scheme shall be developed and submitted by bidder during detailed engineering for approval.
3 | Section Project | Clause 3.3.7 a)-h) | Integration with the existing communication system | Existing communication details/drawings required. Please provide the same. | Corient 7080 SDH equipment is installed at Durgapur Substaion.
4 |  |  |  | Kindly provide the equipment connector detail for Durgapur S/S | Bidder is advised to visit the substation site and acquaint themselves with the topography, infrastructure and also the design philosophy.
400 kV AIS Kahalgaon (NTPC) sub-station
1 | Section Project | Clause 3.4.6 | ……...Any other miscellaneous works like erection h/w, cables, wiring, integration etc arises due to replacement of circuit breaker & PLCC as mentioned above is also under present scope of work and deemed to be included under item “ERECTION H/W-MISC WORK”. | Please provide the layout drawings of existing Durgapura Substation to work out the misc. work included under scope. | Bidder is advised to visit the substation site and acquaint themselves with the topography, infrastructure and also the design philosophy.
2 | Section Project | Clause 3.4.7 | 3.3.5 Any modification in Control & Protection panel drawings (addition / modifications of CB signals) associated with Circuit Breakers under present scope. However, supply of new Protection IED/ BCU etc. are not envisaged under present scope. | Please provide the list of signal to be included for work under scope. Also details of existing CRP's required. | Make and model of existing panels are mentioned detailed augmentation scheme shall be developed and submitted by bidder during detailed engineering for approval.
3 | Section Project | Clause 3.4.9 a)-f) | Integration with the existing communication system | Existing communication details/drawings required. Please provide the same. | Corient 7080 SDH equipment is installed at Kahalgaon Substaion.
4 |  |  |  | Kindly provide the equipment connector detail for Kahalgaon S/S | Bidder is advised to visit the substation site and acquaint themselves with the topography, infrastructure and also the design philosophy.
General
1 | Tender Documents |  |  | The SLD, overall layout plan and sectional drawings of Durgapur & Kahalgaon Substation is not available with the tender documents. The same shall be required for estimation of cables & hardwares. Request you to share the same. | Bidder is advised to visit the substation site and acquaint themselves with the topography, infrastructure and also the design philosophy.
2 |  |  |  | In reference to your above referred tender, we have a valid UAN registration, please confirm whether an exemption of EMD can be availed on the basis of MSME | The bidders are required to refer the provisions of bidding documents inter-alia ITB Clause 13.1, ITB/BDS, Vol-I which is amply clear in this regard.