## PGCIL Ext.
Clarification No.-I to the Bidding Documents for Substation Extension Package-SS69 for (i) 400/220 kV Muzaffarpur S/S extn including ICT, (ii) 400 kV Saharsa S/S extn, (iii) 400 kV Durgapur S/S extn and (iv) 400kV Kahalgaon S/S (NTPC) extn associated with Eastern Region Strengthening Scheme-XXIII. [Spec. No.: CC-CS/1010-ER1/SS-4083/3/G2]
S.No. | Description | Tender Document reference Clause no. & page no. | Clarification by Contractor | POWERGRID’s Reply/Clarification
QUERIES/CLARIFICATIONS FOR ELECTRICAL WORK
1. For 400/220kV Muzaffarpur substation extension:
1 | Vol II: Section-Project: | 3.1. X | Existing earthmat layout drawing for Muzzafarpur substation is not enclosed with tender documents as mentioned in the clasue 3.1 X of section project. Kindly provide the same. Also furnish the GIS hall earthing details for 220kV existing GIS hall | Earthmat is already existing in Muzaffarpur in 400kV AIS with spacing of 10MX10M. Earthing of GIS shall be done by the bidder as per their design. This shall be connected to main earthmat.
2 | Vol II: Section-Project: | 3.1. XVI | Kinldy provide existing RTCC scheme drawings for 400/220kV Muzaffarpur ICT bays. | As per section project clause 3.1 (XVI), "Digital RTCC panel for ICT-IV is under present scope which also includes Digital RTCC relays for existing ICTs. These Digital RTCC relays are to be installed, commissioned for the existing 400/220kV ICT’s and their existing conventional RTCC is to be disintegrated/discarded"
3 | BPS Schedule-I | (II). 16 & 18 | 400kV BPI support structures required as per tender layout are 3 nos however in BPS sr no (II).16 it is given as 6 nos. Similarly for 400kV High level BPI structures requred as per tender layout are 6 nos; wereas in BPS sr. no (ii) 18 it is mentioned as 3 nos. Kindly check & confirm. | Bidder to quote as per BPS
4 | Vol II: Section-Project: | 3.1 XIV | kindly provide scheme drawings for existing dupicate 400KV Bus bar protection scheme of M/s Reyroll make. Also provide details for 400 & 220kkV existing control panels & 220kV busbar protection scheme. | Make & model are mentioned in the section project. Detailed scheme drawing shall be provided during detailed engineering
5 | 400kV Autotransformer_R11 Dynamic Short Circuit Test requirement For 400 kV Class Auto transformer | 3.13,page 7 of 119 | We understand that Test Reports/certificate for Dynamic Short Circuit test to be provided with the Bid from any one of the qualifying Transformer manufacturer who meets the Technical Requirements as per tender. Kindly Confirm | Confirmed. However, as per clause 95 of Specific requirement Rev02, "Bidder / Manufacturer should have successfully carried out Dynamic Short Circuit test on 315MVA or above rating 400/220/33kV, 3-Phase Auto transformer as on the originally scheduled date of bid opening and shall enclose the relevant Test Report/certificate along with bid. In case bidder/manufacturer has not successfully tested 315MVA or above rating 400/220/33kV, 3-Phase Auto transformer for Dynamic Short Circuit test, their bid shall be considered technically non responsive. Further, design review of offered 400kV Class Auto transformer shall be carried out based on the design of short circuit tested 315MVA or above rating 400/220/33kV, 3-Phase Auto transformer."
6 | 400kV Autotransformer_R11 | Annxure K ANNEXURE - J ANNEXURE - L ANNEXURE - M ANNEXURE - N ANNEXURE - O ANNEXURE - P Annexure–Q | We undertand that follwing fitting and accessories not mentioned in price schedule so not be part of Supply with Transformer. Kindly confrim the same. 1. BDV Kit 2.Portable DGA Kit 3.Nitrogen Injection Type Fire Prevention & Extinguishing System 4.Oil BDV Test Set 5.Portable Dissolved Gas Analysis of Oil 6.Online Dissolved Gas (Multi-gas) and Moisture Analyser 7.On Line Dissolved Hydrogen and Moisture Monitor 8.On-line insulating oil drying system (Cartridge type) 9.Oil sampling bottles 10.Oil Syringe 11.Oil Storage Tank 12.Spare Transformer Unit Storage & Connection Arrangement | Confirmed. Bidder to quote as per BPS.
7 | General |  | Kindly confirm the availability & rating of existing EOT crane in 220kV GIS Hall. | EOT crane is available in 220kV GIS hall and its capacity is 5T
8 | General |  | We understand that there is no need for new lightning protection provisions to be done for our extension bay work at Muzaffarpur substation. Kindly confirm our understanding. | Lightning protection enivisaged with existing LM/Tower & sheild wire. However DSLP calculation to be done during detailed engineering for extension area under present scope.
2. For 400kV Saharsa substation extension:
8 | BPS Schedule-I | Sr. no (III). 73 | 420kV, 4400pF CVT (1ph) quantity for Saharsa substation extension work is mentioned in BPS as 6 nos. However as per our understanding the quantity of CVT should be 12 nos. Kindly confirm. | Same shall be incorpoarted in Amendment -II.
9 | Vol II: Section-Project: | 3.2.1 © | Kindly furnish detailed scheme drawings for existing ABB make Substation Automation System. | Make & model are mentioned in the section project. Detailed scheme drawing shall be provided during detailed engineering
10 | General |  | We understand that there is no need for new lightning protection provisions to be done for our extension bay work at Saharsa substation. Kindly confirm our understanding. | Lightning protection is enivisaged with sheild wire and DSLP calculation to be done during detailed engineering for extension area under present scope. Same is included under Erection hardware.
11 | General |  | As per Site visit it is noted that; the existing substaion work is still in its initial phase of site leveling. Hence all the details regarding existing switchyard need to be provided through approved layouts of agency at work. Kinldy furnish the details. | GA of Saharsa is already attached with bidding documents.
2. For 400kV AIS Durgapur substation extension:
12 | Vol II: Section-Project: | 3.3.5 | Kinldy provide existing Control & Protection shceme details for Durgapur 400kV substation. | Make & model are mentioned in the section project. Detailed scheme drawing shall be provided during detailed engineering
13 | Vol II: Section-Project: | 3.3.7 | In section - Project under scope of work for Durgapur extension substation; FO based communication equipment are mentioned; however there is no provision for any telecom equipments in the Bid Price Schedules. Kindly check & confirm the requirement. | Bidder to quote as per BPS
2. For 400kV AIS Kahalgaon substation extension:
14 | Vol II: Section-Project: | 3.4.7 | Kinldy provide existing Control & Protection shceme details for Kahalgaon 400kV substation. | Make & model are mentioned in the section project. Detailed scheme drawing shall be provided during detailed engineering
15 | Vol II: Section-Project: | 3.4.9 | In section - Project under scope of work for Kahalgaon extension substation; FO based communication equipment are mentioned; however there is no provision for any telecom equipments in the Bid Price Schedules. Kindly check & confirm the requirement. | Bidder to quote as per BPS
QUERIES/CLARIFICATIONS FOR CIVIL WORK
(i) 400/220 kV Muzaffarpur S/S extn including ICT
1 | Buried cable trench | Price schedule Civil works II- 36 | Requirement of PCC is mentioned in the price schedule but PCC is not shown in the typical section drawing, please clarify. | Item amended in BPS and Amendment No.II issued.
2 | Standard drawings | General | Please provide standard foundation drawings of the following: 1).Equipment support structures (400kV CT, 400kV ISO, 400kV BPI, 400kV HBPI & 220kV LA) 2). 500Mva, 400/220kV Autotransformer foundation | These drawings shall be provided to successful bidder during detailed engineering based on requirement of approved manufacturer drawing.
3 | Bus duct Foundation bolts | Price schedule Civil works II- 25 | We understand that foundation bolts required for bus duct support structure is also paid under respective unit item of foundation bolts in the price schedule, please confirm. | Payment shall be governed as per provisions of GIS module & its structure. Bidder has to quote as per BPS.
4 | Existing 220kV GIS building drawings | General | Kindly provide the following drawings forexisting 220kV GIS building for better understannding of scope. 1. Architectural drawing ( Plan,Elevation showing GIB openings & Sectional details) 2. GIS grade slab (showing embedment details for GIS) | Bidder may visit site to get acquainted with their requirement.
5 | Soil Report |  | Kindly provide the soil report inorder to identify the type of soil in the existing substation. | Soil report shall be provided to successful bidder during detailed engineering.
(ii) 400 kV Saharsa S/S extn
1 | Switchyard Panel room | Price schedule Civil works III- 99 Dwg- C/ENGG/CIV/SAH/PR/01 OF 04 | The size of panel room is 9m X 3.69m(33.2 sq.m) as per the standard drawing provided in tender document but in the price shcedule the quantity is mentioned as 81sq.m. Please confirm the dimensions of the panel room. | Drawings are indicative. Bidder has to quote as per BPS. Work shall be executed as per drawing released for construction, which will be issued to successful bidder.
2 | Contour survey report | General | Please provide the contour data report of the proposed area. | Contour data shall be provided to successful bidder during detailed engineering. However, bidder may visit site to get acquainted with site conditions.
3 | Filling Quantity | Price schedule Civil works III- 98 Dwg- C/ENGGE/SAHARSA/EXTN.400KV/GA/01 | The filling quantity of 164170 cum seems to be very high in the mentioned item of the price schedule for the present scope area as per the GA layout provided. Please check and confirm. | Bidder has to quote as per BPS.
4 | Test piles | Price schedule Civil works III- 93,95 | We understand that RCC , reinforcement, boring for the piles required for testing will also be paid under respective unit rate items . Please confirm. | Quantity involved for pile load test shall be paid under unit rate of test pile only.
5 | Standard drawings | Price schedule Civil works III- 86,87,88,89,90,103,100, 101 | Please provide standard drawings of the following: 1). 3.5m wide road works. 2). Drain section types A-A, B-B, C-C and D-D. 3). Stone pitching over sloping. 4). RCC culverts and Cable trench crossings. | Standard drawings are attached as Annexure-I.
COMMERCIAL QUERIES/CLARIFICATIONS
1 | Completion Period of 400kV Saharsa S/S extn (10.5 months) | 03-Section III BDS,page 20 of 21 | After site visit of Saharsa Substation , It has been obsered that existing substation work is in progrees and at very prelimanry stage. Furthermore, we have to extend the 400kV Busbars from existing switchyard and civil work is also huge for this Bay work. So we request you to please incerese the mentioned timelines for this Bay extension work which seems very less. Kindly Confirm | Provisions of bidding documents shall remain unchanged.
2 | Latent Defect Period | 6 Section V_SCC & GCC 22.2,22.8 | There is no latent defect period mentioned specifically for GIS Bay modules. Kindly provide the period for the same. Also we request you to please allow latent defect period of 3 years from the end date of DLP for all the Equipments/Materials from 5 years. | The bidders are required to refer the provisions of bidding documents inter-alia Clause 22.8.1, GCC/SCC, Vol-I which are amply clear in this regard.
3 |  |  | In this connection we would like to intimate you that, as per tender documents at Cl.No.5.5 & 13.1 of Section-II:Instructions to Bidders of the tender documents, it has been mentioned about exemption of submission of cost of bidding documents and bid security in case of MSE entrepreneurs. It is to bring to your kind notice that, we both the partners are in possession of MSME Certificates issued by Ministry of Micro, Small & Medium Enterprises, Govt. of India. Copies of our said certificates are enclosed herewith for kind perusal. Further to above, we are also registered with NSIC, a copy of our registration certificate is also enclosed for kind reference. We therefore, request you to kindly confirm us that, we are exempted for submission of cost of bidding documents and bid security w.r.t. the subject package...... | The bidders are required to refer the provisions of bidding documents inter-alia ITB Clause 5.5 & ITB Clause 13.1, ITB/BDS, Vol-I which are amply clear in this regard.

## 35 PR BSPTCL 2018 (hidden)
|  |  |  | Date: | 2018-07-30
Project | Construction of (2x200MVA+3x50 MVA) 220/132/33KV GSS, Thakurganj(District-Kishanganj) with SAS under Turnkey basis.
Client |  | Bihar State Power Transmission Company Limited.
Contractor |  | Bajaj Electricals Limited.
S.No. | Tender document reference | Clause no. & page no. | Clarification by Contratcor | Response by client | Remarks
1 | General Plot plan |  | Kindly request to provide the general plot plan of the substation area ( length & breadth).
2 | Soil Investigation report |  | Please provide the soil investigation report if avialable for proposed substation area inorder to quantiy the foundation works or Kindly provide safe bearing capacity to be considered at 1.5m below existing ground level.
3 | Contour map |  | Kindly request to provide the contour map for the proposed substation area if available.
4 | Location of site |  | As geotechnical investigation & foundation design is included our scope of work, we would like to do following in proposed substation plot inorder to estimate foundation quantity. 1. Preliminary topographical survey 2. Bore log In this regards, kindly request to provide the plot location of the proposed substation.
5 | Changes in site location |  | We undestand that in case of changes in site location during detailed engineering due to that if we have any impact in foundation type and sizes will be paid as additional to the contarctor, please confirm.
6 | Price schedule -civil works, FFPH building with rest room | sl no. 5-b | Kindly request to provide the area of rooms required to be placed at first floor of pump house building.
7 | Price schedule -civil works, landscaping | sl no. 20 | Kindly request to provide the area required for landscaping and provide the type of landscaping required.
8 | Vol-2D, Civil works, High flood level. | sl no. 25, Page no.12 | In order to finalize the finished ground level of proposed substation, kindly request to provide the highest flood level for proposed substation.
9 | Vol-2D, Civil works, retaining wall/Stone pitching. | sl no. 24-b, Page no.12. | As per mentioned clause, we understand that retaining wall is not required incase of filling less than 2m, whereas for filling up to 2m will required stone pitching slope protection , which will also paid as extra to the contarctor , please confirm.
10 | Vol-2D, Civil works, retaining wall. | sl no. 24-b, Page no.12. | As per mentioned clause, we understand that retaining wall is not required incase of filling less than 2m, whereas for filling above 2m will required same and paid as extra to the contractor as per bihar PWD schdule of rates, please confirm.
11 | Retaining wall and stone pitching |  | In case the above clarification sl no.9 & 10 will not paid additional to contartor, we kindly request to include the item for stone pitching & retaining wall for different heights ( 2m, 2.5, 3m , 3.5m etc.) in price schdule.
12 | Vol-2D, Civil works, Tower and equipment support structure - Galvanization thickness. | sl no. 15-b, Page no.5. | Kindly request to provide the minimum galvanization thickness for structural steel members.
13 | Vol-2D, Civil works, Tower structure - standard drawing. |  | Standard drawings for substation gantry and towers are not avialable in BSPTCL website, kindly request to provide 220kV, 132kV & 33kV tower and gantry GA drawings.
14 | Price schedule -civil works, Boundary wall. | sl no. 21 | Kindly request to rovide BSPTCL standard boundary wall , since same is not available on BSPTCL website.
15 | Price schedule -civil works, dormatory building. | sl no. 18 | Kindly request to provide the standard drawing for dormatory building. OR Kindly provide the area required and type of structure to be considered for dormatory building.
16 | Firewall |  | Please clarify firewall will be paid under which item in price the schdule.
17 | Firewall |  | Kindly request to provide the BSPTCL standard drawings for firewall if any.
18 | Price schdule-Erection, Structural steel for lighting cum lighttning mast. | Sl no. R-2 page no.10 & Sl no. O-1 page no.10 | We understand that structure steel required for lighting cum lightning mast will be paid under Sl no. O-1, page no.10 of erection price schdule, no need to consider additional structural steel quantity for same, please confirm.

## 38 PR BSPTCL 2018 (hidden)
|  |  |  | Date: | 2018-07-30
Project | Construction of (2x200MVA+3x50 MVA) 220/132/33KV GSS, Karmnasha
Client |  | Bihar State Power Transmission Company Limited.
Contractor |  | Bajaj Electricals Limited.
S.No. | Tender document reference | Clause no. & page no. | Clarification by Contratcor | Response by client | Remarks
1 | General Plot plan |  | Kindly request to provide the general plot plan of the substation area ( length & breadth).
2 | Soil Investigation report |  | Please provide the soil investigation report if avialable for proposed substation area inorder to quantiy the foundation works or Kindly provide safe bearing capacity to be considered at 1.5m below existing ground level.
3 | Contour map |  | Kindly request to provide the contour map for the proposed substation area if available.
4 | Location of site |  | As geotechnical investigation & foundation design is included our scope of work, we would like to do following in proposed substation plot inorder to estimate foundation quantity. 1. Preliminary topographical survey 2. Bore log In this regards, kindly request to provide the plot location of the proposed substation.
5 | Changes in site location |  | We undestand that in case of changes in site location during detailed engineering due to that if we have any impact in foundation type and sizes will be paid as additional to the contarctor, please confirm.
6 | Price schedule -civil works, FFPH building with rest room | sl no. 5-b | Kindly request to provide the area of rooms required to be placed at first floor of pump house building.
7 | Price schedule -civil works, landscaping | sl no. 20 | Kindly request to provide the area required for landscaping and provide the type of landscaping required.
8 | Vol-2D, Civil works, High flood level. | sl no. 25, Page no.12 | In order to finalize the finished ground level of proposed substation, kindly request to provide the highest flood level for proposed substation.
9 | Vol-2D, Civil works, retaining wall/Stone pitching. | sl no. 24-b, Page no.12. | As per mentioned clause, we understand that retaining wall is not required incase of filling less than 2m, whereas for filling up to 2m will required stone pitching slope protection , which will also paid as extra to the contarctor , please confirm.
10 | Vol-2D, Civil works, retaining wall. | sl no. 24-b, Page no.12. | As per mentioned clause, we understand that retaining wall is not required incase of filling less than 2m, whereas for filling above 2m will required same and paid as extra to the contractor as per bihar PWD schdule of rates, please confirm.
11 | Retaining wall and stone pitching |  | In case the above clarification sl no.9 & 10 will not paid additional to contartor, we kindly request to include the item for stone pitching & retaining wall for different heights ( 2m, 2.5, 3m , 3.5m etc.) in price schdule.
12 | Vol-2D, Civil works, Tower and equipment support structure - Galvanization thickness. | sl no. 15-b, Page no.5. | Kindly request to provide the minimum galvanization thickness for structural steel members.
13 | Vol-2D, Civil works, Tower structure - standard drawing. |  | Standard drawings for substation gantry and towers are not avialable in BSPTCL website, kindly request to provide 220kV, 132kV & 33kV tower and gantry GA drawings.
14 | Price schedule -civil works, Boundary wall. | sl no. 21 | Kindly request to rovide BSPTCL standard boundary wall , since same is not available on BSPTCL website.
15 | Price schedule -civil works, dormatory building. | sl no. 18 | Kindly request to provide the standard drawing for dormatory building. OR Kindly provide the area required and type of structure to be considered for dormatory building.
16 | Firewall |  | Please clarify firewall will be paid under which item in price the schdule.
17 | Firewall |  | Kindly request to provide the BSPTCL standard drawings for firewall if any.
18 | Price schdule-Erection, Structural steel for lighting cum lighttning mast. | Sl no. R-2 page no.10 & Sl no. O-1 page no.10 | We understand that structure steel required for lighting cum lightning mast will be paid under Sl no. O-1, page no.10 of erection price schdule, no need to consider additional structural steel quantity for same, please confirm.

## 39 PR BSPTCL 2018 (hidden)
|  |  |  | Date: | 2018-07-30
Project | Construction of (2x160MVA+3x50 MVA) 220/132/33KV GSS, Garaul
Client |  | Bihar State Power Transmission Company Limited.
Contractor |  | Bajaj Electricals Limited.
S.No. | Tender document reference | Clause no. & page no. | Clarification by Contratcor | Response by client | Remarks
1 | General Plot plan |  | Kindly request to provide the general plot plan of the substation area ( length & breadth).
2 | Soil Investigation report |  | Please provide the soil investigation report if avialable for proposed substation area inorder to quantiy the foundation works or Kindly provide safe bearing capacity to be considered at 1.5m below existing ground level.
3 | Contour map |  | Kindly request to provide the contour map for the proposed substation area if available.
4 | Location of site |  | As geotechnical investigation & foundation design is included our scope of work, we would like to do following in proposed substation plot inorder to estimate foundation quantity. 1. Preliminary topographical survey 2. Bore log In this regards, kindly request to provide the plot location of the proposed substation.
5 | Changes in site location |  | We undestand that in case of changes in site location during detailed engineering due to that if we have any impact in foundation type and sizes will be paid as additional to the contarctor, please confirm.
6 | Price schedule -civil works, FFPH building with rest room | sl no. 5-b | Kindly request to provide the area of rooms required to be placed at first floor of pump house building.
7 | Price schedule -civil works, landscaping | sl no. 20 | Kindly request to provide the area required for landscaping and provide the type of landscaping required.
8 | Vol-2D, Civil works, High flood level. | sl no. 25, Page no.12 | In order to finalize the finished ground level of proposed substation, kindly request to provide the highest flood level for proposed substation.
9 | Vol-2D, Civil works, retaining wall/Stone pitching. | sl no. 24-b, Page no.12. | As per mentioned clause, we understand that retaining wall is not required incase of filling less than 2m, whereas for filling up to 2m will required stone pitching slope protection , which will also paid as extra to the contarctor , please confirm.
10 | Vol-2D, Civil works, retaining wall. | sl no. 24-b, Page no.12. | As per mentioned clause, we understand that retaining wall is not required incase of filling less than 2m, whereas for filling above 2m will required same and paid as extra to the contractor as per bihar PWD schdule of rates, please confirm.
11 | Retaining wall and stone pitching |  | In case the above clarification sl no.9 & 10 will not paid additional to contartor, we kindly request to include the item for stone pitching & retaining wall for different heights ( 2m, 2.5, 3m , 3.5m etc.) in price schdule.
12 | Vol-2D, Civil works, Tower and equipment support structure - Galvanization thickness. | sl no. 15-b, Page no.5. | Kindly request to provide the minimum galvanization thickness for structural steel members.
13 | Vol-2D, Civil works, Tower structure - standard drawing. |  | Standard drawings for substation gantry and towers are not avialable in BSPTCL website, kindly request to provide 220kV, 132kV & 33kV tower and gantry GA drawings.
14 | Price schedule -civil works, Boundary wall. | sl no. 21 | Kindly request to rovide BSPTCL standard boundary wall , since same is not available on BSPTCL website.
15 | Price schedule -civil works, dormatory building. | sl no. 18 | Kindly request to provide the standard drawing for dormatory building. OR Kindly provide the area required and type of structure to be considered for dormatory building.
16 | Firewall |  | Please clarify firewall will be paid under which item in price the schdule.
17 | Firewall |  | Kindly request to provide the BSPTCL standard drawings for firewall if any.
18 | Price schdule-Erection, Structural steel for lighting cum lighttning mast. | Sl no. R-2 page no.10 & Sl no. O-1 page no.10 | We understand that structure steel required for lighting cum lightning mast will be paid under Sl no. O-1, page no.10 of erection price schdule, no need to consider additional structural steel quantity for same, please confirm.

## 40 PR BSPTCL 2018 (hidden)
|  |  |  | Date: | 2018-07-30
Project | Construction of (2x200MVA+3x50 MVA) 220/132/33KV GSS, Raxaul
Client |  | Bihar State Power Transmission Company Limited.
Contractor |  | Bajaj Electricals Limited.
S.No. | Tender document reference | Clause no. & page no. | Clarification by Contratcor | Response by client | Remarks
1 | General Plot plan |  | Kindly request to provide the general plot plan of the substation area ( length & breadth).
2 | Soil Investigation report |  | Please provide the soil investigation report if avialable for proposed substation area inorder to quantiy the foundation works or Kindly provide safe bearing capacity to be considered at 1.5m below existing ground level.
3 | Contour map |  | Kindly request to provide the contour map for the proposed substation area if available.
4 | Location of site |  | As geotechnical investigation & foundation design is included our scope of work, we would like to do following in proposed substation plot inorder to estimate foundation quantity. 1. Preliminary topographical survey 2. Bore log In this regards, kindly request to provide the plot location of the proposed substation.
5 | Changes in site location |  | We undestand that in case of changes in site location during detailed engineering due to that if we have any impact in foundation type and sizes will be paid as additional to the contarctor, please confirm.
6 | Price schedule -civil works, FFPH building with rest room | sl no. 5-b | Kindly request to provide the area of rooms required to be placed at first floor of pump house building.
7 | Price schedule -civil works, landscaping | sl no. 20 | Kindly request to provide the area required for landscaping and provide the type of landscaping required.
8 | Vol-2D, Civil works, High flood level. | sl no. 25, Page no.12 | In order to finalize the finished ground level of proposed substation, kindly request to provide the highest flood level for proposed substation.
9 | Vol-2D, Civil works, retaining wall/Stone pitching. | sl no. 24-b, Page no.12. | As per mentioned clause, we understand that retaining wall is not required incase of filling less than 2m, whereas for filling up to 2m will required stone pitching slope protection , which will also paid as extra to the contarctor , please confirm.
10 | Vol-2D, Civil works, retaining wall. | sl no. 24-b, Page no.12. | As per mentioned clause, we understand that retaining wall is not required incase of filling less than 2m, whereas for filling above 2m will required same and paid as extra to the contractor as per bihar PWD schdule of rates, please confirm.
11 | Retaining wall and stone pitching |  | In case the above clarification sl no.9 & 10 will not paid additional to contartor, we kindly request to include the item for stone pitching & retaining wall for different heights ( 2m, 2.5, 3m , 3.5m etc.) in price schdule.
12 | Vol-2D, Civil works, Tower and equipment support structure - Galvanization thickness. | sl no. 15-b, Page no.5. | Kindly request to provide the minimum galvanization thickness for structural steel members.
13 | Vol-2D, Civil works, Tower structure - standard drawing. |  | Standard drawings for substation gantry and towers are not avialable in BSPTCL website, kindly request to provide 220kV, 132kV & 33kV tower and gantry GA drawings.
14 | Price schedule -civil works, Boundary wall. | sl no. 21 | Kindly request to rovide BSPTCL standard boundary wall , since same is not available on BSPTCL website.
15 | Price schedule -civil works, dormatory building. | sl no. 18 | Kindly request to provide the standard drawing for dormatory building. OR Kindly provide the area required and type of structure to be considered for dormatory building.
16 | Firewall |  | Please clarify firewall will be paid under which item in price the schdule.
17 | Firewall |  | Kindly request to provide the BSPTCL standard drawings for firewall if any.
18 | Price schdule-Erection, Structural steel for lighting cum lighttning mast. | Sl no. R-2 page no.10 & Sl no. O-1 page no.10 | We understand that structure steel required for lighting cum lightning mast will be paid under Sl no. O-1, page no.10 of erection price schdule, no need to consider additional structural steel quantity for same, please confirm.

## 41 PR BSPTCL 2018 (hidden)
|  |  |  | Date: | 2018-07-30
Project | Construction of (2x160MVA+3x50 MVA) 220/132/33KV GSS, Asthawan.
Client |  | Bihar State Power Transmission Company Limited.
Contractor |  | Bajaj Electricals Limited.
S.No. | Tender document reference | Clause no. & page no. | Clarification by Contratcor | Response by client | Remarks
1 | General Plot plan |  | Kindly request to provide the general plot plan of the substation area ( length & breadth).
2 | Soil Investigation report |  | Please provide the soil investigation report if avialable for proposed substation area inorder to quantiy the foundation works or Kindly provide safe bearing capacity to be considered at 1.5m below existing ground level.
3 | Contour map |  | Kindly request to provide the contour map for the proposed substation area if available.
4 | Location of site |  | As geotechnical investigation & foundation design is included our scope of work, we would like to do following in proposed substation plot inorder to estimate foundation quantity. 1. Preliminary topographical survey 2. Bore log In this regards, kindly request to provide the plot location of the proposed substation.
5 | Changes in site location |  | We undestand that in case of changes in site location during detailed engineering due to that if we have any impact in foundation type and sizes will be paid as additional to the contarctor, please confirm.
6 | Price schedule -civil works, FFPH building with rest room | sl no. 5-b | Kindly request to provide the area of rooms required to be placed at first floor of pump house building.
7 | Price schedule -civil works, landscaping | sl no. 20 | Kindly request to provide the area required for landscaping and provide the type of landscaping required.
8 | Vol-2D, Civil works, High flood level. | sl no. 25, Page no.12 | In order to finalize the finished ground level of proposed substation, kindly request to provide the highest flood level for proposed substation.
9 | Vol-2D, Civil works, retaining wall/Stone pitching. | sl no. 24-b, Page no.12. | As per mentioned clause, we understand that retaining wall is not required incase of filling less than 2m, whereas for filling up to 2m will required stone pitching slope protection , which will also paid as extra to the contarctor , please confirm.
10 | Vol-2D, Civil works, retaining wall. | sl no. 24-b, Page no.12. | As per mentioned clause, we understand that retaining wall is not required incase of filling less than 2m, whereas for filling above 2m will required same and paid as extra to the contractor as per bihar PWD schdule of rates, please confirm.
11 | Retaining wall and stone pitching |  | In case the above clarification sl no.9 & 10 will not paid additional to contartor, we kindly request to include the item for stone pitching & retaining wall for different heights ( 2m, 2.5, 3m , 3.5m etc.) in price schdule.
12 | Vol-2D, Civil works, Tower and equipment support structure - Galvanization thickness. | sl no. 15-b, Page no.5. | Kindly request to provide the minimum galvanization thickness for structural steel members.
13 | Vol-2D, Civil works, Tower structure - standard drawing. |  | Standard drawings for substation gantry and towers are not avialable in BSPTCL website, kindly request to provide 220kV, 132kV & 33kV tower and gantry GA drawings.
14 | Price schedule -civil works, Boundary wall. | sl no. 21 | Kindly request to rovide BSPTCL standard boundary wall , since same is not available on BSPTCL website.
15 | Price schedule -civil works, dormatory building. | sl no. 18 | Kindly request to provide the standard drawing for dormatory building. OR Kindly provide the area required and type of structure to be considered for dormatory building.
16 | Firewall |  | Please clarify firewall will be paid under which item in price the schdule.
17 | Firewall |  | Kindly request to provide the BSPTCL standard drawings for firewall if any.
18 | Price schdule-Erection, Structural steel for lighting cum lighttning mast. | Sl no. R-2 page no.10 & Sl no. O-1 page no.10 | We understand that structure steel required for lighting cum lightning mast will be paid under Sl no. O-1, page no.10 of erection price schdule, no need to consider additional structural steel quantity for same, please confirm.