## Sheet1
Clarification No.-III to the Bidding Documents for Substation Extension Package-SS69 for (i) 400/220 kV Muzaffarpur S/S extn including ICT, (ii) 400 kV Saharsa S/S extn, (iii) 400 kV Durgapur S/S extn and (iv) 400kV Kahalgaon S/S (NTPC) extn associated with Eastern Region Strengthening Scheme-XXIII. [Spec. No.: CC-CS/1010-ER1/SS-4083/3/G2]
S.No. | Clause | Provision of Bidding Documents | Bidder’s Query | POWERGRID REPLY
1 | Vol-II-Part 2 of 7 Civil Drgs-2 | SOIL INVESTIGATION REPORT OF Saharsa-R1 Soil Investigation report_Saharsa -I | Please note that as per the soil report of Saharsa , soil is liquefiable. PGCIL Civil BOQ / Price Schedule for Saharsa Civil Works does not contain item to arrest liquefaction. Hence please confirm if any ground improvement/treatment cost is to be considered in the estimate and please provide line item for same in civil price schedule since if this is executed during detailed engineering/execution stage , this cost will be additional. | The Liquefaction issue shall be taken care as per soil report during detail engineering.Foundation for heavey structures envasiged as Pile foundation,however foundation for lightly loaded structures shall be finalised with open foundation with boulder filling/Pile foundations based on the soil condition upon completion of site filling over natural ground level. Line item for boulder filling mixed with sand has been provided through Amendment-V
| Schedule-3 :- III . 400 kV Substation Extn at Saharsa | CIVIL WORKS
2 | Section Project Cl. 3.1.1. XIV, XV | Existing duplicate 400kV bus bar protection scheme is DAD-N (high Impedance Differential) of Reyroll make. | The existing bus bar protection is not mentioned in 220kV - Muzzafarpur station. Please provide the same as it is not mentioned in Section Project and we are unable to estimate cost of Augmentation of 220kV Bus Bar protection as a result. | Existing 220kV Busbar protection is also DAD-N (high Impedance Differential) of Reyroll make
3 | Section Project For 220kV GIS 3 Phase CB,ES & DS | Customer's Requirement: 3 Phase CB,ES & DS. | Bidder's Remark: We provide single phase CB, ES & DS. However our ES and DS mechanism is gang operated. Kindly accept the same. | Acceptable, as it is inline with intend of bidding document.
4 | Section Project CT data & VT data | Customer's Requirement: N/A | Bidder's Remark: As the CT data and VT data is not mentioned completely, we have considered the same as per the PGCIL technical specification. Kindly accept the same. | Acceptable, as it is inline with intend of bidding document.
5 | BPS PDM | Customer's Requirement: Partial Discharge Monitor (220 kV GIS) - Offline | Bidder's Remark: We would like to inform you that, we have considered the portable type PDM in our offer. Kindly confirm the same. | Acceptable, as it is inline with intend of bidding document.
6 | Section Project Cl. 3.1 I. B. e & f ICT bay termination method | Customer's Requirement: e. Three single phase (isolated) or three phase SF6 ducts inside GIS hall (upto the outer edge of the wall of the GIS hall) f. Termination for GIS bus ducts to XLPE cable interface to connect 220kV GIS with 220kV side of 400/220kV Autotransformer through XLPE cable. | Bidder's Remark: We would like to inform you that, as per our understanding we have considered the GIB till the outer edge of the GIS hall and consider outdoor type cable sealing end for GIS connection with Autotransformer. Kindly confirm the same. | Bidder's understanding is correct i.e cable termination with GIS module shall be outside building. Further as per section project clause 3.1.1 (II B) & IV, GIS to cable end termination kit and SF6 GIS duct required for termination shall be the part of GIS bay module.