| Sl. NO | VOLUME /SEC No. | CLAUSE Ref | Description | Deviation | Reason for deviation | Reply |
| --- | --- | --- | --- | --- | --- | --- |
|  | Section-765KV Shunt reactor, Neutral Grounding Reactor and Surge Arrester Rev.07 | Clause No.4.3 Page No.5 of 68 Annexure-A Technical Particulars/ Parameters of Reactor Point No.1.14(iii) Annexure-B Test Point No.12 Page No.37 of 68 | 4.3 The reactors shall be designed for switching surge overvoltage of 1.9 p. u. and temporary over voltage of the order of 1.4 p .u. for about 10 cycles followed by power frequency overvoltage up to 830 kV rms for about five minutes. (iii) One Minute Power Frequency withstand Voltage 830kV rms (Ph-Earth) for 5 min (to be tested) 12. Short time over voltage Test (830kVrms) Routine | This test is not recommended in IS/IEC. | Kindly it may be noted that during Short time over voltage test, power drawn by the reactor shall be very huge which is 3.53 times than the rated power of the reactor. Hence this test is not recommended in IEC 60076-6 for Um>170 kV and non-uniform insulation. Kindly accept and confirm. | Bidder to quote as per requirements of bidding document |
|  | Section-765KV Shunt reactor, Neutral Grounding Reactor and Surge Arrester Rev.07 | Clause No.9.2 Page No.18 of 68 | Out of two dummy blocks, one block shall be used during manufacturing stage and another one shall be sent with Reactor at site. Before application of vacuum and oil filling, the 2nd dummy block shall be used for DP Test (Degree of polymerisation). | DP test at site shall not be in our scope. | The second dummy block shall be provided. However, the DP test on the second block at site, will not be in our scope. Kindly accept and confirm. | Bidder to quote as per requirements of bidding document |
|  | Section-765KV Shunt reactor, Neutral Grounding Reactor and Surge Arrester Rev.07 | Clause No.11.2 Page No.20 of 68 | 145kV BPI/support insulator shall be solid porcelain type. | Not in our scope. | As per Cl. 3.0,-vi) of Section Project, neutral formation is not in scope, Therefore, we understand that 145kv BPI / support insulator for 80 MVAr shall not be in our scope. Kindly confirm. | Confirmed. |
|  | Section-765KV Shunt reactor, Neutral Grounding Reactor and Surge Arrester Rev.07 SECTION- PROJECT, | Clause No.18.6 Page No.26 of 68 Page No. 4 & 5 of 11 | One number single phase current transformer (outdoor) for earth fault protection shall be provided for each bank of reactor and shall be located in the neutral conductor connecting common neutral point with earth. 3.0 EXCLUSION vi) Arrangement of neutral formation for Reactor(s) and making connection arrangement (HV auxiliary Bus) to connect single phase spare Reactor unit | Loose current transformer shall be provided. | As per Cl. 3.0 of Section Project, neutral formation is not in scope, only loose CT shall be provided for the 110 MVAr. Kindly accept and confirm. | Neutral formation is not in scope. For CT scope, provisions of bidding documents shall prevail. |
|  | Section-765KV Shunt reactor, Neutral Grounding Reactor and Surge Arrester Rev.07 | Annexure-D Reference Drawings | (i) Standard Foundation Drawing STD/RT/765/FDN/POWERGRID/80/110 R01 | Rev.00 drawing is enclosed. | The drawing enclosed is of Rev.00, whereas the revision of the drawing mentioned in Annexure-D is Rev.01. Kindly confirm the revision no. of the drawing. | It is a typographical error. Enclosed drawing Rev 00 to be considered. |
|  | Section-765KV Shunt reactor, Neutral Grounding Reactor and Surge Arrester Rev.07, TS of RTV Coating_Ammend- | Clause 11.2, Page No.- 20 of 68 | 11.2. Bushing for voltage of 800kV shall be of porcelain or composite polymer housing and hermetically sealed Oil filled condenser type. Neutral Bushing for voltage of 145 kV shall be of RIP type with composite polymer insulator housing. 145kV BPI/support insulator shall be solid porcelain type. Technical Specification for RTV Silicone high voltage insulation coating (HVIC) | RTV Coating is not required | Kindly note that as per Clause No 11.2 of Spec SR-R10 it is mentioned that Bushing for voltage of 52 kV and above shall be RIP bushing with composite insulator. 36 kV bushing shall be solid porcelain or oil communicating type. However, in this project Technical Specification for RTV Silicone high voltage insulation coating (HVIC) is attached also. But in section project there is no mention of RTV coating. Therefore, we understand that RTV Coating is not required. And if it is required then kindly specify on which bushing it is to be applied. | Confirmed. |
|  | SECTION- PROJECT, 02_2nd Envelope _Price Schedule_RT08 | Cl. 2.2.1 80MVAr,765 KV Line Reactor, Clause (c ), page no. 03 of 11 80MVAr,765 KV Bus Reactor, Clause (b ), page no. 03 of 11 Cl. 2.2.1 80MVAr,765 KV Bus Reactor, Clause (g ), page no. 04 of 11 | c) On line dissolved gas (Multi-gas) and Moisture Analyzer, on line Insulating oil drying system as per requirement, Oil storage tank as per Bid Price Schedule. b) On line dissolved gas (Multi-gas) and Moisture Analyzer, on line Insulating oil drying system as per requirement, Oil storage tank as per Bid Price Schedule. g) On line dissolved gas (Multi-gas) and Moisture Analyzer, on line Insulating oil drying system as per requirement, Oil storage tank as per Bid Price Schedule. | Oil storage tank not specified in BPS | Since, Oil storage tank is not specified in BPS, we understand that Oil storage tank is not in scope. Kindly confirm. | Confirmed. |
|  | ---------- | --------- | ----------- | --------------- | In the endeavour to get quality product Load loss, I2R loss and Eddy & Stray losses were fixed in the meeting with CEA (Central Electricity Authority) along with PGCIL, NTPC, NHPC and various transformers and reactors manufacturer. We welcome this step taken by M/s PGCIL along with CEA. M/s PGCIL has come up with huge requirement of transformers under subject package. Requesting M/s PGCIL to implement the losses (I2R and Eddy & Stray) in the ongoing/subject tender also. | Bidder shall quote as per provisions of Bidding Document. |