|  | Clarification No.-I to the Bidding Documents for Reactor Package RT-08 for (i) 7 x 80 MVAr, 765kV, 1-Phase Line Reactor and 6 x 80 MVAr, 765kV, 1-Phase Bus Reactor at 765/400 KV Bhadla-II (New) Pooling Station, (ii) 7 x 80 MVAr, 765kV, 1-Phase Bus Reactor at Fatehgarh-II (New) Pooling Station under Transmission Scheme for Solar Energy Zones in Rajasthan. Spec. No(s): CC-CS/912-NR1/RT-3940/3/G5. |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Sl. No. | VOLUME/SEC No. | CLAUSE Ref (if any) | Relevant Clause | Description of Query | Reply |
|  | Section Project. | Clause 6.2 | Seismic Zone : Zone V | According to IS1893 part 1: 2016 (attached for ready reference), Fatehgarh site fall in Zone II or maximum in Zone III. So Kindly reconfirm this will have huge Impact on bushing price. | It is clarified that, the Seismic Design Requirements for Reactor & its accessories shall be corresponding to an acceleration of 0.3g in the horizontal direction. |