| Sl. No. | Clause ref | Queries asked by the bidder | POWERGRID’s clarification |
| --- | --- | --- | --- |
| 1. | Volume-II Section-IA, Clause 1.3 & 1.4 | Transmission Line Route KMZ file not provided. Request you to share. | Bidders may refer Clause 1.3.1, Section-IA, Volume-II (Technical specifications) which interalia indicates that bidders may visit the line route to acquaint themselves with terrain conditions and associated details of the proposed transmission lines. For this purpose they are requested to contact the following address: Chief General Manager (Projects) POWER GRID CORPORATION OF INDIA LTD. Northern Region Transmission System-II Grid Bhawan, Near Bahu Plaza, Rail Head Complex, Jammu-180012 |
|  |  | It is understood the proposed 66kV D/c Transmission line is between 220kV/66kV Drass Substation, UT Ladakh & 66/11kV Zoji La substation. Kindly share sending end & receiving end GPS coordinates |  |
|  | Price Schedule – 1, item no.55 | In price schedule under supply BoQ “Item no.55 Earth continuity cable as per Technical specifications - 8KMs quantity”., for which specifications are not provided in Volume-II. However, under section-V, GALVANISED STEEL EARTHWIRE specifications provided for 7/3.15 mm, 7/3.66 mm, 7/4.5 mm, 19/ 3.00 mm GS Earth wire given. Request you to confirm & share the specification for this line-item no.55 | The Rating/Sizing of Earth continuity cable shall be decided during detailed engineering based on the calculation submitted by successful bidder meeting the requirement as per TS. Please refer clause no: 1.16.7 of Section: EHV XLPE Power Cable (Rev01). Earthwire specifications given shall not be referred for earth continuity cable requirement. |
| 2 | BPS | Price Schedule: SCH3 (i.e. Erection schedule) Sl. No. 25 & 26, the installation of aviation requirement was in contractors scope, whereas in SCH1 (i.e. Supply schedule) the supply of aviation equipment were missing, So, we understood that the aviation equipment is the owner supplied material and the installation is in the contractors scope. Please confirm. | Kindly refer Amendment-I. |
| 4 | SCHEDULE OF RATES & PRICES, Schedule -1: PLANTS & EQUIPMENTS TO BE SUPPLIED Item No. 69 SINGLE PHASE EARTH LINK BOX FOR 220KV XLPE CABLE | We understand that there is a requirement of 66 kV instead of 220 kV kindly confirm. | Kindly refer Amendment-1. |
| 5 | SCHEDULE OF RATES & PRICES, Schedule -3: INSTALLATION CHARGES. Item No. 41. JOINT BAY Construction | Construction of Joint Bay for Cable Joints is not indicated in the Price Schedule Line Item, kindly review and advise accordingly. | Please refer the description of BPS mentioned at Sl. Nos: 41 in SCHEDULE OF RATES & PRICES, Schedule -3 where in Construction of Joint Bay already included. |
| 6 | SCHEDULE OF RATES & PRICES, Schedule -3: INSTALLATION CHARGES. Item No. 41 .- JOINT BAY | Joint Bay Drawing not available. It is requested to please share drawing for our reference. | Please refer clause no: 24 Joint bay of TS SECTION: EHV XLPE POWER CABLE (Rev 01), the Joint bay drawing is in the scope of bidder. |
| 7 | Cls No 1.2 & 1.12 : SECTION: EHV XLPE POWER CABLE | Pls clarify the Metallic sheath type i.e. Corrugated Aluminum sheath or Lead sheath Required. Both are mentioned in the Technical specification. | Please refer clause no: 10.6 of TS section project (Rev00) of cable scope. Accordingly, Extruded Lead alloy “E” sheath has been envisaged. |
| 8 | Cls No 4.6 System Parameter SECTION: EHV XLPE POWER CABLE | There is no any Specific Fault current of Metallic sheath is mentioned, however we presume that the desired Fault current is 31.5 kA for 3 sec as mentioned in Cls No 4.6 System parameter for 66 kV . Pls note that Conductor Size 185 sqmm Copper, itself not adequate to carry out not Rated Short ckt current of 31.5 kA for 3 sec , Only suitable for 26.4 kA for 1 sec ( ie 15.2 kA for 3 sec) . Hence Pls review the Requirement of Short ckt current & duration of Metallic sheath & inform us. | Please refer clause no: 4.1 (viii) & (x) of section project for 66 kV Underground Cable work regarding rated short time current of cable. The Short circuit current of metallic sheath shall be 25 kA/1 Sec Bidder shall quote meeting the requirement as per TS. |
| 9 | Volume-II, Section IA | Technical specification & Drawings of 66kV hardware fittings not available, please furnish. | Bidders may refer Clause 2.4.1, Section-IA, Volume-II of Technical specifications. |