| Sl. No. | Ref Clause No. | Provision in Bidding documents | Bidder’s Queries | POWERGRID’s reply |
| --- | --- | --- | --- | --- |
|  | Section project Clause 2.1 | Design, Engineering, Manufacture, testing at Manufacture’s works, supply, transportation, unloading and delivery at site, insurance & Storage. erection, testing & commissioning at site for the following Transformers including insulating oil, all fittings, accessories, marshaling box for each Auto-Transformer, Digital RTCC relays and Panel (as applicable), foundation bolts and cables as per Technical specification for the following: i. 3X500MVA, (765/ √3)/(400/√3) / 33 kV 1-Phase ICT at Maheshwaram (PG) substation. ii. 3X500MVA, (765/√3)/(400/√3) / 33 kV 1-Phase ICT at KPS-3 (GIS) iii. 3X500MVA, (765/√3)/(400/√3) / 33 kV 1-Phase ICT at Padghe (PG) GIS | Since KPS -3 Khavda & Padghe s/s is mentioned as GIS substation hence kindly confirm/ clarify the type of termination of bushings required is Oil to Air or Oil to SF6 so that correct bushing can be considered. | Requirement of Bushing is ample clear in Bidding document As per Clause no. 10 of Section – 765kV Auto-Transformer REV 08. Transformer terminations for KPS-3, Padghe and Maheshwaram (PG) shall be through Oil to Air Bushings. |
|  | Section project Clause 4.2 | The locations of substations are indicated below: Sl. No.; Name of Substation; State/UT; Nearest Rail Head. 3; Padghe; Maharashtra; KHANDESHWAR (KNDS). | The nearest railhead for Padghe S/s mentioned is Khandeshwar, please re-check the provided information or provide the coordinates of the site. | Terms & conditions in bidding document shall prevail |
|  | ITB 24.1 (c) in BDS, GCC 1.1(e), 1.1 (ee) & GCC 21.1 in SCC | The Time for Completion shall be as under : Description; Duration in Months from the date of Notification of Award. Taking Over by the Employer upon successful Completion of. Transformer Package TR-50 for:. 3x500MVA, 1-Ph, 765/400kV ICT at Maheshwaram (PG) substation associated with “Augmentation of transformation capacity by 1x1500 MVA (3rd), 765/400kV ICT at Maheshwaram (PG) substation in Telangana”; 18 (Eighteen) months. 3x500MVA, 1-Ph, 765/400kV ICT at KPS-3 GIS associated with “Transmission System for Evacuation of Power from potential renewable energy zone in Khavda area of Gujarat under Phase-IV (7 GW): Part E3”; 20 (Twenty) months. 3x500MVA, 1-Ph, 765/400kV ICT at Padghe (PG) GIS associated with “Transmission System for Evacuation of Power from potential renewable energy zone in Khavda area of Gujarat under Phase-IV (7 GW): Part E4”; 20 (Twenty) months. | Kindly change the Time for Completion to 30 Months instead of 18Month / 20 Months due to present order book position / delivery commitments of existing projects in order to consider the bid decision. | The provisions of the bidding documents shall remain unchanged. |
|  | 6.11 pg 15/79, 6.12 pg 15/79, Cl. 2.2(d) pg 3/5, Cl 2.2(d) pg 3/5 | a) Cl. 6.11 &6.12: Any special cable required for shielding purpose, for connection between PT100 temperature sensor and transducer, shall be in the scope of Contractor. 4-20mA signal shall be wired to Digital RTCC panel / BCU for further transfer data to SCADA through IS/IEC 61850 compliant communications. b) Cl. 2.2(d): All cables including special cables from Transformer to marshalling box and only special cable (if any) from marshalling box to C&R panels shall be in the scope of contractor. c) Cl: 2.2(d): Any special cable for RTCC relay Operation, between Transformer MB/DM to Owners switchyard panel room/control room, shall be in the scope of contractor. | a) Kindly provide the distance between control room and MB/CMB. b) As there is no special accessories like DGA, FOS, etc, special cables are not applicable for this project. hence same is not considered. Kindly confirm. c) RTCC relay panel not applicable for maheshwaram and KPS-3 SS, hence same is not considered, Special cables for Padghe SS between control room to MB/DM will not be in our scope. kindly confirm. | a) Bidder may visit the site & get acquainted with actual site condition including distance. b) Supply of online drying system,including any special cable (if required) is envisaged in present scope. c)Bidder to quote meeting requirement of TS |
|  | Cl.13.4.3 pg 26/79 | Cl. 13.4.3: Auxiliary power supply distribution scheme shall be submitted for approval. Supply and laying of Power, Control and special cables from common marshalling box to individual MB/Cooler Control Cubicle (including spare unit) & further distribution from IMB/CCC to all accessories is in the scope of the contractor. Further any special cable (if required) from CMB to Owner’s Control Panels is also in the scope of the contractor | Only Supply of Power, Control and special cables from individual marshalling box to common marshalling box is in the our scope of supply. trenches/ laying of cables is not in our scope. As there is no special accessories like DGA, FOS etc, special cables are not applicable for this project. hence same is not considered. Kindly confirm. | Terms & conditions in bidding document shall prevail |
|  | Cl.14 pg 27/79 Cl.13(a) pg 66/79 | Buchholz Relay, Magnetic Oil Level Gauge, Pressure Relief Device & Sudden pressure relay to be wired through unarmoured cable of 1.5 sq.mm (minimum), inside GI conduit, with no part exposed. Cable shall be protected by flexible stainless steel pipe, at both ends as per requirement. Proper sealing arrangement to be provided at both ends to avoid ingress of water. STANDARD TECHNICAL DATA SHEET - 1.1kV kV GRADE PVC CONTROL CABLES | As per PGCIL approved standard practice, for all equipments mounted on transformer, we will provide armoured cable in cable tray(till IMB), which are suitable for outdoor applications instead of mentioned conduit, as per CEA guidlines also option for giving cable tray is given, hence we provide cable tray against conduit requirement, kindly confirm. Also as per STANDARD TECHNICAL DATA SHEET - 1.1kV kV GRADE PVC CONTROL CABLES it is mentioned all the control cables are armoured. Hence, kindly accept armoured cable with cable tray. | Terms & conditions in bidding document shall prevail |
|  | Cl.no: 18(cc) pg 37 of 79 | Managed Ethernet switch, LIU patch cords etc. shall be provided in CMB/MB (as per clause 16). All IEC 61850 compliant signals from various monitoring equipment/accessories shall be wired upto the Ethernet switch (if applicable). | Pl confirm the requirement in this project. | Terms & conditions in bidding document shall prevail |
|  | Cl 4.1 pg 4/5 | Coastal area for KPS-3 SS | Kindly confirm RTV coating applicability for porcelain insulators as per Cl.no: 22.9 of GTR. | Requirement in Bidding document is ample clear. Bidder to quote meeting requirement of TS |
|  | Cl 4.1 pg 4/5 | Seismic zone as per IS 1893 (Part 1) For the scope at KPS-3, ZONE-V is to be considered in line with Seismic Zone - IS 1893 (Part 1) | 1.800kV OIP Bushing, we have performed the seismic test considering Zone III requirement (0.16g) and when bushings are mounted with zero degree mounting angle on transformer tank. 2.400KV OIP Bushing, we have performed the seismic test considering Zone V requirement (0.3 g) . Due to setup limitation, we have performed test keeping bushing vertical. Kindly confirm above bushings are acceptable for mentioned seismic zone, also kindly share seismic zone level for other SS(Maheshwaram and Padghe). | Requirement in Bidding document is ample clear. Bidder to quote meeting requirement of TS. Bidders to correct the parameter in line with Seismic zone as per IS 1893 (Part 1) |
|  | Cl 2.2(i) pg 3/5 | Maheshwaram SS: Cost of the wiring & integration, for parallel operation of the New Transformer bank , with existing banks of the Transformers is deemed to be included in the cost of Transformer & no additional payment shall be admissible. | Wiring and integration will not be in our scope, as existing AVR scheme(AVR model) and distance are not available at this stage. Kindly accept. | Bidder’s query is irrelevant |