| Sl. No. | Clause ref | Existing clause | Queries asked by the bidder | POWERGRID’s clarification |
| --- | --- | --- | --- | --- |
|  | Technical Specifications |  | We do not find Technical specification for AACSR EARTHWIRE (194.6SQ.MM) either in the Tender Specification or in the Amendments' Kindly provide the same to get appropriate quote from the vendors to enable us to submit our most competitive offer also please provide Qualification requirement for Contractor supplied line material for AACSR Earthwire to get appropriate quotes from the vendors. | Refer Amendment-III. |
|  | Clause No. OPGW Specifications Section-X subsection 2.1.2.3 | “The Max Allowable Tension shall also be less than or equal to 0.45 times the UTS.” | While maintaining 90% of conductor sag at minimum temperature no wind conditions for OPGW. We are not able to satisfy utilization factor of 0.45. In order to maintain utilization factor of 0.45 the maximum sag of OPGW will increase by minimum 7.0 mtrs. It will cause unnecessary increment of peak height by 7 meters. Therefore, peak height will be at least 16.0 m instead of 9.0 m. | Refer Amendment-III. |
|  | Vol-II/Section-IVD/Clause No. 1.7.12 (Page No. 15) & Price schedule | For foundation in coastal areas or creek or aggressive soil areas or under marine environment, if mentioned in BPS, Ready Mix Concrete of M30 Grade shall be used to avoid use of locally available saline water. However, design mix concrete of M30 Grade conforming to IS 456 with potable water can be used at locations where transportation of ready-mix concrete is not feasible. Minimum cement content in any case shall not be less than 330kg/m3. The surface of the reinforcement steel shall be treated with epoxy-based coating to enhance corrosion performance of foundation. Use of epoxy coated reinforcement in foundation shall be as per IS 13620. In addition, 02 (two) numbers of coats of bituminous painting of minimum 1.6 kg/m2 per coat shall be applied on all the exposed faces of the foundation (i.e. pedestal & base slab). Double coat 20 mm thick cement plaster shall be provided on all exposed concrete surface as well up to 300 mm below ground level to give protection to concrete surface from environmental and saline effect. Before coping of chimney top portion, three coats of anti-corrosive paint of minimum 30-35 microns dry film thickness each shall be applied on the stub in the 50 mm coping portion as well as up to 350mm above CL portion. Cost of the above shall be deemed to be included in the rates quoted | As per the clause & Price Schedule, we understand that the line is passing through Coastal areas. Therefore the below mentioned work cost has to be include in the foundation cost 1) 02 (two) numbers of coats of bituminous painting of minimum 1.6 kg/m2 per coat shall be applied on all the exposed faces of the foundation (i.e. pedestal & base slab). 2) Double coat 20 mm thick cement plaster shall be provided on all exposed concrete surface as well up to 300 mm below ground level to give protection to concrete surface from environmental and saline effect. 3) Before coping of chimney top portion, three coats of anti-corrosive paint of minimum 30-35 microns dry film thickness each shall be applied on the stub in the 50 mm coping portion as well as up to 350mm above CL portion Kindly confirm our understanding correct. | Bidders understanding is correct. |
|  | Vol-II/Section-IVD/Clause No. 1.7.12 (Page No. 15) & Price schedule | For foundation in coastal areas or creek or aggressive soil areas or under marine environment, if mentioned in BPS, Ready Mix Concrete of M30 Grade shall be used to avoid use of locally available saline water. However, design mix concrete of M30 Grade conforming to IS 456 with potable water can be used at locations where transportation of ready-mix concrete is not feasible. Minimum cement content in any case shall not be less than 330kg/m3. The surface of the reinforcement steel shall be treated with epoxy-based coating to enhance corrosion performance of foundation. Use of epoxy coated reinforcement in foundation shall be as per IS 13620. In addition, 02 (two) numbers of coats of bituminous painting of minimum 1.6 kg/m2 per coat shall be applied on all the exposed faces of the foundation (i.e. pedestal & base slab). Double coat 20 mm thick cement plaster shall be provided on all exposed concrete surface as well up to 300 mm below ground level to give protection to concrete surface from environmental and saline effect. Before coping of chimney top portion, three coats of anti-corrosive paint of minimum 30-35 microns dry film thickness each shall be applied on the stub in the 50 mm coping portion as well as up to 350mm above CL portion. Cost of the above shall be deemed to be included in the rates quoted. | The Grade/Specification wise the paint cost use to vary. Kindly request to specify the grade/specification of bituminous & anti-corrosive paint. | Bidder to use suitable bituminous & anti-corrosive paint as per provision of Technical specification. |
|  | General |  | To conduct proper site survey, we request you to provide the GPS Coordinates of Proposed Navasari (New) (South Gujarat) Sub Station. | Please refer FAQs. |
|  | BPS | AMOUNT LINKED TO ESTABLISHMENT OF FACILITIES FOR LABOUR. | As per the clause, we understand that establishment facilities for site labor to be arranged/provided by Contractor, for the same we will be paid by owner as per payment terms specified in the tender documents. At end, the same will be taken back by the contractor after completion of works. Kindly confirm our understanding is correct. | As per Cl. 2.12 Sec-II of Technical specification, Contractor shall provide his/ their laborer with sufficient number of Tents & Portable (tyre- mounted) Bio toilet. Accordingly rate of these services are covered under item “ESTABLISHMENT OF LABOUR CAMPS……FOR LABOURERS IN TECHNICAL SPECIFICATION.” It is discretion of Contractor to dispose-off/take back the same after completion of works. |