| Sl No | Cl No. | Existing Clause/item | Amendment |
| --- | --- | --- | --- |
| 1. | 2.4. of Sec-IA of Technical specification | - For Tower Package TW03 & TW04 As Transmission line covered under the subject packages passes through Coastal area, following requirements shall replace/supplement the requirements in different sections of the Technical Specification: - - Details of Line Materials shall be following: - 765 kV Double Circuit Transmission Line with Hexa AACSR Zebra conductor - Details of conductor & Earthwire/OPGW 1; Conductor; Six AACSR ZEBRA conductor per phase with sub-conductor spacing of 457 mm in vertical configuration.. 2; Earthwire / OPGW; One AACSR Earthwire and one OPGW with mechanical & electrical properties equivalent to the used AACSR earthwire.. - Details of Insulator Strings with composite long rod insulators Following insulator strings with composite long rod insulators shall be used in the transmission line covered under the above package. All other requirement of composite long rod insulators and insulator strings shall be as per Section-VIII of this specification: - Sl. No; Type of String; Size of Composite Insulator (Core dia x Nominal length) (mm); Minimum Creepage Distance (mm) per unit; No. of individual Units per String (Nos.); Electro- Mechanical Strength of Insulator Unit (kN); Mechanical Strength of Insulator String along with Hardware Fittings (kN). 1; Double “I” suspension; 24*x 2975; 12400; 2 x 2; 210; 2 x 210. 2; Single “I” suspension pilot; 24*x 2975; 12400; 1 x 2; 210; 210. 3; Single Tension; 24*x 2975; 12400; 1 x 2; 210; 210. 4; Quad Tension; 32**x2 975; 12400; 4 x 2; 320; 4 x 320. * The core dia of composite insulators for indicative purpose. The bidder shall offer composite long rod insulators of suitable core dia, not less than the value specified above, to meet specified E&M and torsion strength requirements. **For offered core dia, less than indicated in table above, the bidder shall submit documentary evidence of past supplies & satisfactory operation of the same for minimum period of three years. However, the overall string length shall be within the limits specified in the drawing. - Maximum temperature of AACSR ZEBRA conductor and AACSR Earthwire shall be 850C and 530C respectively in design of tower. - Following Modulus of elasticity and coefficient of Linear expansion of AACSR ZEBRA conductor and AACSR Earthwire shall be considered for sag Tension calculation: - Conductor/ Earthwire; Modulus of elasticity (kg/mm2); Coefficient of Linear expansion ( /0C). AACSR ZEBRA conductor; 7036; 19.3 x 10-6. AACSR Earthwire; 13300; - 10-6. | 2.4.1 For Tower Package TW03 & TW04 As Transmission line covered under the subject packages passes through Coastal area, following requirements shall replace/supplement the requirements in different sections of the Technical Specification: - - 2.4.1.1 Details of Line Materials shall be following: - 765 kV Double Circuit Transmission Line with Hexa AACSR Zebra conductor - Details of conductor & Earthwire/OPGW 1; Conductor; Six AACSR ZEBRA conductor per phase with sub-conductor spacing of 457 mm in vertical configuration.. 2; Earthwire / OPGW; One AACSR Earthwire and one OPGW with mechanical & electrical properties equivalent to the used AACSR earthwire.. - Details of Insulator Strings with composite long rod insulators Following insulator strings with composite long rod insulators shall be used in the transmission line covered under the above package. All other requirement of composite long rod insulators and insulator strings shall be as per Section-VIII of this specification: - Sl. No; Type of String; Size of Composite Insulator (Core dia x Nominal length) (mm); Minimum Creepage Distance (mm) per unit; No. of individual Units per String (Nos.); Electro- Mechanical Strength of Insulator Unit (kN); Mechanical Strength of Insulator String along with Hardware Fittings (kN). 1; Double “I” suspension; 24*x 2975; 12400; 2 x 2; 210; 2 x 210. 2; Single “I” suspension pilot; 24*x 2975; 12400; 1 x 2; 210; 210. 3; Single Tension; 24*x 2975; 12400; 1 x 2; 210; 210. 4; Quad Tension; 32**x2 975; 12400; 4 x 2; 320; 4 x 320. * The core dia of composite insulators for indicative purpose. The bidder shall offer composite long rod insulators of suitable core dia, not less than the value specified above, to meet specified E&M and torsion strength requirements. **For offered core dia, less than indicated in table above, the bidder shall submit documentary evidence of past supplies & satisfactory operation of the same for minimum period of three years. However, the overall string length shall be within the limits specified in the drawing. - Maximum temperature of AACSR ZEBRA conductor and AACSR Earthwire shall be 850C and 530C respectively in design of tower. - Following Modulus of elasticity and coefficient of Linear expansion of AACSR ZEBRA conductor and AACSR Earthwire shall be considered for sag Tension calculation: - Conductor/ Earthwire; Modulus of elasticity (kg/mm2); Coefficient of Linear expansion ( /0C). AACSR ZEBRA conductor; 7036; 19.3 x 10-6. AACSR Earthwire; 13300; 14.56 x 10-6. |
| 2. | 2.4. of Sec-IA of Technical specification | - For Tower Package TW04 As Transmission line covered under the package TW04 also passes through hilly terrain as well as coastal area as mentioned above, following additional requirements shall replace/supplement the requirements in different sections of the Technical Specification: - - The towers shall be designed so as to be suitable for adding -6.0m & -4.5m body truncations/ extensions/ leg extensions also apart from those specified in clause 1.2.1, 1.2.3 of Section-IVA. - The tension towers shall be designed with maximum difference between the shortest and the longest leg of 6m in place of 3m specified in clause 1.2.3 of Section-IVA. - In the BPS, charges for design & fabrication of Basic body (including common plan at Basic Level) and leg extensions (including all panel(s) / parts of common plan of one quadrant of tower, other than that at basic level, required to be connected from basic body level) are required to be quoted. Charges for the Normal/ Standard tower (i.e. Basic Body+0 m) and other extension towers shall be summation of the unit price of the Basic Body and the total unit prices of four applicable leg extensions. | - 2.4.2 For Tower Package TW04 As Transmission line covered under the package TW04 also passes through hilly terrain as well as coastal area as mentioned above, following additional requirements shall replace/supplement the requirements in different sections of the Technical Specification: - - 2.4.2.1 The towers shall be designed so as to be suitable for adding -6.0m & -4.5m body truncations/ extensions/ leg extensions also apart from those specified in clause 1.2.1, 1.2.3 of Section-IVA. - 2.4.2.2 The tension towers shall be designed with maximum difference between the shortest and the longest leg of 6m in place of 3m specified in clause 1.2.3 of Section-IVA. - 2.4.2.3 In the BPS, charges for design & fabrication of Basic body (including common plan at Basic Level) and leg extensions (including all panel(s) / parts of common plan of one quadrant of tower, other than that at basic level, required to be connected from basic body level) are required to be quoted. Charges for the Normal/ Standard tower (i.e. Basic Body+0 m) and other extension towers shall be summation of the unit price of the Basic Body and the total unit prices of four applicable leg extensions. |
| 3. | 1.4.9. f) of Sec-IVA of Technical specification | For towers in coastal areas (wherever mentioned in BPS), an additional factor viz. K4 = 1.3 shall be considered for design of towers to take care of cyclonic wind conditions. | For towers in coastal areas (wherever mentioned in BPS), an additional factor viz. K4 = 1.3 shall be considered for design of towers to take care of cyclonic wind conditions. To take care of cyclonic wind loading, design of towers in coastal areas (wherever mentioned in BPS), shall be carried out considering design wind speed based on multiplying an additional factor K4 = 1.3 to the reference wind speed. The increased wind pressure so calculated, shall be applied to Tower structure only and normal wind as per IS:802 shall be applied on Conductor/Earthwire/OPGW/Insulator. Further, the provisions for Narrow front wind loading condition shall remain as per IS:802 and no any additional coastal factor shall be considered. |
| 4. | Section IA of technical specification | Existing Section IA of technical specification | Revised Section IA of technical specification |
| 5. | Bid Price Schedules (BPS), Vol-III of the Bidding Documents | On account of changes in Bill of Quantities (BOQ), the existing excel sheet(s) titled “Price_schedule_TW03_Rev1” (for package TW03); and “Price_schedule_TW04_Rev1” (for package TW04); for 2nd Envelope Bid Form and Price Schedules as available in Volume-III of the Bidding Documents, stands replaced with file titled: “Price_schedule_TW03_Rev2” (for package TW03); and “Price_schedule_TW04_Rev2” (for package TW04); attached herewith. Note- Bidders are required to consider the revised excel sheet(s) [i.e. “Price_schedule_TW03_Rev2” (for package TW03) and “Price_schedule_TW04_Rev2” (for package TW04)] for bid preparation/submission for the respective package. It may be noted that while submitting the bid(s), bidders are required to change the excel file name ‘Price_schedule’. As per the provisions of the portal, it is mandatory to upload excel file with titled ‘Price_schedule’ (Bidders may refer user manuals at the portal https://etender.powergrid.in regarding submission of bid). |  |