| Sl. No. | Clause/ Drg. No. | Existing provision |  | Amended provision |
| --- | --- | --- | --- | --- |
| 1 | Clause B.I.(i) of Annexure IV to Section Project | GIS Bus bar Module: Three isolated phase, SF6 gas-insulated metal enclosed bus bar module, each set comprising of the following: i. Three (3) no’s 4000A individual bus bars enclosures running across the length of the switchgear to interconnect each of the bay modules in one and a half breaker bus system. ii. One (1) number 3-phase, single pole, group operated safety grounding switches, complete with manual and motor driven operating mechanisms. iii. Three (3) numbers 1-phase Potential Transformers complete with manual operated isolating Switch/device. iv. Gas monitoring devices, barriers, pressure switches, UHF PD Sensors, Support structures etc., as required. v. End Piece (Interface) modules with the isolating test link for Future extension (on one side) of Bus bar module. The end piece module shall be designed in such a way so that future GIS module may be tested without extending voltage to existing bus by removing the test link. End piece interface module for both the buses shall be in one alignment. vi. Three (3) numbers single phase, SF6 ducts (as required) inside GIS hall. vii. Local Control Cubicle (if required separately). |  | GIS Bus bar Module: Three isolated phase, SF6 gas-insulated metal enclosed bus bar module, each set comprising of the following: i. Three (3) no’s 4000A individual bus bars enclosures running across the length of the switchgear to interconnect each of the bay modules in one and a half breaker bus system. ii. Gas monitoring devices, barriers, pressure switches, UHF PD Sensors, Support structures etc., as required. iii. End Piece (Interface) modules with the isolating test link for Future extension (on one side) of Bus bar module. The end piece module shall be designed in such a way so that future GIS module may be tested without extending voltage to existing bus by removing the test link. End piece interface module for both the buses shall be in one alignment. iv. Three (3) numbers single phase, SF6 ducts (as required) inside GIS hall. v. Local Control Cubicle (if required separately). |
| 2 | Annexure-I (List of Drawing) of Section Project |  | S. No.; DRAWING NO.; TITLE. Electrical Drawings. 400kV Jeypore GIS Sub-Station. 1.; C/ENGG/ER-WR INTERCONNECTION/ JEYPORE/SLD; Single Line Diagram of 400kV Jeypore SS Extn (Rev-0). | S. No.; DRAWING NO.; TITLE. Electrical Drawings. 400kV Jeypore GIS Sub-Station. 1.; C/ENGG/ER-WR INTERCONNECTION/ JEYPORE/SLD; Single Line Diagram of 400kV Jeypore SS Extn (Rev-01). |