## Pre-Bid Query
Clarifications No.1 to the bidding documents of 400kV GIS Substation Extension Package SS-112 for (i) Extension of 765/400kV Navsari (New) GIS Substation under ICT Augmentation at Navsari (New) associated with integration of additional 7 GW RE power from Khavda RE park under Phase-III, (ii) Extension of 400/220kV Mysore Substation under Augmentation of transformation capacity by 1x500 MVA, 400/220kV ICT (4th) at Mysore S/S, (iii) Extension of 400kV Indore Substation under Scheme to control fault level at 400kV Indore Substation and (iv) Extension of 400kV Jeypore (POWERGRID) Substation under Transmission scheme for Inter-regional ER-WR interconnection scheme” (Specification No.: CC/NT/W-GIS/DOM/A06/23/03905)
Sl. No. | Volume / Section | Clause No. | Description | Bidders Query | POWERGRID reply
A | Electrical Queries
1 | Annexure-IV (VT) of Section Project- Jeypore S/s | Cl. No. ( B-I-i) Pg. No. 04/07 | ii. One (1) number 3-phase, single pole, group operated safety grounding switches, complete with manual and motor driven operating mechanisms. iii. Three (3) numbers 1-phase Potential Transformers complete with manual operated isolating Switch/device. | We woud like to inform you that, As per adjacent clause we understand that, V.T. with I.D. is required. But in tender SLD it is not shown. And Earth switch for Main Bus is not mentioned in SLD and in section project Earth switch required. Please clarify the Bus PT & Bus Earth switch is required for Both Main Buses in GIS section. | Please refer Sr. no. 1 & 2 of Amendment no. -1
2 | JEYPORE SLD | - | Three (3) numbers single phase, SF6 ducts inside GIS hall (up to the outer edge of the wall of GIS Hall). | We would like to inform you that , we understand that 2 no. of line bays are terminate up to the outer edge of the wall. Kindly confirm the same. | Please refer Sr. no. 4 of table specified under Clause no. 2.0 of Section-Project. The scope is amply clear. Bidder to quote as per provision of Bidding documents.
3 | Annexure-IV (Terminal Connectors) of Section Project- Indore S/s | Cl. No. (C-iii-b) Pg. No. 7/7 | SF6/Air bushings along with terminal connectors & support structures etc. | We would like to inform you that, we will provide only support structure for bushings. Terminal connector shall not in GIS scope of supply. Kindly confirm the same. | Complete equipments/items as per Clause no. (C-iii-b) of Annexure-IV_Section Project are under the Scope of Contractor. Bidder to quote accordingly.
4 | Annexure-IV (Earth Switch) of Section Project- Indore S/s | Cl. No. C-I. i) (v) Pg. No. 6/7 | Three (3) numbers 3-phase, single pole, group operated safety grounding switches, complete with manual and motor driven operating mechanisms. | We would like to inform you that, As per Annexure-IV 3 number of earth switch required for each Bay. We understand that 2 number of ES is use for CB maintanence purpose and one ES for one side of Main Bus & for another side of Main bus ES will be in AIS part. Please clarify the same. | The requirement of E/s & Location is clearly marked on the Tender SLD. Bidder to quote accordingly.
5 | Annexure-IV (Foundation Bolts) of Section Project- Mysore S/s | Cl. No. D-II Pg. No. 7/7 | Single phase SF6/Air bushings along with terminal connectors, support structures, foundation bolts, fasteners etc. as required. | We would like to inform you that, terminal connectors, support structures, foundation bolts, fasteners etc. should be in EPC scope of supply. Kindly accept the same. | Complete equipments/items as per Clause no. D-II of Annexure-IV_Section Project are under the Scope of Contractor. Bidder to quote accordingly.
6 | Annexure-IV (Equipment Description) of Section Project- Mysore S/s | Cl. No. D-II Pg. No. 7/7 | - | We understand that only GIB and GAB is in GIS supply of scope and reamining all equipment will not be in GIS scope. Kindly confirmt he same. | 220kV GIB along with associated items as per Clause no. D-I of Annexure-IV_Section Project and SF6/Air bushings along with associated items as per Clause no. D-II of Annexure-IV_Section Project are under the present scope of Contractor. Bidder to quote accordingly.
7 | TENDER SLD_NAVSARI SS | - | - | We would like to inform you that, In section Project its mentioned that in both ICT feeder GIB are upto outer edge of GIS Hall but in Tender SLD GIB is present scope only for ICT feeder of 765/400kV LV side and not in 400/220kV HV side. so, we follow as per tender SLD. Kindly confirm the same. | Please refer Clause no. 10. (vi) of Specific Requirement of Section Project, where scope of GIB associated with HV side of 400/220kV ICT is amply clear. Bidder to quote as per provision of Bidding documents.
8 | BOQ (Special Tools & Spare Parts) | - | - | We would like to inform you that, Special tool & Spare parts are considered same as per BOQ. Kindly confirm the same. | Bidder to refer clause no. 14.2 of Section-GTR (Rev-15) for Special tools & Tackles.

## 35 PR BSPTCL 2018 (hidden)
|  |  |  | Date: | 2018-07-30
Project | Construction of (2x200MVA+3x50 MVA) 220/132/33KV GSS, Thakurganj(District-Kishanganj) with SAS under Turnkey basis.
Client |  | Bihar State Power Transmission Company Limited.
Contractor |  | Bajaj Electricals Limited.
S.No. | Tender document reference | Clause no. & page no. | Clarification by Contratcor | Response by client | Remarks
1 | General Plot plan |  | Kindly request to provide the general plot plan of the substation area ( length & breadth).
2 | Soil Investigation report |  | Please provide the soil investigation report if avialable for proposed substation area inorder to quantiy the foundation works or Kindly provide safe bearing capacity to be considered at 1.5m below existing ground level.
3 | Contour map |  | Kindly request to provide the contour map for the proposed substation area if available.
4 | Location of site |  | As geotechnical investigation & foundation design is included our scope of work, we would like to do following in proposed substation plot inorder to estimate foundation quantity. 1. Preliminary topographical survey 2. Bore log In this regards, kindly request to provide the plot location of the proposed substation.
5 | Changes in site location |  | We undestand that in case of changes in site location during detailed engineering due to that if we have any impact in foundation type and sizes will be paid as additional to the contarctor, please confirm.
6 | Price schedule -civil works, FFPH building with rest room | sl no. 5-b | Kindly request to provide the area of rooms required to be placed at first floor of pump house building.
7 | Price schedule -civil works, landscaping | sl no. 20 | Kindly request to provide the area required for landscaping and provide the type of landscaping required.
8 | Vol-2D, Civil works, High flood level. | sl no. 25, Page no.12 | In order to finalize the finished ground level of proposed substation, kindly request to provide the highest flood level for proposed substation.
9 | Vol-2D, Civil works, retaining wall/Stone pitching. | sl no. 24-b, Page no.12. | As per mentioned clause, we understand that retaining wall is not required incase of filling less than 2m, whereas for filling up to 2m will required stone pitching slope protection , which will also paid as extra to the contarctor , please confirm.
10 | Vol-2D, Civil works, retaining wall. | sl no. 24-b, Page no.12. | As per mentioned clause, we understand that retaining wall is not required incase of filling less than 2m, whereas for filling above 2m will required same and paid as extra to the contractor as per bihar PWD schdule of rates, please confirm.
11 | Retaining wall and stone pitching |  | In case the above clarification sl no.9 & 10 will not paid additional to contartor, we kindly request to include the item for stone pitching & retaining wall for different heights ( 2m, 2.5, 3m , 3.5m etc.) in price schdule.
12 | Vol-2D, Civil works, Tower and equipment support structure - Galvanization thickness. | sl no. 15-b, Page no.5. | Kindly request to provide the minimum galvanization thickness for structural steel members.
13 | Vol-2D, Civil works, Tower structure - standard drawing. |  | Standard drawings for substation gantry and towers are not avialable in BSPTCL website, kindly request to provide 220kV, 132kV & 33kV tower and gantry GA drawings.
14 | Price schedule -civil works, Boundary wall. | sl no. 21 | Kindly request to rovide BSPTCL standard boundary wall , since same is not available on BSPTCL website.
15 | Price schedule -civil works, dormatory building. | sl no. 18 | Kindly request to provide the standard drawing for dormatory building. OR Kindly provide the area required and type of structure to be considered for dormatory building.
16 | Firewall |  | Please clarify firewall will be paid under which item in price the schdule.
17 | Firewall |  | Kindly request to provide the BSPTCL standard drawings for firewall if any.
18 | Price schdule-Erection, Structural steel for lighting cum lighttning mast. | Sl no. R-2 page no.10 & Sl no. O-1 page no.10 | We understand that structure steel required for lighting cum lightning mast will be paid under Sl no. O-1, page no.10 of erection price schdule, no need to consider additional structural steel quantity for same, please confirm.

## 38 PR BSPTCL 2018 (hidden)
|  |  |  | Date: | 2018-07-30
Project | Construction of (2x200MVA+3x50 MVA) 220/132/33KV GSS, Karmnasha
Client |  | Bihar State Power Transmission Company Limited.
Contractor |  | Bajaj Electricals Limited.
S.No. | Tender document reference | Clause no. & page no. | Clarification by Contratcor | Response by client | Remarks
1 | General Plot plan |  | Kindly request to provide the general plot plan of the substation area ( length & breadth).
2 | Soil Investigation report |  | Please provide the soil investigation report if avialable for proposed substation area inorder to quantiy the foundation works or Kindly provide safe bearing capacity to be considered at 1.5m below existing ground level.
3 | Contour map |  | Kindly request to provide the contour map for the proposed substation area if available.
4 | Location of site |  | As geotechnical investigation & foundation design is included our scope of work, we would like to do following in proposed substation plot inorder to estimate foundation quantity. 1. Preliminary topographical survey 2. Bore log In this regards, kindly request to provide the plot location of the proposed substation.
5 | Changes in site location |  | We undestand that in case of changes in site location during detailed engineering due to that if we have any impact in foundation type and sizes will be paid as additional to the contarctor, please confirm.
6 | Price schedule -civil works, FFPH building with rest room | sl no. 5-b | Kindly request to provide the area of rooms required to be placed at first floor of pump house building.
7 | Price schedule -civil works, landscaping | sl no. 20 | Kindly request to provide the area required for landscaping and provide the type of landscaping required.
8 | Vol-2D, Civil works, High flood level. | sl no. 25, Page no.12 | In order to finalize the finished ground level of proposed substation, kindly request to provide the highest flood level for proposed substation.
9 | Vol-2D, Civil works, retaining wall/Stone pitching. | sl no. 24-b, Page no.12. | As per mentioned clause, we understand that retaining wall is not required incase of filling less than 2m, whereas for filling up to 2m will required stone pitching slope protection , which will also paid as extra to the contarctor , please confirm.
10 | Vol-2D, Civil works, retaining wall. | sl no. 24-b, Page no.12. | As per mentioned clause, we understand that retaining wall is not required incase of filling less than 2m, whereas for filling above 2m will required same and paid as extra to the contractor as per bihar PWD schdule of rates, please confirm.
11 | Retaining wall and stone pitching |  | In case the above clarification sl no.9 & 10 will not paid additional to contartor, we kindly request to include the item for stone pitching & retaining wall for different heights ( 2m, 2.5, 3m , 3.5m etc.) in price schdule.
12 | Vol-2D, Civil works, Tower and equipment support structure - Galvanization thickness. | sl no. 15-b, Page no.5. | Kindly request to provide the minimum galvanization thickness for structural steel members.
13 | Vol-2D, Civil works, Tower structure - standard drawing. |  | Standard drawings for substation gantry and towers are not avialable in BSPTCL website, kindly request to provide 220kV, 132kV & 33kV tower and gantry GA drawings.
14 | Price schedule -civil works, Boundary wall. | sl no. 21 | Kindly request to rovide BSPTCL standard boundary wall , since same is not available on BSPTCL website.
15 | Price schedule -civil works, dormatory building. | sl no. 18 | Kindly request to provide the standard drawing for dormatory building. OR Kindly provide the area required and type of structure to be considered for dormatory building.
16 | Firewall |  | Please clarify firewall will be paid under which item in price the schdule.
17 | Firewall |  | Kindly request to provide the BSPTCL standard drawings for firewall if any.
18 | Price schdule-Erection, Structural steel for lighting cum lighttning mast. | Sl no. R-2 page no.10 & Sl no. O-1 page no.10 | We understand that structure steel required for lighting cum lightning mast will be paid under Sl no. O-1, page no.10 of erection price schdule, no need to consider additional structural steel quantity for same, please confirm.

## 39 PR BSPTCL 2018 (hidden)
|  |  |  | Date: | 2018-07-30
Project | Construction of (2x160MVA+3x50 MVA) 220/132/33KV GSS, Garaul
Client |  | Bihar State Power Transmission Company Limited.
Contractor |  | Bajaj Electricals Limited.
S.No. | Tender document reference | Clause no. & page no. | Clarification by Contratcor | Response by client | Remarks
1 | General Plot plan |  | Kindly request to provide the general plot plan of the substation area ( length & breadth).
2 | Soil Investigation report |  | Please provide the soil investigation report if avialable for proposed substation area inorder to quantiy the foundation works or Kindly provide safe bearing capacity to be considered at 1.5m below existing ground level.
3 | Contour map |  | Kindly request to provide the contour map for the proposed substation area if available.
4 | Location of site |  | As geotechnical investigation & foundation design is included our scope of work, we would like to do following in proposed substation plot inorder to estimate foundation quantity. 1. Preliminary topographical survey 2. Bore log In this regards, kindly request to provide the plot location of the proposed substation.
5 | Changes in site location |  | We undestand that in case of changes in site location during detailed engineering due to that if we have any impact in foundation type and sizes will be paid as additional to the contarctor, please confirm.
6 | Price schedule -civil works, FFPH building with rest room | sl no. 5-b | Kindly request to provide the area of rooms required to be placed at first floor of pump house building.
7 | Price schedule -civil works, landscaping | sl no. 20 | Kindly request to provide the area required for landscaping and provide the type of landscaping required.
8 | Vol-2D, Civil works, High flood level. | sl no. 25, Page no.12 | In order to finalize the finished ground level of proposed substation, kindly request to provide the highest flood level for proposed substation.
9 | Vol-2D, Civil works, retaining wall/Stone pitching. | sl no. 24-b, Page no.12. | As per mentioned clause, we understand that retaining wall is not required incase of filling less than 2m, whereas for filling up to 2m will required stone pitching slope protection , which will also paid as extra to the contarctor , please confirm.
10 | Vol-2D, Civil works, retaining wall. | sl no. 24-b, Page no.12. | As per mentioned clause, we understand that retaining wall is not required incase of filling less than 2m, whereas for filling above 2m will required same and paid as extra to the contractor as per bihar PWD schdule of rates, please confirm.
11 | Retaining wall and stone pitching |  | In case the above clarification sl no.9 & 10 will not paid additional to contartor, we kindly request to include the item for stone pitching & retaining wall for different heights ( 2m, 2.5, 3m , 3.5m etc.) in price schdule.
12 | Vol-2D, Civil works, Tower and equipment support structure - Galvanization thickness. | sl no. 15-b, Page no.5. | Kindly request to provide the minimum galvanization thickness for structural steel members.
13 | Vol-2D, Civil works, Tower structure - standard drawing. |  | Standard drawings for substation gantry and towers are not avialable in BSPTCL website, kindly request to provide 220kV, 132kV & 33kV tower and gantry GA drawings.
14 | Price schedule -civil works, Boundary wall. | sl no. 21 | Kindly request to rovide BSPTCL standard boundary wall , since same is not available on BSPTCL website.
15 | Price schedule -civil works, dormatory building. | sl no. 18 | Kindly request to provide the standard drawing for dormatory building. OR Kindly provide the area required and type of structure to be considered for dormatory building.
16 | Firewall |  | Please clarify firewall will be paid under which item in price the schdule.
17 | Firewall |  | Kindly request to provide the BSPTCL standard drawings for firewall if any.
18 | Price schdule-Erection, Structural steel for lighting cum lighttning mast. | Sl no. R-2 page no.10 & Sl no. O-1 page no.10 | We understand that structure steel required for lighting cum lightning mast will be paid under Sl no. O-1, page no.10 of erection price schdule, no need to consider additional structural steel quantity for same, please confirm.

## 40 PR BSPTCL 2018 (hidden)
|  |  |  | Date: | 2018-07-30
Project | Construction of (2x200MVA+3x50 MVA) 220/132/33KV GSS, Raxaul
Client |  | Bihar State Power Transmission Company Limited.
Contractor |  | Bajaj Electricals Limited.
S.No. | Tender document reference | Clause no. & page no. | Clarification by Contratcor | Response by client | Remarks
1 | General Plot plan |  | Kindly request to provide the general plot plan of the substation area ( length & breadth).
2 | Soil Investigation report |  | Please provide the soil investigation report if avialable for proposed substation area inorder to quantiy the foundation works or Kindly provide safe bearing capacity to be considered at 1.5m below existing ground level.
3 | Contour map |  | Kindly request to provide the contour map for the proposed substation area if available.
4 | Location of site |  | As geotechnical investigation & foundation design is included our scope of work, we would like to do following in proposed substation plot inorder to estimate foundation quantity. 1. Preliminary topographical survey 2. Bore log In this regards, kindly request to provide the plot location of the proposed substation.
5 | Changes in site location |  | We undestand that in case of changes in site location during detailed engineering due to that if we have any impact in foundation type and sizes will be paid as additional to the contarctor, please confirm.
6 | Price schedule -civil works, FFPH building with rest room | sl no. 5-b | Kindly request to provide the area of rooms required to be placed at first floor of pump house building.
7 | Price schedule -civil works, landscaping | sl no. 20 | Kindly request to provide the area required for landscaping and provide the type of landscaping required.
8 | Vol-2D, Civil works, High flood level. | sl no. 25, Page no.12 | In order to finalize the finished ground level of proposed substation, kindly request to provide the highest flood level for proposed substation.
9 | Vol-2D, Civil works, retaining wall/Stone pitching. | sl no. 24-b, Page no.12. | As per mentioned clause, we understand that retaining wall is not required incase of filling less than 2m, whereas for filling up to 2m will required stone pitching slope protection , which will also paid as extra to the contarctor , please confirm.
10 | Vol-2D, Civil works, retaining wall. | sl no. 24-b, Page no.12. | As per mentioned clause, we understand that retaining wall is not required incase of filling less than 2m, whereas for filling above 2m will required same and paid as extra to the contractor as per bihar PWD schdule of rates, please confirm.
11 | Retaining wall and stone pitching |  | In case the above clarification sl no.9 & 10 will not paid additional to contartor, we kindly request to include the item for stone pitching & retaining wall for different heights ( 2m, 2.5, 3m , 3.5m etc.) in price schdule.
12 | Vol-2D, Civil works, Tower and equipment support structure - Galvanization thickness. | sl no. 15-b, Page no.5. | Kindly request to provide the minimum galvanization thickness for structural steel members.
13 | Vol-2D, Civil works, Tower structure - standard drawing. |  | Standard drawings for substation gantry and towers are not avialable in BSPTCL website, kindly request to provide 220kV, 132kV & 33kV tower and gantry GA drawings.
14 | Price schedule -civil works, Boundary wall. | sl no. 21 | Kindly request to rovide BSPTCL standard boundary wall , since same is not available on BSPTCL website.
15 | Price schedule -civil works, dormatory building. | sl no. 18 | Kindly request to provide the standard drawing for dormatory building. OR Kindly provide the area required and type of structure to be considered for dormatory building.
16 | Firewall |  | Please clarify firewall will be paid under which item in price the schdule.
17 | Firewall |  | Kindly request to provide the BSPTCL standard drawings for firewall if any.
18 | Price schdule-Erection, Structural steel for lighting cum lighttning mast. | Sl no. R-2 page no.10 & Sl no. O-1 page no.10 | We understand that structure steel required for lighting cum lightning mast will be paid under Sl no. O-1, page no.10 of erection price schdule, no need to consider additional structural steel quantity for same, please confirm.

## 41 PR BSPTCL 2018 (hidden)
|  |  |  | Date: | 2018-07-30
Project | Construction of (2x160MVA+3x50 MVA) 220/132/33KV GSS, Asthawan.
Client |  | Bihar State Power Transmission Company Limited.
Contractor |  | Bajaj Electricals Limited.
S.No. | Tender document reference | Clause no. & page no. | Clarification by Contratcor | Response by client | Remarks
1 | General Plot plan |  | Kindly request to provide the general plot plan of the substation area ( length & breadth).
2 | Soil Investigation report |  | Please provide the soil investigation report if avialable for proposed substation area inorder to quantiy the foundation works or Kindly provide safe bearing capacity to be considered at 1.5m below existing ground level.
3 | Contour map |  | Kindly request to provide the contour map for the proposed substation area if available.
4 | Location of site |  | As geotechnical investigation & foundation design is included our scope of work, we would like to do following in proposed substation plot inorder to estimate foundation quantity. 1. Preliminary topographical survey 2. Bore log In this regards, kindly request to provide the plot location of the proposed substation.
5 | Changes in site location |  | We undestand that in case of changes in site location during detailed engineering due to that if we have any impact in foundation type and sizes will be paid as additional to the contarctor, please confirm.
6 | Price schedule -civil works, FFPH building with rest room | sl no. 5-b | Kindly request to provide the area of rooms required to be placed at first floor of pump house building.
7 | Price schedule -civil works, landscaping | sl no. 20 | Kindly request to provide the area required for landscaping and provide the type of landscaping required.
8 | Vol-2D, Civil works, High flood level. | sl no. 25, Page no.12 | In order to finalize the finished ground level of proposed substation, kindly request to provide the highest flood level for proposed substation.
9 | Vol-2D, Civil works, retaining wall/Stone pitching. | sl no. 24-b, Page no.12. | As per mentioned clause, we understand that retaining wall is not required incase of filling less than 2m, whereas for filling up to 2m will required stone pitching slope protection , which will also paid as extra to the contarctor , please confirm.
10 | Vol-2D, Civil works, retaining wall. | sl no. 24-b, Page no.12. | As per mentioned clause, we understand that retaining wall is not required incase of filling less than 2m, whereas for filling above 2m will required same and paid as extra to the contractor as per bihar PWD schdule of rates, please confirm.
11 | Retaining wall and stone pitching |  | In case the above clarification sl no.9 & 10 will not paid additional to contartor, we kindly request to include the item for stone pitching & retaining wall for different heights ( 2m, 2.5, 3m , 3.5m etc.) in price schdule.
12 | Vol-2D, Civil works, Tower and equipment support structure - Galvanization thickness. | sl no. 15-b, Page no.5. | Kindly request to provide the minimum galvanization thickness for structural steel members.
13 | Vol-2D, Civil works, Tower structure - standard drawing. |  | Standard drawings for substation gantry and towers are not avialable in BSPTCL website, kindly request to provide 220kV, 132kV & 33kV tower and gantry GA drawings.
14 | Price schedule -civil works, Boundary wall. | sl no. 21 | Kindly request to rovide BSPTCL standard boundary wall , since same is not available on BSPTCL website.
15 | Price schedule -civil works, dormatory building. | sl no. 18 | Kindly request to provide the standard drawing for dormatory building. OR Kindly provide the area required and type of structure to be considered for dormatory building.
16 | Firewall |  | Please clarify firewall will be paid under which item in price the schdule.
17 | Firewall |  | Kindly request to provide the BSPTCL standard drawings for firewall if any.
18 | Price schdule-Erection, Structural steel for lighting cum lighttning mast. | Sl no. R-2 page no.10 & Sl no. O-1 page no.10 | We understand that structure steel required for lighting cum lightning mast will be paid under Sl no. O-1, page no.10 of erection price schdule, no need to consider additional structural steel quantity for same, please confirm.