| Sl. No | Clause No | Existing clause | Amended as |
| --- | --- | --- | --- |
|  | Vol-II Part- A, Section-0 | CONTENTS | Revised contents are attached at Annexure-A |
|  | Vol-II Part- A, Section-1, Bullet 8 of Clause:1.8 | Intent of the Project - Integration with Offline Applications with Main and Backup SLDC. | Intent of the Project Replace with - Integration with Offline Applications with Main and Backup SLDC. The integration with these applications shall be as per the interfaces mentioned in the Technical Specification. |
|  | Vol. II Part-A, Section – 1, Clause no. –1.8, Intent of the Project | ……..If there is any conflicting requirement, the applicable requirement shall be decided by the employer and that shall be binding on the Supplier….. | Replace with ……… If there is any conflict in requirements specified in different sections of technical specification, the applicable requirement shall be decided by the employer and that shall be binding on the contractor….. |
|  | Vol. II Part-A, Section – 1, Clause no. – 1.9 | Overview of the Proposed Systems ……… The existing and new system shall be operated in parallel for minimum three months before shifting the entire operation to the new system. ……… | Replace with Overview of the Proposed Systems ……… The existing and new system shall be operated in parallel for a duration of three months before shifting the entire operation to the new system. ……… |
|  | Vol. II Part-A, Section – 1, Clause no. – 1.10 | Scope of Work a)……Both main and backup control center shall work in active-active mode and in case of failure of main control center backup shall come in role of main without any manual interruption (except commands/signals). b) Integration of existing and New RTUs, SASs, DCPC/ Terminal server with Main and Back up Control Center System. The interoperability profile of existing RTUs……… The devices required for integration of RTUs shall be in the scope of the contractor. The integration of existing and new RTUs at Control center end shall also be in the scope of the Contractor. Further, future bay integration shall not be treated as new RTU integration during AMC period, and any Bay extension during AMC shall be in the scope of the contractor without any commercial implication to the Owner. The term AMC in this Specification shall be read as AMC including extension if any. j.…..The displays shall comply with the Display Building guidelines as per Appendix of vol-II. v.….The new System and existing system shall run in parallel for at least Three months before the dismantling of existing system…… | Scope of Work Replace with - ….. Both main and backup control center shall work in active-active mode and in case of failure of main control center backup shall come in role of main without any manual interruption. However, control command authority shall require explicit transfer. b) Integration of existing and New RTUs, SAS, DCPCs/Terminal Servers with Main and Back up Control Center System. The scope of works under integration of RTU with control centre is inclusive of work of integration (including database and display) with DCPC/Terminal Server also, if any. The interoperability profile of existing RTUs……………. The devices required for integration of RTUs at control centre shall be in the scope of the contractor. Further, future bay integration shall not be treated as new RTU integration during AMC period (including extension if any), and any Bay extension during AMC (including extension if any) shall be in the scope of the contractor without any commercial implication to the Owner. The term AMC in this Specification shall be read as AMC including extension if any, as per provisions mentioned under Clause 1.12.6, Section-1, Part-A of technical specifications along with other scope of works specified under the contract. j.……The displays shall comply with the Display Building guidelines IS 18058: 2023 and as per contract document. v.…...The new System and existing system shall run in parallel for three months before the dismantling of existing system.……. |
|  | Vol. II Part-A, Section – 1, Clause no. – 1.10, Scope of Work | ff) During entire contract period (including extension of contract, if any), if OEM discontinues/ ends support to any item supplied (software/hardware/security solution) under the contract, contractor has to replace such hardware, software (or both, depending on software or hardware dependency) without any additional cost to Owner. Replacement shall be of either same or higher configuration and from same OEMs. | Replace with ff) During entire contract period, if OEM discontinues or declared end of support/end-of-life, whichever is later for any item supplied (Software/Hardware/Security Solution/OS) under the contract, the contractor has to replace such hardware, software (or both, depending on software or hardware dependencies on each-other) as per provisions mentioned under Clause 1.12.6, Section-1, Part-A of technical specifications along with other scope of works specified under the contract. |
|  | Vol. II Part-A, Section-1, Clause No.- 1.10 (II) | Comprehensive AMC……… specified in BOQ. All spare shall have pre-loaded software and required licenses in order to make it readily available for use at all times | Comprehensive AMC……… specified in BOQ. All Spares (except Firewall) shall be fully loaded with licensed OS & SCADA/EMS Application Software to test patch management and keeping ready to use during contingency and failures. The Comprehensive AMC of KASBA & ALDC Control Center of WBSETCL shall be covered under Main control centre AMC BOQ for same duration of WBSETCL and no separate line item has been specified in BOQ for AMC of KASBA & ALDC CC. All the scope of work during AMC defined for SLDC under the proposed contract shall also be applicable for the KASBA & ALDC CC for the items envisaged for KASBA & ALDC CC in BOQ. |
|  | Vol. II Part-A, Section-1, Clause No.- 1.10 (pp) | Scope of work C10 Capacity test shall be done periodically (yearly), to determine whether the rating of battery is holding up using capacity test. If the battery capacity is less than 80% of its design value in any of the cases, the battery shall have to be replaced by contractor during entire period of contract (including extension of contract, if any) without any cost implications to owner. If number of cells replaced (cumulative) in battery bank exceeds more than 25% of total battery bank in any of the cases during entire period of contract (including extension of contract, if any), then contractor shall replace that entire battery bank without any additional cost to the Owner. Also, Refer Section 3 & Section 8 PART C of TS | Scope of work Replace with pp) Capacity test @ C10 shall be done periodically (yearly), for assessment of health of the battery bank (UPS & DCPS wherever applicable) to determine charge holding capacity of battery bank. The conditions for batteries/battery bank replacement for entire period of contract (including extension of contract, if any) is as follows: - Irrespective of the design/expected life of the supplied battery banks, If the battery bank capacity is less than 80% of its design value at end cell voltage of 1.75V/cell in any of the cases, Replacement of faulty battery cells/battery banks shall be in the scope of the contractor, without any cost implication to the Owner. - If the number of cells replaced (cumulative) in the supplied battery bank exceeds more than 25% of total batteries, then contractor shall replace that entire battery bank without any additional cost implication to the Owner. Also, Refer Section 3 & Section 8 of PART C and Section 2 of PART D technical specification. |
|  | Vol. II Part-A, Section-1, Clause No.- 1.10 (qq) | Scope of work Necessary support for providing Security Logs from Firewalls/Other Cyber Security Devices to NCIIPC and integration of supplied SCADA/EMS system with the future Security Operations Center (SOC) and Security Orchestration, Automation and Response (SOAR) systems to be procured by Owner(s). | Scope of work Replace with Necessary support for providing Logs from firewalls/other cyber security devices through SIEM to NCIIPC and for integration of entire SIEM logs with the future Security Operations Center (SOC) and Security Orchestration, Automation and Response (SOAR) systems to be procured by Owner(s). |
|  | Vol. II Part-A, Section – 1, Clause no. – 1.10, Scope of Work | Inserted new clause | tt. The SCADA/EMS system sizing shall be as per the appendix F. The Owner at its own discretion may allocate any unutilized quantum of analog points to status points and status points to analog points as per their requirement, within the overall limit of number of licensed points configured for the LDCs. (uu) Integration & upgradation of existing VPS (8x2) of OPTCL at Main control centre as per Bill of Quantity and comprehensive maintenance during the AMC period for 7 years from the date of SAVT of the project. The contractor scope of work for integration & upgradation of existing VPS is as below: - - Upgradation of the existing VPS. - Integration, testing and validation of existing VPS. - Commissioning of installed hardware. - Supply of Power & Data cables including connectors/connecting cables, if found not suitable. - All necessary software such SCADA/EMS client, Historian client as required for an operator workstation including OS, Endpoint & other agents as required. The contractor shall also be responsible for annual maintenance of the existing VPS modules and controller for a period of 7 years from the date of integration of the existing VPS. This maintenance support for existing VPS shall commence from the date of completion of SAVT of the project. The Contractor shall do all the necessary upgrades/refresh in existing VPS to achieve desired performance for the entire contract duration without any additional cost to Owner. As a minimum, following activity of upgrades/refresh shall be performed by the contractor during commissioning & Integration of existing VPS: - Technical Refresh for replacing LED Chains - Technical refresh for the controller due to OS obsolesce/EOL/EOS including graphics card and drivers. - Technical refresh/Upgrade required to maintain controller desired performance and compatibility with the latest Operating system. - Changing of LED Engines - Ensuring Brightness & healthiness of VPS - Any other refresh/upgrade to maintain desired performance during entire contract duration. - Spare parts availability & support for entire contract duration The contractor shall also be responsible for carrying out technical refresh/replacement during maintenance period of entire contract duration to meet the desired performance without any additional cost to Owner. (vv) Dismantling and buy back of existing UPS Battery bank & battery Charger, Isolation & output Transformer, Input & Output ACDB and Cables from Backup CC of ERLDC (Guwahati, NERLDC) as mentioned in Appendix J. |
|  | Vol-II Part- A, Section-1, para 5 of Clause:1.11 | General Requirements …..The procurement/bid proposal shall be compliant to these standards. The contractor shall ensure compliance with all the statutory guidelines issued during the entire period of contract from all the regulatory bodies. Before supply, the contractor shall certify the items for relevant cyber security standards …. | Replace with General Requirements ….The procurement/bid proposal shall be compliant to these standards. The contractor shall ensure compliance with all the statutory guidelines issued during the entire period of contract from all the regulatory bodies as per the provisions mentioned under Clause 1.12.6, Section 1, PART A of technical specifications along-with other scope of works specified under the contract. Before supply, the contractor shall certify the items for relevant cyber security standards …… |
|  | Vol. II Part-A, Section – 1, Clause no. – 1.11 | General Requirements ….The contractor has to ensure during the entire contract period, if any supplied item (software and hardware including third party solutions/services) under the contract is discontinued / ends support/ is end-of-life, for all such items the contractor has to replace and provide the software/hardware/solution/service as per scope of technical specification without any additional cost to Employer/Owner..… | General Requirements Replace with …. The contractor has to ensure maintenance and services of entire system supplied under the contract during the entire period of contract including extension if any as per provisions mentioned under Clause 1.12.6, Section 1, PART A of technical specifications along-with other scope of works specified under the contract. …. |
|  | Vol. II Part-A, Section-1, Clause No.- 1.11 | General requirements The supplied system (hardware & software) shall comply with cyber security standard relevant clause of the Central Electricity Authority (Technical Standards for Communication System in Power System Operations) Regulations, 2020, Indian or International Security Standards e.g., IT and IT related elements against ISO/IEC 15408 standards, for Information Security Management System against ISO 27000 series Standards, IEC 62443 for OT Network Security, IEC 62351. | General requirements Replace with The supplied system (hardware & software) shall comply with cyber security standard relevant clause of the Central Electricity Authority (Technical Standards for Communication System in Power System Operations) Regulations, 2020, Indian or International Security Standards e.g., IT and IT related elements against ISO/IEC 15408 standards, for Information Security Management System against ISO 27000 series Standards, IEC 62443 (IEC 62443-3-3 and IEC 62443-4-1) for OT Network Security, IEC 62351. |
|  | Vol. II Part-A, Section-1, Clause No.-1.12.2 | Contractor’s Responsibilities and Obligations - Provide Type Test report to the Employer/Owner and if required, conduct type test. The contractor shall submit type test reports for all the equipment as per specification for review & approval by Employer within 30 days of Contract Award. The type test reports submitted shall be of the tests conducted within last five (5) years prior to the date of bid opening. In case the test reports are older than five (5) years ago on the date of bid opening or the type test reports are not meeting the specification requirement, the contractor shall carry out the type testing at no additional cost to the employer. | Contractor’s Responsibilities and Obligations Replace with - Provide Type Test report to the Employer/Owner and if required, conduct type test. The requirement of type test is mentioned at Part-A, Section-3, Clause no. – 3.7.7. New Clause Added - The contractor shall provide Email Interface and SMS Interface application and shall be responsible for integrating with the SMS and EMAIL services provided by the Owner. |
|  | Vol. II Part-A, Section – 1, Clause no. – 1.12.2 | Contractor’s Responsibilities and Obligations - All provisions and orders of DPIIT, MoP, DoT, Meity or any other Nodal Ministry have to be mandatorily complied by the contractor with subsequent amendments in the entire period of contract (including extension of contract, if any)...… | Contractor’s Responsibilities and Obligations Replace with - All provisions and orders of DPIIT, MoP, DoT, Meity or any other Nodal Ministry have to be mandatorily complied by the contractor with subsequent amendments during entire contract period (including extension of contract, if any) as per the provisions mentioned under Clause 1.12.6, Section 1, PART A of technical specifications along-with other scope of works specified under the contract. - All networking equipment (Switches, Routers Firewall etc.) shall comply to the requirement for Mandatory testing & certification of telecom equipment (MTCTE) under the provision of Indian Telegraph (amendment) Rules, 2017. [Refer MoP Order No. 14/02/2021-UR & SI-II-Part- (1) (E-258136) dated 10.01.2024 viz. DoT notification no. 5-2/2021-TC/TEC/185 dated 27.12.2023 for MTCTE compliance of networking equipment as per statutory guidelines. (www.mtcte.tec.gov.in)]. |
|  | Vol. II Part-A, Section-1, Clause No.-1.12.4 | Owner’s Responsibilities and Obligations - Internet connectivity of required bandwidth. - Email Server | Owner’s Responsibilities and Obligations Replace with - Internet connectivity of required bandwidth and public IP for remote diagnostic - Email Server Facility - SMS Service shall be provided by the owner preferably from govt. agencies such as NIC etc. - Adequate Storage Space at site for supply items including spare parts. - Proper environmental conditions for equipment’s supplied under this project at site for their smooth functioning. |
|  | Vol. II Part-A, Section-1, Clause No.-1.12.6 | Maintenance and Support Services Scope | Maintenance and Support Services Scope Inserted Maintenance and Support Services Scope Clause attached at Annexure-A. |
|  | Vol. II Part-A, Section-1, Clause No.-1.15 | Main and Backup Control Center Operational Philosophy …..The takeover of main Control Center functions by Backup Control Center shall not require manual intervention. | Main and Backup Control Center Operational Philosophy Replace with … The takeover of main Control Center functions by Backup Control Center shall not require manual intervention as mentioned at Clause 1.10 of Part A, Technical Specification. |
|  | Volume II, Part-A, Section-1, 1.13, | 1.13 Relocation and Commissioning at New Location (as per BOQ) ………………… Following are the Owner scope of work at control centre which is being shifted during Relocation and Commissioning at New Location: - Transportation, Loading, unloading, F & I of dismantled hardware. - Supply & Laying of Power Cables up to UPS (i.e., Utility Supply to UPS). - ……………………………. Air Conditioning. | Replace with 1.13 Relocation and Commissioning at New Location (as per BOQ) ………………… Following are the Owner scope of work at control centre which is being shifted during Relocation and Commissioning at New Location: - Supply & Laying of Power Cables up to UPS (i.e., Utility Supply to UPS). - ……………………………. Air Conditioning. |
|  | Volume II, Part-A, Section-1, 1.13, Relocation and Commissioning at New Location (as per BOQ) | 1.13 Relocation and Commissioning at New Location (as per BOQ) ………………… …………………. Following are the contractor scope of work at control centre which is being shifted and other affected control centres (if any) during relocation and commissioning at New Location: - Backup of all servers. - …………………… - Technical management. ……………………….. ……………………….. | Replace with 1.13 Relocation and Commissioning at New Location (as per BOQ) ………………… …………………. Following are the contractor scope of work at control centre which is being shifted and other affected control centres (if any) during relocation and commissioning at New Location: - Backup of all servers. - …………………… - Technical management. - Transportation, Loading, unloading, F & I of dismantled hardware. ……………………….. ……………………….. |
|  | Vol. II Part-A, Section-1, Clause No.-1.13.2 | Inserted New Clause | 1.13.2 Integration of existing VPS at SLDC In OPTCL, one existing Video projection system with 16 modules having configuration of 8x2 at Main control centre is to be integrated with SCADA/EMS system. The detail of existing VPS is provided at Part-A, Appendix-L. The contractor scope of work is as below: - - Integration, testing and validation. - Supply of power & data cables (connectors/connecting cables shall be used from existing setup) - All necessary software such SCADA/EMS client, Historian client as required for an operator workstation including OS, Endpoint & other agents as required. |
|  | Vol. II Part-A, Section – 1, Clause no. – 1.17 | Applicable Standards ……….. All latest guidelines issued by regulatory authorities such as MoP CEA, NCIIPC, MEITY etc. shall be complied by the bidders for the offered products (hardware and software) under the project. These should be established and tested product (hardware and software) considering criticality of the system. In this regard, bidder has to comply with order issued by MoP No. 25-11/6/2018-PG dated 2.7.2020 (with all amendments) and CEA Cyber Security in Power System Guidelines, 2021 (with all amendments) throughout the period of contract……… | Applicable Standards Replace with ……….. All latest guidelines issued by regulatory authorities such as MoP, CEA, NCIIPC, MEITY etc. shall be complied by the bidders for the offered products (hardware and software) under the project. These should be established and tested product (hardware and software) considering criticality of the system. In this regard, bidder has to comply with order issued by MoP No. 25-11/6/2018-PG dated 2.7.2020 (with all amendments) and CEA Cyber Security in Power System Guidelines, 2021 (with all amendments) throughout the period of contract as per the provisions mentioned under Clause 1.12.6, Section 1, PART A of technical specifications along-with other scope of works specified under the contract. |
|  | Vol. II Part-A, Section – 2, Clause no. – 2.1 | Training ….. 3rd party Supplied Software Training shall be involved with respective OEMs/authorized partners. ….. | Training Replace with ….. 3rd party Supplied Software & Hardware Training shall be involved with respective OEMs/authorized partners. ….. |
|  | Vol. II Part-A, Section – 2, Clause no. – 2.2.1.3 | 2.2.1.3.2 Application Software Course - EMS (a) EMS Applications: All PSA applications of EMS to be covered along with its integration with PMU and various databases along with all functionalities. | 2.2.1.3.2 Application Software Course – EMS (a) EMS Applications: All PSA applications of EMS supplied under this project, to be covered and various databases along with all functionalities. |
|  | Vol. II Part-A, Section – 3, Clause no. – 3.7.7 | Type Testing ….The Contractor shall submit, within 30 days of Contract Award, copies of test reports and certificates for all of the Type Tests that are specified in the specifications and that have previously been performed. The type test reportssubmitted shall be of the tests conducted within last five (5) years prior to the date of bid opening. In case the test reports are older than five (5) years ago on the date of bid opening or the type test reports are not meeting the specification requirement, the contractor shall carry out the type testing at no additional cost to the Employer/Owner. | Type Testing Replace with ….The Contractor shall submit, within 30 days of Contract Award, copies of test reports and certificates for all of the Type Tests that are specified in the specifications and that have previously been performed. The type test reports submitted shall be of the tests conducted within the duration specified in the Table no. 1 of Part-A, Appendix-M (attached at Annexure-A) from the date of NOA. The type test requirement of LT Switchgear & associated items is explicitly mentioned in Part C, section 9, LT Switchgear In case the test reports are older than specified duration on the date of NOA or the type test reports are not meeting the specification requirement, the contractor shall carry out the type testing at no additional cost to the employer/owner. |
|  | Vol. II Part-A, Section – 4, Clause no. – 4.2, Maintenance support | Maintenance support ……The Owner at their own discretion may extend the duration of maintenance period for up to 2 years based on the same rates, same terms and conditions of the contract. For any addition (e.g. integration of new RTUs or new control center) during maintenance period, contractor shall provide all the services at control center end without any additional cost during entire period of the contract including extension (if any)……. | Maintenance support Replace with …… The Owner at their own discretion may extend the duration of maintenance period for up to 2 years at the same rates, terms and conditions of the contract. During extension of contract (i.e. 8th and 9th years), if any, contractor shall ensure maintenance of supplied items (hardware and software) as per the provisions mentioned under Clause 1.12.6, Section 1, PART A of technical specifications along with other scope of works specified under the contract. For any addition (e.g. integration of new RTUs or integration of new control center) during maintenance period, contractor shall provide all the services at control center end without any additional cost during entire period of the contract including extension (if any) ……. |
|  | Vol. II Part-A, Section – 4, Clause no. – 4.2, Maintenance support | Maintenance support ……… The system availability shall be measured Control Centre wise, for example the availability of Main Control Centre and Backup Control Centre shall be considered separately. Similarly, the availability of various systems for e.g., SCADA/EMS System (Hardware and Software & Video Projection System) shall be considered separately at each of the control Centers. For all third-party equipment (Hardware & Software) Contractor shall have back-to-back support & warranty along with supply of spare with appropriate response time from OEM and these Back-to-Back contracts will be shared with owner before start of defect liability period. Contractor shall be responsible for coordination with the OEM for all matter related to that equipment. The Contractor shall be responsible for meeting the overall response times and availability requirements specified in the Specification. Contractor shall also be responsible for hardware/software replacement/upgradation without any additional cost in case OEM declares end of life/end of support/ obsolescence for the product….. | Maintenance support Replace with ……… The system availability shall be measured Control Centre wise, for example the availability of Main Control Centre and Backup Control Centre shall be considered separately. Similarly, the availability of various systems for e.g., SCADA/EMS System (Hardware and Software & Video Projection System) shall be considered separately at each of the control Centers. The availability of items supplied at KASBA & ALDC Control Center of WBSETCL shall be also considered for calculation of system availability of Main control centre. However, weightage of availability of KASBA & ALDC Control Center items, in calculation of system availability, shall be multiplied by a factor of 0.25 with respect to similar items at Main control centre. The severity and scope of work under AMC of items envisaged for KASBA & ALDC Control Center, shall be same, as that of defined for same items at Main control centre. For all third-party equipment (Hardware & Software) Contractor shall have back-to-back support & warranty along with supply of spare with appropriate response time from OEM and these Back-to-Back contracts will be shared with owner before start of defect liability period. Scope of contractor shall be as per the provisions mentioned under Clause 1.12.6, Section 1, PART A of technical specifications along-with other scope of works specified under the contract. Contractor shall be responsible for coordination with the OEM for all matter related to that equipment. The Contractor shall be responsible for meeting the overall response times and availability requirements specified in the Specification. Contractor shall also be responsible for hardware/software replacement/upgradation without any additional cost in case if any supplied item (software and hardware including third party solutions/services) under the contract is discontinued or declared end of support /end-of-life, whichever is later as per the provisions mentioned under Clause 1.12.6, Section 1, PART A of technical specifications along-with other scope of works specified under the contract.…. |
|  | Vol. II Part-A, Section – 4, Clause no. – 4.2, Maintenance support | f. OEM back-to back support i. All the supplied system shall be under OEM (Hardware and Software) warranty & support till the completion of entire AMC period (including extension of contract, if any). | f. OEM back-to back support Replace with i. All the supplied system shall be under OEM (Hardware and Software) warranty & support as per the provisions mentioned under Clause 1.12.6, Section 1, PART A of technical specifications along-with other scope of works specified under the contract. |
|  | Vol. II Part-A, Section – 4, Clause no. – 4.2, Maintenance support | f(ii). During entire contract period (including extension of contract, if any), if OEM discontinues/ declared ends support to any item supplied (software/hardware/security solution/OS) under the contract, contractor has to replace such hardware, software (or both, depending on software or hardware dependencies on each-other) without any additional cost to Owner. Replacement shall be of either the same or higher configuration keeping required performance specified under the contract and it shall be from the same OEMs. OEM can be changed only after the receipt of letter from OEM regarding non-availability of similar or higher configuration of non-supported item(s). | f. OEM back-to back support Replace with f(ii). During entire contract period, If OEM discontinues / declared end of support/end-of-life, whichever is later for to any item supplied (software/hardware/security solution/OS) under the contract, contractor has to replace such hardware, software (or both, depending on software or hardware dependencies on each-other) without any additional cost to Owner as per the provisions mentioned under Clause 1.12.6, Section 1, PART A of technical specifications along-with other scope of works specified under the contract. |
|  | Vol. II Part-A, Section – 4, Clause no. – 4.14 | Responsibility Matrix | Responsibility Matrix Replace with The revised table 4.5 Responsibility Matrix is attached at Annexure-A. |
|  | Vol. II Part-A, Section – 4, Clause no. – 4.2, Maintenance support | Table 4.1 Maintenance support and Availability requirements System; Scope; System Availability requirements. All systems & subsystem such as SCADA, EMS, AGC, ICCP, Web System, Historian, NMS, VPS, Video Conferencing System, Cyber security system etc. supplied in this project; Hardware and software in Control centres; 99.99%. APS, DG set; 99.99%. | Replace with Table 4.1 Maintenance support and Availability requirements System; Scope; System Availability requirements. All systems & subsystem such as SCADA, EMS, AGC, ICCP, Web System, Historian, NMS, VPS, Cyber security system etc. supplied in this project; Hardware and software in Control centres; 99.99%. APS & DCPS; 99.99%. Video Conferencing System, DG set; Hardware and software for the respective system as applicable in Control Centers; 98%. |
|  | Volume II Part-A Section-4, Clause - 4.2 ,Maintenance support | ---- | New point added (i) Integration of new feeders in LSS/ADMS application and new generating units in AGC application during one year DLP and AMC period including extension if any. |
|  | Volume II Part-A Section-4, Clause - 4.2 ,Maintenance support | - C10 Capacity test shall be done periodically (yearly), to determine whether the rating of battery is holding up using capacity test. If the battery capacity is less than 80% of its design value in any of the cases, the battery shall have to be replaced by contractor during entire period of contract (including extension of contract, if any) without any cost implications to owner. If number of cells replaced(cumulative) in battery bank exceeds more than 25% of total battery bank in any of the cases during entire period of contract (including extension of contract, if any), then contractor shall replace that entire battery bank without any additional cost to the Owner. Also, Refer Section 3 & Section 8 PART C of TS. | Replace with iv. Capacity test @ C10 shall be done periodically (yearly), for assessment of health of the battery bank to determine charge holding capacity of battery bank. The conditions for batteries/battery bank replacement shall be as per the provisions mentioned under Clause 1.10, Section 1, PART A of technical specifications along-with other scope of works specified under the contract. |
|  | Vol. II Part-A, Section-4, Clause No.- 4.3 | Preventive Maintenance Activity (m) Taking an Image back-up of all the Systems. At any time, Last four (04) image back-up shall be maintained. Back-up image shall be tested once in three (03) months using spare servers of all systems. Two (02) copies of back-up shall be maintained on backup appliance (along with other backup details mentioned in Appendix-H, PART-B) and another Two (02) copies shall be maintained, out of which one shall remain with Contractor on SAN/NAS and other with Owner. Contractor shall provide the hard disks (as per item mentioned in BoQ.) for the back-up for owner’s copy. If no BoQ item is mentioned for HDD then Owner shall provide the hard disks for the back-up of owner's copy. | Preventive Maintenance Activity Replace with m) Taking an Image back-up of the supplied systems and retaining number of copies as per retention policy defined under DRS of Backup appliance in Part-B, Appendix-H. Apart from this, Two (02) more copies of back-up shall be maintained outside the backup appliance i.e. one shall be on SAN or NAS and another on external hard disks. Contractor shall provide the hard disks (as per line item mentioned in BoQ) for the back-up for owner’s copy. If no BoQ item is mentioned for hard disk, then Owner shall provide the hard disks for the back-up of owner's copy. Back-up image shall be tested once in three (03) months using spare servers. |
|  | Vol. II Part-A, Section-4, Clause No.- 4.3.1 | Hours of Cover …… The support personnel so deployed shall be qualified personnel having at least 2 years of experience in the SCADA/EMS system including one-year experience in the delivered SCADA/EMS system. The person deputed shall be a permanent employee on the direct pay roll of the contractor | Hours of Cover …… Replace with The Contractor shall provide software engineer at Main & Backup control centre, who are on direct pay roll of the SCADA/EMS OEM/subsidiary of SCADA/EMS OEM. The software personnel so deployed shall be qualified having at least 2 years of experience in the SCADA/EMS system including one-year experience in the delivered SCADA/EMS system. The other engineers (hardware/network engineers/RTU as applicable at respective control centers) shall be on the direct payroll of either contractor or OEM or subsidiary of OEM of the SCADA/EMS. The other engineers (hardware/network engineers/RTU as applicable at respective control centers) so deployed shall have at least 1 year in maintenance of control centre hardware/networking equipment/RTU in the areas of SCADA/EMS/DMS/data center etc. |
|  | Vol. II Part-A, Section-4, Clause-4.3.1 | Hours of cover Table - man power requirement for RTUs AMC 5. Sikkim ¦ 2 ¦ Two RTU Engineer for maintenance | Hours of cover Table - man power requirement for RTUs AMC Sikkim – Deleted |
|  | Vol. II Part-A, Section – 4, Clause no. –4.3.3.3 | Cyber security System monitoring and Monitoring and compliance manager for Critical Infrastructure Protection …… All advisories given by CERT-In / CERT-GO/NCIIPC /CEA/ Meity etc. shall be complied with in the timely manner during entire contract period including extension of contract, if any….. | Replace with Cyber security System monitoring and compliance manager for Critical Infrastructure Protection …. All advisories given by CERT-In / CERT-GO/NCIIPC /CEA/ Meity etc. shall be complied with in the timely manner during entire contract period including extension of contract, if any as per the provisions mentioned under Clause 1.12.6, Section 1, PART A of technical specifications along-with other scope of works specified under the contract. ….. |
|  | Vol. II Part-A, Section – 4, Clause no. –4.3.4, Patch Management | The contractor shall upgrade the various applications delivered under the project through patch management and upgrade to make it compliant with IEC standards as envisaged under the specification during entire contract period including extension of contract, if any. Updated patches shall be applied in the system within the timelines given below. Non-compliance will be considered under Severity-2. | Replace with The contractor shall update patches including security patches in the various applications/solutions delivered under the project through patch management solution and update to make it compliant with IEC 62443 during entire contract period including extension of contract, if any. Updated patches shall be applied in the system within the timelines given below. Non-compliance will be considered under Severity-2. However, if patch update support to any supplied solution gets discontinued by the OEM, the upgradation/replacement of the same shall be done by the contractor without any additional cost to owner. |
|  | Vol-II Part- A, Section-4, Para 1 of Clause- 4.3.8 | Preventive and Break down maintenance of the supplied DCPS & Battery System 19. C-3 discharge test on batteries once a year during 3rd quarterly visit. | Preventive and Break down maintenance of the supplied DCPS & Battery System Replace with 19. Yearly C-10 discharge test on batteries |
|  | Vol-II Part- A, Section-4, Para 1 of Clause- 4.3.9 | Furniture The Furniture and fixtures supplied with the system shall have comprehensive maintenance contract with OEM. Any spares…....……. | Furniture Replace with The Motorized Furniture and fixtures supplied under this contract shall have comprehensive maintenance contract with OEM and for non-motorized furniture supplied under this contract, contractor shall ensure maintenance by themselves or through back-to-back OEM/3rd party support. Any spares….... |
|  | Vol. II Part-A, Section – 4, Clause no. –4.4, Spare Inventory | Spare Inventory ….. The spares shall be used as and when required and no separate charges are payable other than the AMC charges. All spare shall have pre-loaded software and all required licenses in order to make it readily available for use at all times. The Contractor shall be responsible for the availability and quality of these materials (tested and approved as regards reliability of operation). ……. In case mandatory spares (Table 4.2) have been used in the system, the replenishment of such spare shall be done within 45 calendar days (for UPS Spares it shall be 15 calendar days), otherwise it will be considered as non-availability as per Severity-2. All Spares shall be fully loaded with licensed OS and all required Application Software etc. to test patch management and keeping ready to use during contingency and failures….. | Spare Inventory Replace with …… The spares shall be used as and when required and are to be replenished. No separate charges are payable for this replenishment other than the AMC Charges. The Contractor shall be responsible for the quality of the initial and replenished spares supplied during the AMC contract. (tested and approved as regards reliability of operation). …… In case mandatory spares (as specified in Part-B, Appendix-G, Bill of Quantity) have been used in the system, the replenishment of such spare shall be done within 45 calendar days (for UPS Spares it shall be 15 calendar days), otherwise it will be considered as non-availability as per Severity-2. All Spares (except Firewall) shall be fully loaded with licensed OS & SCADA/EMS Application Software to test patch management and keeping ready to use during contingency and failures. |
|  | Vol-II Part- A, Section 4: Maintenance and support Clause 4.5 | Integration of new equipment/control centre ……………. The integration services to be provided by the Contractor will include the Communication Front End (CFE) configuration, addition of New ICCP connection and its integration, addition of interface for off-line Applications, OPC Clients etc…. | Integration of new equipment/control centre ……………. The integration services to be provided by the Contractor will include the RTU integration including DCPC (if applicable), Communication Front End (CFE) configuration, addition of New ICCP connection and its integration, addition of interface for off-line Applications, OPC Clients. Integration scopes inter-alia includes development of database and displays in all the associated system i.e. CFE, OPC, ICCP, SCADA, EMS, AGC integration. Integration of any station on OPC protocol shall be considered as integration of RTU which inter-alia includes configuration, integration, database and display preparation etc. at control centre end. Charges shall be considered accordingly. Contractor shall integrate the Forecasting and Scheduling application (if desired by Owner/employer), supplied under REMC project or procured independently, along-with preparation of associated Database and Display. Payment for the same shall be applicable as per the integration protocol/methodology and rate specified in BoQ……. |
|  | Vol-II Part- A, Section 4: Maintenance and support Clause 4.5 | The numbers specified in BOQ are indicative only. Actual number of RTUs and CCs integration during AMC period may vary. Payment to the contractor shall be based on the unit rate and actual number of RTUs or CCs integrated | The numbers specified in BOQ for Services (Integration and supply) and Annual Maintenance Contract (Integration and supply) including DLP period are tentative only. Actual numbers of services may vary during Services (Integration and supply) and AMC (Integration and supply) including DLP period. Payment to the contractor shall be released based on the unit rate and actual number of services availed. |
|  | Vol. II Part-A, Section – 4, Clause no. – 4.6.1.2, Severity-2 | c) Failure of any redundant system component affecting the critical redundancy like loss of any one Application Processor, Router and CFE would also be included in this category. | Replace with c) Failure of any redundant system component affecting the critical redundancy like loss of any one Application Processor, Firewall, Router, Switch and CFE would also be included in this category. |
|  | Vol. II Part-A, Section – 4, Clause no. – 4.6.1.2, Severity-2 |  | Inserted s) Failure of DG set shall be considered under severity level 2 except condition mentioned above at S.no. (b) of 4.6.1.2. In case of failure of DG set, a maximum time of 24 hrs for arrangement of manpower/spares and travelling shall be provided in the worst case for all RLDC/SLDCs other than Sikkim SLDC. The response time shall be 48 hrs for Sikkim SLDC. t) Failure of complete DCPS or its battery bank shall be considered under severity level 2. In case of failure of DCPS or its battery bank, a maximum time of 24 hrs for arrangement of manpower/spares and travelling shall be provided in the worst case for all RLDC/SLDCs other than Sikkim SLDC. The response time shall be 48 hrs for Sikkim SLDC. The failure of redundant rectifier modules or battery cells of DCPS, not impacting the functioning, shall be treated under severity-3. |
|  | Vol. II Part-A, Section – 4, Clause no. – 4.6.1.3, Severity-3 |  | Inserted …….. The non-functioning of Video Conferencing System shall be treated under severity-3. In case of failure of Video Conferencing System, a maximum time of 48 hrs for arrangement of manpower/spares and travelling shall be provided in the worst case. Failure to replace weak battery cells identified in C-10 capacity test for UPS and DCPS batteries, within a week time, not impacting the functioning of entire UPS system, shall be also treated under Severity-3. |
|  | Vol. II Part-A, Section – 4, Clause no. – 4.8.1 | Availability computation for complete SCADA/EMS System and Auxiliary Power Supply System | Replace with Availability computation |
|  | Vol. II Part-A, Section – 4, Clause no. – 4.8.2 | Payment of maintenance charges (based on SCADA/EMS system and Auxiliary Power supply availability) | Replace with Payment of maintenance charges |
|  | Vol. II Part-A, Section – 4, Clause no. –4.10 | Detailed Scope of work during Warranty and AMC Period viii. Technical upgrade of the installation to the new version (wherever applicable), as and when required, shall be done by the Contractor. Any version upgrade (in version) of the software / tool / appliance by Contractor to be done after taking prior approval of Owner and after submitting impact assessment of such upgrade at no additional cost to Owner. | Detailed Scope of work during Warranty and AMC Period Replace with viii. Technical upgrade of the installation (wherever applicable), as and when required, shall be done by the Contractor. If patch update support to any solution gets discontinued by the OEM, then upgrade (in version)/replacement of the software / tool / appliance by Contractor to be done after taking prior approval of Owner and after submitting impact assessment of such upgrade at no additional cost to Owner. Software embedded with the SCADA/EMS Application software shall not be treated as 3rd party software for this version upgrade requirement subject to security vulnerabilities. |
|  | Vol. II Part-A, Section-4, Clause No.- 4.10 | Detailed Scope of work during Warranty and AMC Period xi) Provide a single-point-of-contact for the resolution of Hardware related problems or to request an equipment upgrade or consultation. If the Hardware supplied by the Contractor is to be replaced permanently, then the Contractor shall replace the equipment of same Make/Model/configuration or of higher configuration. | Detailed Scope of work during Warranty and AMC Period Replace with xi) Provide a single-point-of-contact for the resolution of Hardware related problems or to request an equipment upgrade or consultation. If the Hardware supplied by the Contractor is to be replaced permanently, then the Contractor shall replace the equipment of same configuration or of higher configuration as per the provisions mentioned under Clause 1.12.6, Section 1, PART A of technical specifications along-with other scope of works specified under the contract. |
|  | Vol. II Part-A, Section-4, Clause-4.12.1 | Introduction …..If any special testing equipment/s is/are required for testing and repair of the system, same shall be arranged by the contractor. | Introduction Replace with …..If any special testing equipment/s is/are required for testing and repair of the system, same shall be arranged by the contractor with no additional cost to owner. |
|  | Vol. II Part-A, Section-4, Clause-4.12.3 | Response Time & Uptime Contractor shall depute his engineer so as to reach site within 12 Hrs. of the fault reporting time. This RT is in case of RTU not reporting to control centre. The response time for other type of faults (Analog/Digital data not coming correct/Data validation) shall be 24 Hrs. Uptime/rectification time of the fault shall be 4 Hrs. after access to the site. The contractor engineer shall carry the components which may be required for rectification of the fault based on the preliminary inputs from the repairing site. | Response Time & Uptime Replace with Contractor shall depute his engineer so as to reach site within 12 Hrs. of the fault reporting time. This RT is in case of RTU not reporting to control centre. The response time for other type of faults (Analog/Digital data not coming correct/Data validation) shall be 24 Hrs. Uptime/rectification time of the fault shall be 4 Hrs. after access to the site. The contractor engineer shall carry the components which may be required for rectification of the fault based on the preliminary inputs from the repairing site. |
|  | Vol. II Part-A, Section-4, Clause-4.12.3 | Contractor shall nominate two (02) qualified and experienced engineer/ official at Sikkim SLCD & JUSNL SLDC for maintenance of RTU supplied for Sikkim & JUSNL | Deleted |
|  | Vol. II Part-A, Section – 4, Clause no. – 4.12.4, (c) | C. Integration of new bays & reconfiguration The scope of work under Integration of new bays & reconfiguration work includes- …… Further, integration of new Bays shall not be treated as new RTU integration during AMC period, and any such bay extension during AMC shall be in the scope of the contractor The cost of new bay integration shall be inclusive in the Annual Maintenance charges. | C. Integration of new bays & reconfiguration Replace with A separate line item has been provisioned in Price Schedule & Appendix G for new bay integration at Substation end during AMC period for the scope described below: - The scope of work under Integration of new bays & reconfiguration work includes- …….Further, integration of new Bays shall not be treated as new RTU integration during AMC period, and any such bay extension during AMC shall be in the scope of the contractor. |
|  | Vol. II Part-A, Appendix-B | Interoperability Profile of IEC 60870-5-101 and IEC 60870-5-104 Testing specifications with IEC 60870 5-104 IEC defines IEC 60870-5-601/604 document with the basis test procedures to validate controlling and controlled station that use the standards IEC 60870-5-101/104. The test cases to be executed depend on the device capabilities defined in their interoperability document. | Interoperability Profile of IEC 60870-5-101 and IEC 60870-5-104 Replace with Testing specifications with IEC 60870 5-104 IEC defines IEC 60870-5-601/604 document with the basis test procedures to validate controlling and controlled station that use the standards IEC 60870-5-101/104. The test cases to be executed depend on the device capabilities defined in their interoperability document and shall be used for the conformance testing of the protocol supplied for control center end and RTU supplied under this project. This requirement is not for the routine, field testing and integration at site. …… |
|  | Vol. II, Part-A Appendix-D | Network Architecture | Replace with Network Architecture is revised and attached at Annexure-A. |
|  | Volume II Part-A Appendix-H, Table: Details of New Control Centres under this Project | Details of New Control Centres under this Project. SI. No.; SLDC; Main; Backup. 2; WBSETCL; Howrah; Abhikshan Bhawan. 4; Sikkim; Gangtok; Melli. | Replace with Details of New Control Centres under this Project. SI. No.; SLDC; Main; Backup. 2; WBSETCL; Howrah; NBU. 4; Sikkim; Gangtok; Ranipool. |
|  | Vol. II, Part-A Appendix-J | List of Buy Back items | New item inserted. LIST OF BUY BACK ITEM for BSPTCL, ERLDC Back up, WBSETCL inserted and same is attached at Annexure-A. |
|  | Vol. II, Part-A, Appendix-L | Inserted New Appendix | Appendix-L, Details of Existing VPS is attached at Annexure-A |
|  | Vol. II, Part-A, Appendix-M | Inserted New Appendix | Appendix-M, Type test validity is attached at Annexure-A |
|  | Vol. II Part-B, Introduction | Critical & Non-Critical functions … i) The following functions are classified as Critical functions: j) Cyber Security System | Critical & Non-Critical functions Replace with … i) The following functions are classified as Critical functions: j) Cyber Security System (Firewalls, Routers, Switches etc.) |
|  | Vol. II Part-B, Section-1, Clause 1.1.1 | All the functions for RTU data acquisition as described in the sub-sections below shall be implemented for existing RTUs. Feature shall be available in SCADA System to accumulate data for a user defined time period (i.e.,15-minutes,1- day,1-week,1-month) and it shall be automatically reset the same after user defined time. | Replace with All the functions for RTU data acquisition as described in the sub-sections below shall be implemented for existing RTUs. Feature shall be available in SCADA System to display accumulated data for a user defined time period (i.e.,15-minutes, 30-minutes etc. shall be automatically reset the same after user defined time. Further, for accumulation period of 1-day,1-week,1-month, it can be provided either in SCADA or in historian. |
|  | Vol-II Part- B, Section 1: SCADA System Functions, Para 1 of Clause 1.1.1.3 | Backup Communication Channel Processing …. If valid data cannot be acquired from one of the RTUs, the Control Centre System shall automatically failover to the backup Communication channel. ....... | Backup Communication Channel Processing Replace with …. If valid data cannot be acquired from one of the channels of RTUs, the Control Centre System shall automatically failover to the backup Communication channel.......... |
|  | Vol. II Part-B, Section-1, Clause 1.2.1 | Data Exchange with Control Centres c)Block 4 (information messages) | Data Exchange with Control Centres - Deleted |
|  | Vol. II Part-B, Section-1, Clause- 1.2.3 | Data Exchange with Other Systems & Third-party applications …. The SCADA system shall provide web services that allow multiple applications to exchange any real time data points & vice-versa including alarms and events in secure manner ensuring latest cyber security guideline from statutory authority…. | Data Exchange with Other Systems & Third-party applications Replace with …. The SCADA system shall provide web services either on SOAP or on REST API that allow multiple applications to exchange (bi-directional) any data points (real time, future values (like various forecasts/schedules) including alarms and events in secure manner ensuring cyber security measures and guidelines specified in this specification. Data transfer from SCADA/EMS to IT/Any Other network should be made through secure services such as API calls. As per the requirement of the User, the Contractor shall incorporate new APIs in the SCADA System during AMC period also. If required, the APIs should be modified in such a way that, the corresponding data can only be accessed using API Keys. Standard API to fetch the data from SCADA/EMS system for example SCADA/EMS server and Data Historian server to provide the data to other owner applications. It should at least include the following. - Data values with quality code identified by point id/tag - Multiple values (at least 1000 samples every 10 sec) of same point id/tag with quality code - Range of values of consecutive point id/tag upto 100 nos. - State estimator values, Area Control Errors ……. |
|  | Vol. II Part-B, Section-1, Clause 1.2.3 | SCADA System shall have inbuilt OPC-UA Server and client functionality. ….. | Replace with SCADA System shall have OPC-UA Server and client functionality. ….. |
|  | Vol-II Part- B, Section -1, Clause- 1.2.4 | Data Exchange with Market Applications and Open Access …… All data mentioned in the above bulleted points would be available in one or more of the following formats shall be finalized during detail engineering– • Dedicated API • SOAP/REST • OPC etc…. | Data Exchange with Market Applications and Open Access …… All data mentioned in the above bulleted points would be available in one or more of the following formats shall be finalized during detail engineering– • Dedicated API •Either SOAP or REST • OPC …. |
|  | Vol-II Part- B, Section- 1, Clause 1.3.3 | Calculated Data Processing SCADA/EMS system shall be capable of performing the following calculations at the indicated rates and storing the result in the database as calculated data corresponding to same SCADA field/point and shall be available for display. This calculation output shall not be considered as additional SCADA field/point for system sizing….. | Calculated Data Processing Replace with SCADA/EMS system shall be capable of performing the following calculations at the indicated rates and storing the result in the database as calculated data corresponding to same SCADA field/point and shall be available for display. The inherent Calculations associated with the field point (i.e., MVA, ROC, Min. Max. Avg etc.) shall not be considered as additional SCADA field/point for system sizing…… |
|  | Vol. II Part-B, Section-1, Clause 1.3.1 | c) Limit Monitoring ….. The override value shall be recognized, and any display, report, or log containing the value of the overridden limit shall include it as such. An override value shall be used instead of the permanent value until the user removes the override condition, selects an alternative limit set, or the system is re-initialized…… | c) Limit Monitoring Replace with ….. The override value shall be recognized, and any display, report, or log containing the value of the overridden limit shall include it as such. An override value shall be used instead of the permanent value until the user removes the override condition, selects an alternative limit set…… |
|  | Vol. II Part-B, Section – 1, Clause no. –1.3.3 | Calculated Data Processing ……The user interface and suitable API shall be provided to real time Calculations for SCADA Data as well as estimated Data. There shall be no limitation on number of calculations and arguments involved in each calculation, which shall be defined in the real-time calculations. | Calculated Data Processing Replace with …. Suitable application/GUI/display shall also be provided to define calculations. There shall be no limitation on number of calculations and there shall be capability to create calculations with a number of arguments involved in each calculation as per limit specified in Part-B, Appendix-C. |
|  | Vol. II Part-B, Section-1, Clause 1.3.3.3 | # Rate of Change The rate of change of variables shall be automatically calculated for each analog data using the following formula that filters the rate of change via exponential smoothing: NewRate = A * OldRate + (1 - A) (NewValue - OldValue)/Time Interval ……… | # Rate of Change Replace with The rate of change of variables shall be automatically calculated for each analog data using the following formula that filters the rate of change: NewRate = (NewValue - OldValue)/TimeInterval ……… |
|  | Vol. II Part-B, Section-1, Clause 1.3.3.4 | Average Value Calculations For calculation of the average value of an analog points (all lines, loads, generators and transformers), the sampling frequencies of the point shall be same as scan rate and the time periods duration of interest shall be defined by the user. # Average of value over duration of interest = Sum of values of samples/No. of samples……….. | Average Value Calculations Replace with For calculation of the average value of an analog points (all lines, loads, generators and transformers), the sampling frequencies of the point shall be same as scan rate and the time periods duration of interest shall be defined by the user. The average shall be calculated as time weighted average. # Deleted the formula………. |
|  | Vol. II Part-B, Section-1, Clause 1.3.3.5 | Max. and Min. Value Calculations # …These calculations shall use the real- time clock and initially shall be performed for 15-minute intervals and it should be available to operators for last 24 hours……… | # Max. and Min. Value Calculations Replace with # ………These calculations shall use the real- time clock and initially shall be performed for 15-minute intervals and it should be available to operators for last 24 hours either in SCADA or in Historian ………. |
|  | Vol. II Part-B, Section-1, Clause 1.3.5 | Real-time Data Storage and Playback Para-1 All real-time data shall be continuously available online for at least one (01) year at scan rate for the trending, reporting and playback. Data older than one (01) year shall be automatically archived and shall be accessible for playback if required by owner. Para-2 ….. It shall also be possible to set a different sampling rate for playback than the sampling rate for data storage. It shall be possible to have tabular and graphical trends from the stored data. The trending of graphs from the displays of the playback shall also represent historical data with corresponding time-stamp. Para-3 The user shall be able to view the stored data on SCADA/EMS system displays such as on Single Line diagram, Network Diagram & Trend display by placing a workstation console monitor in a history mode for a specified time and date. Any system displays subsequently called up on that monitor shall display the data that existed at the specified time and date, or the closest previous time available…. Para-5 The users shall be able to select the time window of interest to save part of above playback data in a separate file (file name of the playback data file could be user editable for describing incident/disturbance data contained in the file) for archival of above important data in the Historian system for future retrieval and playback in SCADA system. This archived data shall be transferable in database of Historian system for generation of reports. The snapshot of archived data shall be used by EMS applications in study mode. Para-6 Trending of any Analog Data should be possible during playback period. Playback can be done in same display no changes shall be required for HDR, only selection required input shall be required. | Real-time Data Storage and Playback Replace with Para-1 All real-time data shall be continuously available online for at least one (01) year at scan rate for trending, reporting and playback. Data older than one (01) year shall be automatically archived and shall be accessible for playback if required by owner. Total storage period shall be two years i.e. one year online and one year in archive. Para-2 …It shall also be possible to set a different sampling rate for playback than the sampling rate for data storage. # Para-3 # The user shall be able to view the stored data on SCADA/EMS system displays such as on Single Line diagram, Network Diagram & Trend display by placing a display window in a history mode/playback mode for a specified time and date. Any system displays subsequently called up on that display window shall show the data that existed at the specified time and date, or the closest previous time available….. # Para-5 Deleted # Para-6 …….Playback can be done in same display no changes shall be required for historical data playback, only selection required input shall be required. |
|  | Vol. II Part-B, Section-1, Clause 1.4 | Network Status Processor …..Network Status Processor shall be able to compute availability of elements in real-time and given duration of interest based on historical data of output of NTP. | Network Status Processor …. Para Deleted |
|  | Vol-II Part- B, Section 1: SCADA System Functions. Para 2 of Clause 1.8 | Historian ……Functionalities mentioned under this section (including visualization) shall be meet by the Historian itself and from SCADA wherever specifically mentioned… | Historian Replace with ….. Functionalities mentioned under this section (including visualization) shall be met by the Historian and from SCADA wherever specifically mentioned… |
|  | Vol. II Part-B, Section-1, Clause 1.8.3 | e. Graphical user interface - The UI should have interface with MS tool and XML. | e. Graphical user interface - Deleted |
|  | Vol-II Part- B, Section 1, Clause 1.8.3, Point (b) | Organization of data and configuration The asset or power system topology model hierarchical structure shall be stored in Historian System with versioning/archiving capability, and with roll-ups to aggregate data on real-time basis. The Historian System must be able to link data points held within the Historian to the process model defined in SCADA System. | Organization of data and configuration Replace with The structure of Historian shall be as per power system hierarchical structure with versioning/archiving capability. The Historian System must be able to automatically populate the data points in the Historian once defined/modelled in SCADA System. |
|  | Vol. II Part-B, Section – 1, Clause no. –1.8.3 , Point (c) | Real-time data interfaces The Historian System shall provide real-time, fault-tolerant, high-speed links from any industrial automated real-time data sources through an industry standard interfaces such as multiple OPC industry standards, OPC DA, OPC UA and OPC HDA, connector. Also, it shall have interfaces compatible with DAS (1.0a and 2.0) compliant servers, SOAP, REST, SQL, ODBC, OLEDB, Modbus, ASCII, and text…. | Real-time data interfaces Replace with The Historian System shall have real-time, fault-tolerant, high-speed links for data exchange (import & export) from/to any industrial automated real-time and archived data sources through industry standard interfaces such as multiple OPC industry standards, OPC DA, OPC UA and OPC HDA, connector. Also, it shall have interfaces compatible with either SOAP or REST, SQL, ODBC, OLEDB, Modbus, ASCII, and text (csv/excel formats)….. |
|  | Vol. II Part-B, Section – 1, Clause no. –1.8.3 (d), Calculated values | The calculation engine shall be able to define calculation functions as aggregations; based on equipment type, system voltage, station-wise, region-wise, area-wise, asset type, totalizers (accumulators), and performance equations formulas and shall support periodic or time-based or event-based triggers. | The calculation engine shall be able to define calculation functions as per user requirements and shall support periodic or time-based or event-based triggers. |
|  | Vol. II Part-B, Section – 1, Clause no. –1.8.3 (e), Graphical user interface | …End-users tool to build, modify and manage displays bar-charts (horizontal or vertical), XY plots (as per PART-B, Appendix-B (B14 and B15) and PART-B, Appendix-N also, it can be rotated in any direction), pie-charts, scatter plot, box-plot (refer to Appendix-B(B25) and Appendix-N), duration curve, violin plots, histograms, 3-D plots (single and double surface), multi-state symbols, layers, etc. (refer to Appendix-N)… | Replace with …End-users tool to build, modify and manage displays bar-charts (horizontal or vertical), XY plots (as per PART-B, Appendix-B (B14 and B15) and PART-B, Appendix-N also, it can be rotated in any direction), pie-charts, scatter plot, box-plot (refer to Appendix-B(B25) and Appendix-N), duration curve, violin plots, histograms, 3-D plots (single and double surface) etc. (refer to Appendix-N)… |
|  | Vol. II Part-B, Section – 1, Clause no. –1.8.3 (g), Manual Data Entry | …. An API tool to be provided for bulk insertion of manual data on schedule basis/or on demand. | Replace with ….An API tool to be provided for bulk insertion of data on schedule basis/or on demand. |
|  | Vol. II Part-B, Section – 1, Clause no. –1.8.3 (h) | Interface with Business Applications …. The Historian System must offer connectivity to third party systems using multiple protocols (at least two) e.g; OPC/ ODBC/ OLEDB/ JDBC and web services….. | Interface with Business Applications Replace with …. The Historian System must offer connectivity to third party systems using multiple protocols e.g., OPC, ODBC, OLEDB and web services….. |
|  | Vol-II Part- B, Section 1, Clause no. - 1.8.3, (j) | Interface with External System …The Historian system shall provide web services on SOAP and REST to publish data into the database through multiple applications… | Interface with External System Replace with …The Historian system shall provide web services on either SOAP or REST to publish data into the database through multiple applications… |
|  | Vol-II Part- B, Section 1, Clause no. - 1.8.4 | Reports A Business Tool shall be provided with user friendly configurable with drag and drop query builder, report builder and trend builder facility….. | Reports Replace with A Report Development & Generation Software shall be provided with user friendly configurable with drag and drop query builder, report builder and trend builder facility. |
|  | Vol. II Part-B, Section – 1, Clause no. –1.8.5, Historical Trending | Historical Trending r) Shall be able to put two cursor points on the trend, with a feature to calculate the value difference between the cursor points. | Historical Trending Deleted |
|  | Vol. II Part-B, Section – 2, Clause no. – 2.2, Power System Analysis | - Facility is to be provided to run PSA on Separate Network Model (National/ Regional/ State/Individual Control Area/ Voltage Level). | Replace with - Facility is to be provided to run PSA on Separate Network Model (Regional/ State/Individual Control Area/ Voltage Level). |
|  | Vol. II Part-B, Section-2, Clause No.-2.2 | Power System Analysis c) Import and export a detailed CIM (latest Version) based model of the power system under its area of jurisdiction as well as Power System of boundary-regions (Nearby systems), consisting all the Network elements at 110 kV and above. The supplied system should support IEC 61970-452 (i.e., Equipment Profile), and +IEC 61970-456 (i.e., Analog Measurements Profile, Discrete Measurements Profile, State Variable Profile and Topology Profile) standards. | Replace with Power System Analysis c) Import and export a detailed CIM (latest Version) based model of the power system under its area of jurisdiction as well as Power System of boundary-regions (Nearby systems), consisting of all the Network elements at 110 kV and above. The supplied system shall have feature to convert the older versions of CIM compliant data to latest CIM version and import the same in the EMS system, any tools for such conversion shall also be under the scope of the Contractor. The supplied system should support IEC 61970-452 (i.e., Equipment Profile), and IEC 61970-456 (i.e., Analog Measurements Profile, Discrete Measurements Profile, State Variable Profile and Topology Profile) standards. |
|  | Vol. II Part-B, Section-2, Clause 2.2 | Power System Analysis d) …. EMS application should have compatibility with C.37 protocol for exchange of synchro phasor measurements directly from the available PDC of the control center. | Power System Analysis Replace with d) …. SCADA/EMS system shall have compatibility to exchange PMU data from through respective SCADA system. The number of points is specified Part-B, Appendix-F. |
|  | Vol. II Part-B, Section – 2, Clause no. – 2.2.2 Modelling | - HVDC Links - Two-terminal and multi-terminal HVDC systems with LCC and VSC shall be represented in application with comprehensive converter models and flexible DC network configurations. - FACTS Devices - Popular FACTS devices, such as SVC, STATCOM, TCSC, TCTCT, TCPST and UPFC shall be modelled in application. | Replace with - HVDC Links - Two-terminal HVDC systems and multi-terminal (may be modelled with combination of two-terminal) HVDC systems with LCC and VSC shall be represented in application with comprehensive converter models and flexible DC network configurations. - FACTS Devices - Popular FACTS devices, such as SVC, STATCOM, TCSC shall be modelled in application. |
|  | Vol. II Part-B, Section-2, Clause No. 2.2.5.3 | Alternating Current Model The EMS-CIM should be able to do conversion of third-party network model formats to CIM compliant model and vice versa. | Replaced with Alternating Current Model The EMS-CIM should be able to do conversion of CIM compliant third-party network model formats to another version of CIM compliant model and vice versa. |
|  | Vol. II Part-B, Section-2, Clause No.- 2.2.5.3 Alternating Current Model | r) It shall model Flexible A.C. Transmission Systems (FACTS) devices such as Thyristor Controlled Series Compensator (TCSC), STATCOM, Thyristor Controlled Phase Angle Regulator (TCPAR), etc. s) It shall model Renewable energy sources such as Wind generator, Solar generation and Battery Energy Storage System (BESS) including electrolyser model as per IEEE standard, WECC generic models & user defined model. Model type with attributes will be decided during the finalization of the engineering document. | Replace with r) It shall model Flexible A.C. Transmission Systems (FACTS) devices such as Thyristor Controlled Series Compensator (TCSC), STATCOM etc. s) It shall model Renewable energy sources such as Wind generator, Solar generation and Battery Energy Storage System (BESS) including electrolyser model with attributes will be decided during the finalization of the engineering document. |
|  | Vol. II Part-B, Section-2, Clause 2.2.5.4 | High Voltage Direct Current Model ……. The HVDC model should have the ability to include Multi-terminal HVDC and VSC (Voltage Source Converter) along with conventional models of HVDC also. | High Voltage Direct Current Model Replace with ……. The HVDC model should have the ability to include Multi-terminal HVDC (may be modelled with combination of two-terminal) and VSC (Voltage Source Converter) along with conventional models of HVDC also. |
|  | Vol. II Part-B, Section-2, Clause 2.2.5.5 | HVDC model application - Multi-terminal HVDC | HVDC model application Replace with - Multi-terminal HVDC (may be modelled with combination of two-terminal) |
|  | Vol. II Part-B, Section – 2, Clause no. – 2.2.8, State Estimation | State Estimation shall provide a complete and reliable power system model solution containing information for use by other PSA functions and for display…… | State Estimation shall provide a complete and reliable power system model solution (using weighted least square algorithm or better) containing information for use by other PSA functions and for display…… |
|  | Vol. II Part-B, Section – 2, Clause no. – 2.2.8, State Estimation | User shall be able to select algorithm for State Estimation (SE) out of orthogonal and Weight Least Square Algorithm. | Replace with The state estimation (SE) shall be developed with Weighted Least Square Algorithm or better. |
|  | Vol. II Part-B, Section-2, Clause 2.3 | Dispatcher Training Simulator c) It shall model Renewable energy sources such as Wind generator and Solar model. The generator models of type 1, 2, 3, 4 and 5 must also be provided. Wind model detail is given in Appendix M (2). | Dispatcher Training Simulator Replace with c) It shall model Renewable energy sources such as Wind generator and Solar model. The generator models of type 1, 2, 3 and 4 must also be provided. Wind model detail is given in Appendix M (2). |
|  | Vol. II Part-B, Section-2, Clause 2.3.1 | b) Energy Source and Frequency Models ……The Instructor shall be able to enable/disable (block) governor action on an individual unit basis. The ability to include the steady state effects of automatic voltage regulators (AVRs) and power system stabilizers (PSS) shall be provided…… | b) Energy Source and Frequency Models Replace with …….The Instructor shall be able to enable/disable (block) governor action on an individual unit basis. The ability to include the steady state effects of automatic voltage regulators (AVRs) shall be provided….. |
|  | Vol. II Part-B, Section-2, Clause 2.3.1 | j) User Defined models that can be built from smaller logical blocks (such as low pass filter, high pass filter, differentiator block, integrator block, band pass, band reject filters etd) to simulate the performance of power electronic devices or other non-standard models of equipment such as AVR/PSS etc. | Replace with j) User Defined models that can be built from smaller logical blocks (such as low pass filter, high pass filter, differentiator block, integrator block, band pass, band reject filters etc.) to simulate the performance of power electronic devices or other non-standard models of equipment such as AVR. |
|  | Vol. II Part-B, Section-2, Clause 2.3.2 | Hydro System Model ….. HSM shall include a representation of mechanisms that allow personnel other than the Control Centre computer system user to affect the hydro system plus a simulation of the hydro equipment the Control Centre computer system monitors and controls. HSM shall include the ability to compute …..: | Hydro System Model Replace with ….. HSM shall include a representation of mechanisms that allow personnel other than the Control Centre computer system user to affect the hydro system plus a simulation of the hydro equipment the Control Centre computer system monitors and controls. Since Inflow forecasting is not required in real-time applications, Contractor may develop a simple simulation for reservoir fill level, one inflow value and one spillway outflow value and by defining a relationship between these parameters. HSM shall include the ability to compute …..: |
|  | Vol. II Part-B, Section-2, Clause 2.3.4 | Instructor control c) Probabilistic Events: The instructor shall be able to define an event within a given time interval with a pre-defined probability. Such as there is a 25 percent chance that a load point will increase by 100 MW during the specified time window. | Instructor control Deleted |
|  | Vol-II Part- B, Section -2, Clause- 2.3.4 b) & Point f) Instructor Control | Point (b) Slow Forward (Power System Model only): Allows the Instructor to move a training scenario forward at an Instructor-specified speed slower than real-time. Point (f) Periodic Snapshot: Allows the Instructor to create a historical file that is periodically updated with session data necessary to resume simulation as it occurs during the simulation. The DTS shall not pause while the snapshots are being collected and saved. The snapshot save area shall be circular in nature where the oldest snapshot will be overwritten each time a new snapshot is saved when the save area is full. | Replace with Point (b) Simulation Speed change (slow/fast) (Power System Model only): Allows the Instructor to move a training scenario forward at an Instructor-specified speed other than real-time simulation. Point (f) Periodic Snapshot: Allows the Instructor to create a historical file that is periodically updated with session data necessary to resume simulation as it occurs during the simulation. The snapshot save area shall be circular in nature where the oldest snapshot will be overwritten each time a new snapshot is saved when the save area is full. |
|  | Vol. II Part-B, Section – 2, Clause no. – 2.4, Automatic Generation Control (AGC) | Pan India AGC with all 5 regions and constituents within it could be considered as one control area with user flexibility to spilt/merge control areas. Each regional/state/constituents entity power station within its jurisdiction is a control area by itself. Split/Merging of control area should be user dependent without any limitation on creation of number of new control areas. Each of the neighbouring country power system interconnected with the National Grid shall be defined as another control area for defining the trans-national exchanges. | Replace with AGC being supplied at RLDC/SLDCs shall be considered as one control area i.e. Region for RLDC and State for SLDC with user flexibility to spilt/merge control areas within the jurisdiction of respective RLDC/SLDCs. Each regional/state/constituents’ entity within its jurisdiction is a control area by itself. Split/Merging of control area should be user dependent without any limitation (either technical or commercial) on creation of number of new control areas. Each of the neighbouring region/state power system interconnected with the Grid shall be defined as another control area. |
|  | Vol. II Part-B, Section – 2, Clause no. – 2.4.1, Generation Control | .....These functions shall monitor and coordinate generation while supporting state, regional and national LDC operating personnel…….. | Replace with .....These functions shall monitor and coordinate generation while supporting state and regional LDC operating personnel…….. |
|  | Vol-II Part- B, Section -2, Clause 2.4.1.1 Operations Monitor | The following calculations as a minimum shall be performed at an adjustable periodicity (initially set to 1 minute; minimum configurable periodicity shall be 2 second) and shall consider quality of every signal. | The following calculations as a minimum shall be performed at an adjustable periodicity (with minimum configurable periodicity shall be 2 second and can be set to 1 minute, 5 mins, 15 mins and 60 mins as per system requirement) and shall consider quality of every signal. |
|  | Vol. II Part-B, Section – 2, Clause no. – 2.4.1.1, Operations Monitor | - Actual Generation MW: - Total for all India - Total for each control area - Total for each company/part…. - Total number of plants…… Generation shall be mentioned fuel-wise also. | Replace with - Actual Generation MW: - Total for each control area i.e. RLDC/SLDCs/Sub SLDCs - Total for each company/part…. - Total number of plants…. Generation shall be mentioned fuel-wise also. |
|  | Vol. II Part-B, Section – 2, Clause no. – 2.4.1.1, Operations Monitor | (b) Spinning Reserve MW: 1) Total for all India 2) Total for each control area 3) Total for each company/part…. 4) Total for cross Border, international (as applicable). 5) Up and Down…… ….. | Replace with (b) Spinning Reserve MW: (1) Total for each control area i.e. RLDC/SLDCs/Sub SLDCs. (2) Total for each company/part…… (3) Up and Down…… …………………………………….. |
|  | Vol. II Part-B, Section – 2, Clause no. – 2.4.1.1, Operations Monitor | Net Interchange MW (actual, scheduled, and deviation from schedule): Net Interchange definitions and calculations shall be user-definable: (1) Net for all India and breakdown per region and control area. | Replace with Net Interchange MW (actual, scheduled, and deviation from schedule): Net Interchange definitions and calculations shall be user-definable: (1) Net for respective RLDC/SLDCs/Sub SLDCs and breakdown per region and control area. |
|  | Vol. II Part-B, Section – 2, Clause no. – 2.4.1.1, Operations Monitor | (e) Actual Drawl MW (including transmission losses): - Total for all India - Total for each control area. - Total for regional entities - Total for Inter-Regional ……………………….. | Replace with (e) Actual Drawl MW (including transmission losses): - Total for each control area i.e., RLDC/SLDCs/Sub SLDCs - Total for regional entities - Total for Inter-Regional ……………………………………. |
|  | Vol. II Part-B, Section – 2, Clause no. – 2.4.1.1, Operations Monitor | (f) Area Control Error (ACE): ACE for operating (5-Five Regions and constituents within each Regions) and processed ACE values shall be calculated based on actual frequency, actual net interchange (regional/state and constituents), scheduled frequency, and scheduled net interchange. Control areas and associated ACE calculations will be defined by Employer/Owner during project implementation. Flexibility to create new control areas shall be provided. (1) For all India (2) For each control area. | Replace with (f) Area Control Error (ACE): ACE for operating areas of respective region/state and processed ACE values shall be calculated based on actual frequency, actual net interchange (regional/state and constituents), scheduled frequency, and scheduled net interchange. Control areas and associated ACE calculations will be defined by Employer/Owner during project implementation. Flexibility to create new control areas shall be provided. (1) For each control area as RLDC/SLDCs/Sub SLDCs |
|  | Vol. II Part-B, Section-2, Clause 2.4.1.2 | Automatic Generation Control Functions ……. There shall be suitable display at operator screen to monitor the following parameters: • Status and Mode of AGC Operation for each of the Area • Graphical trend of ACE for each area • Total Load and Generation of the respective area • Spinning reserve (both Up and Down reserves) and operating reserve requirement of the respective area • Spinning reserve (both Up and Down reserves) and operating reserve availability of the respective area • AGC despatchable margin (both Up and Down margins) of the respective area Automatic Generation Control Functions | Automatic Generation Control Functions Replace with …… There shall be suitable display at operator screen to monitor the following parameters: • Status and Mode of AGC Operation for each of the Area • Graphical trend of ACE for each area • Total Load and Generation of the respective area • Spinning reserve (both Up and Down reserves) and operating reserve requirement of the respective area • AGC despatchable margin (both Up and Down margins) of the respective area |
|  | Vol-II Part- B, Section 2, Para 3 of Clause 2.4.2.3 Generating Unit Limits Bullet 3, 4, 9 &10 Additional limits and Prohibited Zones for Hydro Power Plants Bullet 2 P2 & P3 Limits | …. 3) Regulating Max: This limit is the summation of ULSP+OFFSET for each unit. OFFSET is entered manually for each unit in the AGC software. This allows LDC to restrict DeltaP. 4) Regulating Min: This limit is the summation of ULSP-OFFSET for each unit. OFFSET is entered manually for each unit in the LDC AGC software. This allows LDC to restrict DeltaP. … 9) In-effect Regulating Max: In-effect Regulating Max is the lowest value amongst all the limits. In-effect Regulating Max = min (Telemetered Max, Regulating Max, Name plate Max, Dispatch Entered Max). 10)In-effect Regulating Min: In-effect Regulating Min is the highest value amongst all the limits. In-effect Regulating Min = max (Telemetered Min, Regulating Min, Nameplate Min, Dispatch Entered Min) …. 2. P2 & P3 Limits: P2 – P3 is the forbidden zone / cavitation zone for all the Francis turbine based hydro power plants … | …. 3) Regulating Max: This limit is the summation of ULSP+OFFSET for each unit. OFFSET is entered manually/API based for each unit in the AGC software. This allows LDC to restrict DeltaP. 4) Regulating Min: This limit is the summation of ULSP-OFFSET for each unit. OFFSET is entered manually/API based for each unit in the LDC AGC software. This allows LDC to restrict DeltaP. … 9) Commercial Limit Max: It is the highest value amongst ULSP and Maximum Capacity of unit. Commercial Limit Max = Max (ULSP, Cap_Max) 10) Commercial Limit Min: It is the lowest value amongst ULSP and Minimum Capacity of unit. Commercial Limit Min = Min (ULSP, Cap_Min) 11) In-effect Regulating Max: In-effect Regulating Max is the lowest value amongst all the limits. In-effect Regulating Max = min (Telemetered Max, Regulating Max, Name plate Max, Dispatch Entered Max, Commercial Limit Max). 12)In-effect Regulating Min: In-effect Regulating Min is the highest value amongst all the limits. In-effect Regulating Min = max (Telemetered Min, Regulating Min, Nameplate Min, Dispatch Entered Min, Commercial Limit Min). …. 2. P2 & P3 Limits: P2 – P3 is the forbidden zone / cavitation zone for all the Francis turbine based hydro power plants with threshold MW Limits on actual MW at boundary of P2 & P3. … |
|  | Vol. II Part-B, Section-2, Clause 2.4.1.2 | Automatic Generation Control Functions ……. At the RLDC/SLDCs the capability shall be provided for the dispatcher to monitor the execution of the Generation Control applications within the RLDCs/SLDCs through periodically and on-demand updated Generation/Load Summary displays. Data for each generating unit region wise shall be displayed. | Automatic Generation Control Functions Replace with ……At the RLDC/SLDCs the capability shall be provided for the dispatcher to monitor the execution of the Generation Control applications within the RLDCs/SLDCs through periodically updated Generation/Load Summary displays. Data for each generating unit region wise shall be displayed. |
|  | Vol. II Part-B, Section-2, Clause 2.4.2.4 | Turbine Control Logic ........ when a unit fails to respond. The response models shall include stored energy effects so as to allow selected units to move faster than their response rate limit for a short period. Unit dead bands and other logic shall be used to avoid issuing control signals smaller than the control resolution of units while at the same time ensuring that control errors do not accumulate. | Turbine Control Logic Replace with …. when a unit fails to respond. Unit dead bands and other logic shall be used to avoid issuing control signals smaller than the control resolution of units while at the same time ensuring that control errors do not accumulate. |
|  | Vol-II Part- B, Section- 2, Clause- 2.4.2.8 | AGC Performance Monitor ….... It shall be possible to generate input vs output scatter plots and Correlation numbers. configurable for Daily, Weekly, Monthly, Annual assessments. Statistics shall be maintained as required to complete the defined Performance Criteria….. | AGC Performance Monitor Replace with .... It shall be possible to generate input vs output scatter plots and Correlation numbers, configurable for Daily, Weekly, Monthly, Annual assessments. Performance statistics may be retrieved from the historian/reporting tool. Statistics shall be maintained as required to complete the defined Performance Criteria..... |
|  | Vol-II Part- B, Section -2, Clause 2.4.5 | Production Statistics Production Statistics (PS) shall be provided at the RLDC/SLDCs to maintain an accurate accounting of relevant production performance, production cost, plant availability factor, scheduled vs actual generation, and daily/weekly/ monthly/annually generation regulation participation. Results shall be saved for display and trending and historical purposes and for daily and monthly reports. ….. | Production Statistics Replace with Production Statistics (PS) shall be provided at the RLDC/SLDCs to maintain an accurate accounting of relevant production performance, production cost, plant availability factor, scheduled vs actual generation, and daily/weekly/ monthly/annually generation regulation participation. Production statistics may be retrieved from the historian/reporting tool. Results shall be saved for display and trending and historical purposes and for daily and monthly reports. ….. |
|  | Vol-II Part- B, Section 2, Clause: 2.5.1, other features | Voltage Security Assessment Tool ……. - Data conversion tool to import power flow data in third-party formats including PSS/E, PSLF, Power Factory etc. …… - Analysis of power systems of up to 100,000 buses. | Voltage Security Assessment Tool ….. Replace with - Data conversion tool to import power flow data in third-party formats including PSS/E, PSLF etc. .…… - Analysis of power systems of buses as per Part-B, Appendix F. |
|  | Vol-II Part- B, Section 2, Clause: 2.5.2 | Transient Security Assessment Tool Detailed Contingency Analysis … For compliance studies (such as IEGC), contingencies shall be created by preset rules. | Transient Security Assessment Tool Detailed Contingency Analysis … Replace with For compliance studies, contingencies shall be created by pre-set rules. |
|  | Vol-II Part- B, Section 2, Clause 2.5.2 | Transient Security Assessment Tool Management and validation of remedial action/measures : ….. Adapted relay settings … | Transient Security Assessment Tool Management and validation of remedial action/measures :…. Deleted ….. |
|  | Vol-II Part- B, Section- 2, Model Library, Clause 2.5.2 Transient Security Assessment Tool | Bullet-9 FACTS model library: SVC/SVS, TCBR, STATCOM, TCSC, SSSC, TCMCT, TCPST. Bullet-10 HVDC model library: Two- and multi-terminal HVDC models (LCC and VSC (Bipolar and symmetrical Monopole models)), DC grid modelling, Full bridge and Half bridge based MMC based VSC models. | Replace with Bullet-9 FACTS model library: SVC/SVS, STATCOM, TCSC. Bullet-10 HVDC model library: Two- and multi-Terminal (may be modelled with combination of two-terminal) HVDC models (LCC and VSC (Bipolar and symmetrical Monopole models)), DC grid modelling, Full bridge and Half bridge based VSC models. |
|  | Vol. II Part-B, Section-2, Clause 2.5.2 | Transient Security Assessment Tool Case Setup and Output Analysis…… - Batch plotting capability based on scripting language. | Transient Security Assessment Tool Case Setup and Output Analysis…… - Deleted |
|  | Vol-II Part- B, Section 2, Clause 2.5.2 | Transient Security Assessment Tool - Feature to integrate with EMS for on-line dynamic security assessment. - Generation of simulated PMU signals in IEEE C37.118 format from near real-time simulations - Creation of the complete contingency set automatically according to NERC TPL standard. - Feature of performing hybrid simulations with an electromagnetic transient simulation engine. - Power system components shall be identified using bus numbers, bus names, or equipment names. - Model and data verification tools – - Exciter/governor/renewable generator step response simulations. - No disturbance test simulation. - Injection of bus V magnitude/frequency curves (“playback simulations”). - Case archive feature to store or share study cases. - Snapshot feature to pack a simulation for later continuation of the simulation. - Data conversion tool to import power flow and contingency data in third-party formats including PSS/E, PSLF, BPA, etc. - Distributed computation to enable simultaneous simulations of multi-contingency/scenario cases on multiple servers, or multiple CPU cores. Analysis of power systems of up to 100,000 buses and 15,000 generators. | Transient Security Assessment Tool Replace with - Feature to integrate with EMS for on-line dynamic security assessment. - Generation of simulated PMU signals from near real-time simulations - Creation of the complete contingency set automatically. - Power system components shall be identified using bus numbers, bus names, or equipment names. - Model and data verification tools – - Exciter/governor/renewable generator step response simulations. - No disturbance test simulation. - Injection of bus V magnitude/frequency curves (“playback simulations”). - Case archive feature to store or share study cases. - Snapshot feature to pause a simulation for later continuation of the simulation. - Data conversion tool to import power flow and contingency data in third-party formats including PSS/E, PSLF etc. - Distributed computation to enable simultaneous simulations of multi-contingency/scenario cases on multiple servers, or multiple CPU cores. - Analysis of power systems elements as per Part B, Appendix-F |
|  | Vol. II Part-B, Section-2, Clause 2.5.3 | Small Signal Analysis Tool The eigen-value computation algorithms may also be provided if it is an inherent part of the standard offering of the small signal analysis application. | Small Signal Analysis Tool This paragraph deleted |
|  | Vol-II Part- B, Section 3: Clause - 3.4 | User Interface Environment ……. Geo-spatial display shall be updated on monthly or on-demand basis. Getting dynamic map tiles through map server shall be the owner’s responsibility but its corresponding integration and deployment in displays shall be the responsibility of contractor. | User Interface Environment Replace with …... Geo-spatial display shall be updated on monthly or on-demand basis. Providing map server, getting dynamic map tiles through map server and its subscription shall be the owner’s responsibility but its integration and deployment in displays shall be the responsibility of contractor. However, if on-line map tiles are not available, the geo-spatial displays shall be provided with downloaded offline map tiles. |
|  | Vol-II Part- B, Section 3: Clause - 3.6 | Display recording and playback A licensed application in the main User Interface itself shall be delivered to capture any display screen continuously. The recording should enable playback in standard format such as mp4. The video-file shall get played in any standard video-player software. Video recording shall also be possible in historical reconstruction over a display. | Display recording and playback Replace with A licensed application (DISPLAY SCREEN RECORDING SOFTWARE as specified in BoQ) in the main User Interface itself shall be delivered to capture any display screen continuously. The recording should enable playback in standard format such as mp4. The video-file shall get played in any standard video-player software. Video recording shall also be possible in historical reconstruction over a display. |
|  | Vol-II Part- B, Section 3: Clause - 3.7.2 | Display Note Pad/Memo …….A link to navigate the corresponding SLD shall be available in the same summary display Provision for “Group based Note-Pad/Memos” and “Global Note-Pad/Memos” shall be provided with following visibility requirements:- • Global Note-Pad/Memos: shall be visible to all categories of users. • Group Based Note-Pad/Memos: shall be visible only to specific user-group type (e.g. Dispatcher, Programmer, etc.). | Display Note Pad/Memo Replace with …….A link to navigate the corresponding SLD shall be available in the same summary display Provision for “Global Note-Pad/Memos” shall be provided with following visibility requirements:- • Global Note-Pad/Memos: shall be visible to all categories of users. |
|  | Vol. II Part-B, Section-3, Clause 3.8.3 | Trending (SCADA Application) Trending is a display of series of values of parameters on a time axis. Graphical trends shall be supported by the system for both real-time SCADA data and Historical data separately as per user selectable source for trending. The minimum features to be provided as part of Trending are listed below -…… Bullet No. 6 - Trending of at least 10 parameters on the same display shall be supported (with no limitation on nos. of such trend displays). - …. Bullet No. 10 - Major and minor interval of x & y axis should be user configurable for any data or time. There shall not be any limitation of trends associated with a single display. - … Bullet No. 18 - Trending application shall have standard regression functionalities like linear, polynomial and exponential etc. - .…… | Replace with Trending Trending is a display of series of values of parameters on a time axis. Features specified herein under shall be supported by the supplied systems. The minimum features to be provided as part of Trending are listed below – …… Bullet No. 6 - Trending of at least 10 parameters on the same display shall be supported and with minimum 100 nos. of such trend displays. - …. Bullet No. 10 - Major and minor interval of x & y axis should be user configurable for any data or time. - …. Bullet No. 18 - Deleted - …… |
|  | Vol-II Part- B, Section 3: Clause - 3.8.3.1 | Graphical Trending m) Trend point marker functionality to compare the data for different periods. | Graphical Trending Replace with m) Trend point marker functionality to compare the data for different periods on a single trend window. |
|  | Vol-II Part- B, Section 3: Clause - 3.9 | Alarms ….. The minimum features required in alarm messages system are listed below- …… Bullet No. 8 - Minimum 1,00,000 (One Lakhs) alarm messages shall be available in real-time. | Alarms ….. The minimum features required in alarm messages system are listed below- …… Replace with Bullet No. 8 - Minimum 20,000 on alarm messages shall be available in real-time. The system shall support upto 1,00,000 alarm to be displayed (auto refresh) either through SCADA or SCADA-Historian on demand by the operator. |
|  | Vol. II Part-B, Section-3, Clause 3.9.1 | Alarm Categories …..A means shall be provided for changing operating shifts without reassignment of alarm categories at a console. Console failure shall result in automatic reassignment of alarms to other consoles in a pre-defined manner and shall generate an alarm. ….. | Alarm Categories: Replace with ….. A means shall be provided for changing operating shifts without reassignment of alarm categories at a console. Console failure shall generate an alarm and the user shall be able to reassign the alarms of failed console to other consoles in a pre-defined manner. …… |
|  | Vol. II Part-B, Section-3, Clause 3.9.2 | Alarm Priority levels Each alarm shall be assigned to an alarm priority level. Minimum 16 alarm priority levels shall be supported.…… Every Alarm shall be accompanied by an Audible tone (different audio tones for different types of Alarms configurable by the user) which shall be user configurable also in real time for some particular events also. | Alarm Priority levels Replace with Each alarm shall be assigned to an alarm priority level. Priority levels mentioned in Part-B, Appendix-C shall be supported……… Every Alarm shall be accompanied by an Audible tone. The different audio tones for different types of Alarms shall be configurable by the programmer/engineer for some particular events also. |
|  | Vol. II Part-B, Section-3, Clause 3.9.8 | Events ……Event messages shall be displayed on an events summary. Event messages shall be archived in chronological order. Minimum 100000 (One Lakhs) event messages shall be available in real-time. It shall be possible to sort, display, filter and print event messages from any console.……. | Events Replace with ……Event messages shall be displayed on an events summary. Event messages shall be archived in chronological order. Minimum 20000 event messages shall be available in real-time. The system shall support upto 1,00,000 events to be displayed (auto refresh) either through SCADA or SCADA-Historian on demand by the operator. It shall be possible to sort, display, filter and print event messages from any console. |
|  | Vol-II Part- B, Section 3, Clause: 3.13.16 | ### Voltage Profile Display Voltage profile displays shall be provided to present different voltage levels on a geographical display in form of contours & heat map. Further, the areas with various voltage levels shall be shown with different colours.. | ### Voltage Profile Display Replace with ### Voltage profile displays shall be provided to present different voltage levels on a geographical display in form of contours & heat map either based on the per unit values or based on the actual value. Further, the areas with various voltage levels shall be shown with different colours…… |
|  | Vol. II Part-B, Section-3, Clause 3.14.16 | ### Contour & Heat Map Displays ….Geo-spatial display with contour map of Data within geographical boundary of India shall be provided in which Zoom-in, Zoom-out, Panning option shall be available in the map. Display Builder shall be capable of importing point and placing a predefined picture/symbol as per the Latitude and Longitude specified by the user. ### The“ Playback” option shall be made available in the map so that the continuous pattern over the period of time shall be visualized. The pattern shall be exported in a video format so as to use it in offline mode………. | ### Contour & Heat Map Displays Replace with ……….Geo-spatial display with contour map of Data within geographical boundary of region/state shall be provided in which Zoom-in, Zoom-out, Panning option shall be available in the map. Display Builder shall be capable of importing point and placing a predefined picture/symbol as per the Latitude and Longitude specified by the user. ### The “Playback” option feature shall also be made available in the Geo-spatial display pattern over the period of time shall be visualized. The pattern shall be exported in a video format so as to use it in offline mode. |
|  | Vol. II Part-B, Section-3, Clause 3.14.24 | Weather data on Geographical map display ### The display shall show the weather data superimposed on a geographical display with background such as “Google Maps/Bhuwan Maps/etc.” A sample illustration is included in Appendix –B(B16). | ### Weather data on Geographical map display Replace with The display shall show the weather data superimposed on a geographical display with background such as “Google Maps/Bhuwan Maps/etc.” A sample illustration is included in Appendix –B(B16). Weather data shall be provided by owners. However, the contractor shall display map superimposing weather data. |
|  | Vol. II Part-B, Section-4, Clause- 4.1 | General Requirements …..Bidder has to provide the latest version of all third party application software supplied under the project before the start of Factory Acceptance Test (FAT) without any cost implication. The contractor shall provide details of all the API’s including its source code supplied/used under the contract to the owner without any additional cost. | General Requirements Replace with ….The Contractor shall provide the latest version of all third party application software supplied under the project before the start of Factory Acceptance Test (FAT) without any cost implication. The 3rd party software embedded with the SCADA/EMS Application software shall not be treated as 3rd party software for this version upgrade requirement subject to security vulnerabilities. ### The contractor shall provide details of all the API’s (used in the project) including its source code supplied/used under the contract to the owner without any additional cost. |
|  | Vol. II Part-B, Section – 4, Clause no. – 4.2.1 | Design and Coding Standards for SCADA/EMS applications ….. h) Antivirus Software - All computers and firewalls shall be provided with the latest antivirus software as on date of supply. The antivirus software shall have the capability of having its virus definitions updated from time to time. The Contractor shall be responsible for the maintenance & update of the antivirus software. | Design and Coding Standards for SCADA/EMS applications …… Replace with h) Application Logging - The SCADA/EMS system applications shall have logging that contains information regarding events occurred within the software application. These events logged out by the application shall be written and stored in a file. The feature to export the logs in text format for any of the SCADA/EMS application shall be provided. The event logs include errors and warnings as well as informational events. The types of information and format of messages found in an application log file shall generally include - - Context information: Background information that provides insight into the state of the application at the time of the message. - Timestamps: A specific piece of contextual information for tracking and correlating issues. - Log levels: Labels that help calculate the level of importance for the entries in log file. Levels such as include INFO, DEBUG, WARN, and ERROR. The logs shall be in sufficient details to support the following - - Troubleshooting: Logs shall help identify the root cause of errors or unexpected behaviour by providing context and clues for efficient issue resolution. - Monitoring: Logs shall help in real-time monitoring of performance and health is enabled, allowing detection of anomalies and ensuring optimal application operation. - Auditing and Compliance: Logs shall help meet regulatory requirements by recording events and user actions for security and compliance purposes. - Performance Optimization: Logs shall help identify performance bottlenecks and areas for improvement, leading to better resource allocation. - Security Analysis: Logs shall assist in detecting security breaches and unauthorized access, enhancing application security. |
|  | Vol. II Part-B, Section – 4, Clause no. – 4.2.2 | Operating System ………..The system security shall also be maintained in line with cyber security guidelines/recommendations issued by various statutory authorities like CEA, CERT-In, NCIIPC, MeITY etc. from time-to-time throughout the life cycle of the project……. | Operating System Replace with ………. The system security shall also be maintained in line with cyber security recommendations/guidelines issued by various statutory agencies like CERT-In, NCIIPC, CEA, Meity etc. from time-to-time during entire contract period (including extension of contract, if any) as per the provisions mentioned under Clause 1.12.6, Section 1, PART A of technical specifications along-with other scope of works specified under the contract. |
|  | Vol. II Part-B, Section – 4, Clause no. – 4.2.3 | Commercial Off-The-Shelf (COTS) product Commercial Off-The-Shelf (COTS) product means bidder has to quote product which is independently commercially available in the market. For all such products bidder has to provide at least three references in Govt/Public Listed companies at the time of bid submission and same shall have been sold as an independent product and solution shall be in successful operation for at least three years at the time of bid submission. For that Bidder has to submit copy of PO/LOA and installation/completion/operational certificate issued by Customer for the relevant reference | Commercial Off-The-Shelf (COTS) product Replace with Commercial Off-The-Shelf (COTS) product means bidder has to quote product which is independently commercially available in the market. For all COTS products, the Contractor has to provide at least three references in Govt/Public Listed companies and same shall have been sold as an independent product and solution shall be in successful operation for at least three years as on the date of NOA. For that, the Contractor has to submit copy of PO/LOA and installation/completion/operational certificate issued by Customer for the relevant reference. However, in case of historian and load forecasting applications, which are categorized as Commercial Off-The-Shelf (COTS) products in the technical specifications and Bill of Quantities (BoQ), the contractor can supply their own product subject to submission of at least three references in Govt/Public Listed companies and solution shall be in successful operation for at least three years as on the date of NOA. The contractor can also submit self certified declaration in case the above reference documents cannot be shared with third parties due to Non-disclosure agreements with the customers. |
|  | Vol-II Part- B, Section 4, Clause: 4.5 | Network Management System (NMS) All Active devices such as Servers, Workstations, Storage Devices (SAN, NAS, HDD etc.) | Network Management System (NMS) Replace with All Active devices such as Servers, Workstations, Storage Devices (SAN, NAS etc.) |
|  | Vol. II Part-B, Section-4, Clause 4.6 | Database Development Tools The background color of database tool shall be user configurable. | Database Development Tools Deleted |
|  | Vol-II Part- B, Section 4: Clause 4.6.3.2 | Database Integration (on-lining) … The database changes made in Main Control Center shall be reflected immediately in Backup Control Center with minimal user intervention. At regular intervals (Daily) the database of Main and Backup Control Centers be checked for differences in entries, linkages, calculations and database elements and necessary updation shall be done for the same. | Database Integration (on-lining) Replace with The database changes made in Main Control Center shall be reflected immediately in Backup Control Center with minimal user intervention. The database of Main and Backup Control Centers shall be checked for differences in entries, linkages, calculations and database elements as and when required by owner with minimal user intervention and necessary updation shall be done for the same. |
|  | Vol-II Part- B, Section 4: Clause 4.6.6 | Development System (DDS or PDS) as a test bench | Replace with Development System (PDS) as a test bench section is attached as Annexure-A to this amendment. |
|  | Vol-II Part- B, Section 4: Clause 4.6.7 | CIM (Common Information Model- 61970) compliant Data Modelling Import & Export Tool ……Owner is in process to establish centralized database system which will be CIM complaint. User will have access to this database and shall model required component in this centralized database. Subsequently related database shall be extracted and imported in this proposed system. Contractor shall be responsible to develop CIM tool which shall be able to exchange the files from this database in CIM format….. | CIM (Common Information Model- 61970) compliant Data Modelling Import & Export Tool This para Deleted. |
|  | Vol. II Part-B, Section-4, Clause 4.7 | Display Generation and Management …. Utility to import & export displays through DXF or DWG or XML format (latest version with backward compatibility) from other control centers shall be provided | Display Generation and Management Replace with .…Utility to import & export displays through any of the formats DXF, DWG, XML formats from other control centers shall be provided. For DXF, DWG and XML format (for any of the format), it should support latest version with backward compatibility. |
|  | Vol. II Part-B, Section-4, Clause 4.7.3 | The display generator shall also have facility to export the SCADA/EMS displays in XML or DXF or DWG format (latest version with backward compatibility) to be used in AUTOCAD. For DXF, DWG, XML, AUTOCAD it should support latest version with backward compatibility. | Replace with The display generator shall also have facility to export the SCADA/EMS displays in any of the formats such as XML or DXF or DWG (latest version with backward compatibility) to be used in AUTOCAD. |
|  | Vol. II Part-B, Section-4, Clause 4.8.1 | Backup System …..The utility shall also take image backup daily automatically on backup appliance. It shall keep minimum two (02) set of image backup of all servers and one image backup of all the workstations on backup appliance (along with other backup details mentioned in Appendix-H, PART-B) and another Two (02) copies shall be maintained, out of which one shall be maintained by Contractor on SAN/NAS and other with Owner on external hard disk. Each day it will take image backup, when image backup is successful then it will delete the oldest image backup. It shall be possible to archive these image backups on external hard-disks. Bidder shall supply online agents (if required) for image backup of all the servers, workstations, databases etc.….. It should be possible to restore or recover any software/system at a selected time form backup…… | Backup System Replace with ……The utility shall also take image backup daily automatically on backup appliance and retaining number of copies as per retention policy defined under DRS of Backup appliance in Part-B, Appendix-H. Apart from this Two (02) more copies of back-up shall be maintained outside the backup appliance i.e. one shall be on SAN/NAS and another on external hard disk. In case of SAN/NAS, each day it will take image backup, when image backup is successful then it will delete the oldest image backup. It shall be possible to archive these image backups on external hard-disks. Bidder shall supply online agents (if required) for image backup of all the servers (physical/bare metal as well as virtual), workstations, databases etc. as per scope defined…… It should be possible to restore or recover any software/system at a selected time from backup…. |
|  | Vol-II Part- B, Section- 4, Clause-4.8.5 | Data Exchange Utilities …….. • Through ODBC/JDBC: Capability of export of SCADA data to external system though ODBC and JDBC shall be provided. All system parameters in the real-time database including real-time data, calculated data, application configuration parameters and application output shall be available through the ODBC interface. Limitation if any or pre-requisite on PC for use of this interface, shall be clearly defined. It shall be possible to export data through SQL queries to external system. • Through SOAP and REST: The SCADA system shall provide web services on SOAP and REST that allow multiple applications to exchange any data points including alarms and events. ………… | Data Exchange Utilities Replace with ………… • Through ODBC: Capability of export of SCADA data to external system though ODBC shall be provided. All system parameters in the real-time database including real-time data, calculated data, application configuration parameters and application output shall be available through the ODBC interface. Limitation if any or pre-requisite on PC for use of this interface, shall be clearly defined. It shall be possible to export data through SQL queries to external system. • Through either SOAP or REST: The SCADA system shall provide web services on either SOAP or REST, that allow multiple applications to exchange any data points including alarms and events. …………… |
|  | Vol. II Part-B, Section-5, Clause No.-5.2 | Technical Requirements for Hardware d) The Bidder shall ensure that product/technologies/services quoted under this project are latest and it shall have more than 7 years of life initially (i.e.., “End of Support Life” for minimum 7 years, from date of bid submission) which shall be extended during entire contract period (including extension of contract, if any) by extending the OEM warranty or replacing the product.). e) Proposed hardware offered by the OEMs shall be of the same series which have at least three references in Central / State Govt Organization / PSU / Public Listed Company as on the originally scheduled date of bid opening. For that Bidder has to submit copy of PO/LOA and installation/completion certificate for the relevant reference. h) All the supplied system shall be under OEM (Hardware and Software) warranty & support till the completion of entire AMC period (including extension of contract, if any). I) During entire contract period (including extension of contract, if any), if OEM discontinues/ ends support to any item supplied (software/hardware/security solution) under the contract, bidder has to replace such hardware, software (or both, depending on software or hardware dependency) without any additional cost to Owner. Replacement shall be of either same or higher configuration and from the same OEMs. | Technical Requirements for Hardware Replace with d) The Bidder shall ensure that product/technologies/services quoted under this project are latest and it shall have more than 7 years of life initially (i.e.., “End of Support Life” for minimum 7 years, from date of bid submission) which shall be extended during entire contract period (including extension of contract, if any) as per the provisions mentioned under Clause 1.12.6, Section 1, PART A of technical specifications along-with other scope of works specified under the contract. e) Proposed hardware offered by the OEMs which have at least three references in Central / State Govt Organization / PSU / Public Listed Company as on the originally scheduled date of bid opening. For that Bidder has to submit copy of PO/LOA and installation/completion certificate for the relevant reference. h) The supplied system shall be under OEM (Hardware and Software) warranty & support till the completion of entire AMC period (including extension of contract, if any) as per the provisions mentioned under Clause 1.12.6, Section 1, PART A of technical specifications along-with other scope of works specified under the contract. l) Deleted |
|  | Vol. II Part-B, Section-5, Clause No.-5.13 | Video Projection System (VPS) The contractor shall provide a video projection system based on modular DLP (Digital Light Processing) based high resolution Laser based rear projection technology as per BoQ……… | Video Projection System (VPS) Replace with The contractor shall provide a video projection system based on modular DLP (Digital Light Processing) based high resolution RGB Laser based rear projection technology as per BoQ…… |
|  | Vol. II Part-B, Section-5, Clause No.-5.13 | Video Projection System (VPS) Side of the VPS shall be covered with border for aesthetic look. Type Test Reports shall be provided for VPS and accessories during engineering approvals. The Type Tests should have been carried out at nationally/internationally accredited labs. | Video Projection System (VPS) Replace with Side of the VPS shall be covered with border for aesthetic look. BIS certificate shall be provided for VPS during engineering approvals. |
|  | Vol. II Part-B, Section-5, Clause No.-5.19 | Centralized Keyboard & Mouse Control Solution (CKMC) Para 3 Point d) d) Single multifunctional smart console /keyboard per workplace shall be sufficient to switch between and control any and all systems, in accordance with individual user rights. Add as Point (m) | Centralized Keyboard & Mouse Control Solution (CKMC) Replace with Para 3 Point d) d) Single multifunctional keyboard per workplace shall be sufficient to switch between and control any and all systems, in accordance with individual user rights. Add as Point (m) Contractor shall supply all the associated items required for integration of at-least 12 systems with 4 sets of keyboards and mouses (for RLDC) and 6 systems with 2 sets of keyboards and mouses (for SLDCs) without any additional cost to owner. |
|  | Vol. II Part-B, Section-5, Clause No.-5.21 | Provision of file transfer between OT and IT Provision must be kept to for secure file and data exchange between IT and OT system and between other OT systems. Keeping all security measures and guideline. All necessary hardware & Software shall be provisioned by the contractor accordingly. File exchange shall be as per the owner convenience periodicity. | Replace with Provision of file transfer between OT and IT Provision must be kept for secure file and data exchange between IT and OT system and between other OT systems keeping all security measures and guidelines specified in the technical specification. The periodicity of File exchange shall be as per the owner requirements. The secure file and data exchange between IT and OT system shall be as per functionalities specified in different section of this specification. |
|  | Vol. II Part-B, Section-5, Clause 5.5 | CFE (Communication Front-End) Server …….However, all the data from field to CFE shall be routed through internal Firewall. | CFE (Communication Front-End) Server Replace with ……. However, all the data from field to CFE shall be routed through external Firewall. |
|  | Vol. II Part-B, Section-5, Clause No.-5.8.5 | Routers ….Routers shall have the built-in firewall/security features as required. There shall be 50% spare ports….. | Routers Replace with …. Routers shall have the built-in firewall/security features as required. All routers shall have spare ports as per Appendix H. |
|  | Vol. II Part-B, Section-5, Clause No.-5.9.1 | Storage Area Network (SAN) based storage A Storage Area Network (SAN) based, or any other specialized storage solution shall be provided which shall be sized adequately and be used for online storage and all online data backup. Historian shall be connected ……… | Storage Area Network (SAN) based storage Replace with A Storage Area Network (SAN) based or any other specialized storage solution shall be provided which shall be sized adequately and be used for online storage and all online data backup. In case of any other specialized storage solution, one SAN (as per configuration) shall also be supplied at Main and Backup Control Centre without any cost implication to Owner. Configuration, computation, storage etc. of specialized storage/solution shall be equivalent/higher to equipment proposed under the project. Historian shall be connected……….. |
|  | Vol. II Part-B, Section-5, Clause No.-5.9.3 | Backup Appliance Backup appliance is a type of data storage device / equipment that accumulates the backup software and hardware components within a single device. Dedicated back-up appliance shall be provisioned for the backup of various files, database, image backup etc. as per the functionality mentioned under Appendix-H. It should be possible to restore or recover any software/system at a selected time from backup system. It shall be sized appropriately to take backup of all the supplied system. | Backup Appliance Replace with Backup appliance is a type of data storage device / equipment that accumulates the backup software and hardware components. Dedicated back-up appliance shall be provisioned for the backup of various files, database, image backup (physical/bare metal and virtual servers) etc. as per the functionality mentioned under Appendix-H. It should be possible to restore or recover any software/system at a selected time from backup system including bare metal recovery. It shall be sized appropriately to take backup of all the supplied system. |
|  | Vol. II Part-B, Section-5.15 | -- | New clause added. 5.15.1 Weather Sensors for Server & Battery Room Weather sensors shall be supplied as per the Hardware DRS at Appendix-H, Part-B. The weather sensors data shall be integrated in SCADA system through MODBUS TCP/IP protocol and the same shall be made available in the UI display for viewing of the operator. The weather sensor shall be installed in server room and battery room of control center. Weather sensor data shall also be recorded and archived in the Historian for retrieval similar to other SCADA data. |
|  | Vol. II Part-B, Section-6, Clause 6.6.1 | Server Failover ….The on-line functions of the failed Server, having execution periodicity less than or equal to 30 seconds, shall be assigned to its backup Server within 30 seconds of the failure except for Historian Server…. | Server Failover Replace with ….The on-line functions of the failed Server, having execution periodicity less than or equal to 30 seconds, shall be assigned to its backup Server within 30 seconds of the failure. The failover time for historian server shall be within 60 seconds ….. |
|  | Vol. II Part-B, Section-6, Clause 6.6.2 | 6.6.2 Restart Restart involves the ability of any server to self-detect its non-recoverable errors and to attempt to restart the SCADA/EMS system functions. The restart logic shall determine the desired state of the failed Server and the online function(s) to be initiated in this Server. The restart logic shall also preclude conflicts among Servers, such as assigning too few or too many Servers to the primary state and the erroneous duplication of functions in multiple Servers. All maintenance functions executing in the restarting Server shall be suspended to expedite the restart process. Restart shall include initialization of the SCADA/EMS function(s) and internal parameters, updating of databases, establishing access to peripheral devices, and execution of the function(s). Databases may be updated from backup databases or from static initialization database copies stored on auxiliary memory depending on the nature of the restart. The use of the static initialization databases shall be restricted to user-invoked restarts. If insufficient peripheral devices are available to perform the on-line function(s), the restart logic shall generate an alarm requesting user intervention. Restart as described above shall be completed within 30 seconds except for EMS server which can be 120 seconds. Also, the cold restart of the devices (Firewall, Router, Switch etc.) shall be completed within 5 minutes. | Replace with 6.6.2 Application Restart Application Restart involves the ability of any server to self-detect its non-recoverable errors and to attempt to restart the SCADA/EMS system functions. The restart logic shall determine the desired state of the failed Server and the online function(s) to be initiated in the respective Application. The restart logic shall also preclude conflicts among Servers, such as assigning too few or too many Servers to the primary state and the erroneous duplication of functions in multiple Servers. Application restart on command by user shall also be treated similarly. All maintenance functions executing in the restarting server shall be suspended to expedite the restart process. Restart shall include initialization of the SCADA/EMS function(s) and internal parameters, updating of databases, establishing access to peripheral devices, and execution of the function(s). Databases may be updated from backup databases or from static initialization database copies stored on auxiliary memory depending on the nature of the restart. The use of the static initialization databases shall be restricted to user-invoked restarts. If insufficient peripheral devices are available to perform the on-line function(s), the restart logic shall generate an alarm requesting user intervention. Application Restart as described above shall be completed within 2 minutes for all application (except EMS applications), 3 minutes for EMS applications and 5 minutes for Historian application. Application restart shall not include user interface(s) response time which shall be as per performance requirement. |
|  | Vol. II Part-B, Section-6, Clause 6.6.3 | 6.6.3 Server Start-Up A Server start-up shall be performed when commanded by a user and when Server input power is interrupted and restored such that the operating environment of the Server is established prior to restarting the on-line functions. Establishment of the operating environment may include execution of self-diagnostics, reloading the operating system and system services, and connection to and verification of communications with all nodes on the control center computer system LAN. The server start up shall be completed within 5 minutes with all functions scheduled for execution. | Replace with 6.6.3 Server Restart A Server restart shall be performed when commanded by a user (soft reboot) and/or when Server input power is interrupted (hard reboot) and restored such that the operating environment of the Server is established. The server shall automatically restart itself when input power is interrupted and restored. Establishment of the operating environment may include execution of self-diagnostics, reloading the operating system and system services, initialization of all interfaces, initialization of peripheral devices such as storage, printer etc. , connection to the databases, connection to and verification of communications with all nodes on the control center computer system LAN, resumption of all SCADA/EMS functions, initialization of all communications with data sources and other control centers and notifications to the users that restart has been completed. Server restart shall be completed within 10 (ten) minutes or earlier. Device Restart The restart of the devices (Firewall, Router, Switch etc.) shall be completed within 5 minutes. |
|  | Vol. II Part-B, Section-6, Clause 6.6.4 | System Power-On-Start-Up The SCADA/EMS system shall automatically restart itself when input power is interrupted and restored. System start-up shall include Server start up, initialization of all network devices, initialization of peripheral devices, initialization of all communications with data sources and other control centers, resumption of all SCADA/EMS functions and notifications to the users that startup has been completed. System power-on startup shall be completed within 5 (five) minutes or earlier. | This Para Deleted |
|  | Vol. II Part-B, Section-6, Clause 6.9 | It shall be possible to synchronize databases used for development, display building and source code on daily basis automatically and manually both. | It shall be possible to synchronize databases used for development, display building and source code (Project specific module / scripts / configurations etc.) on daily basis automatically and manually both. |
|  | Vol. II Part-B, Section-7, Clause- 7.4 | Test Initiation d) A complete regeneration of the software under test for which source code is being supplied shall be performed immediately prior to the start of factory testing. | Test Initiation Replace with d) A complete regeneration of the software under test for which API source code is being supplied shall be performed immediately prior to the start of factory testing. |
|  | Vol-II Part- B, Section 7: Clause 7.8 | Site Acceptance Tests (SAT) (also referred as Field Tests) Site Acceptance Test (SAT) shall be conducted on full designed capacity of the supplied system i.e. sizing mentioned in specification and its expansion. Contractor shall make necessary arrangement to demonstrate the performance test. | Site Acceptance Tests (SAT) (also referred as Field Tests) Replace the para with Site Acceptance Test (SAT) shall be conducted on full designed capacity of the supplied system i.e. ultimate sizing mentioned in specification. However, testing shall be done as per available field data and no simulation of data shall be required. Contractor shall make necessary arrangement to demonstrate the performance test. |
|  | Vol. II Part-B, Section – 7, Clause no. –7.10 | System Availability Test (SAVT) After successful completion of SAT (i.e., field performance test), a 1000-hour system availability test (SAVT) shall be conducted on all supplied systems in an integrated and simultaneous manner under normal day-to-day operating conditions. The system under test shall include RLDC and all supplied SLDCs system (main and backup both) and RTUs under the respective RLDC/SLDC. The test shall verify the reliability and integrity of the database, displays, report and all communication interfaces and, under these conditions, verify system availability for 99.9%. | System Availability Test (SAVT) Replace with After successful completion of SAT (i.e., field performance test), a 1000-hour system availability test (SAVT) shall be conducted on the supplied system in an integrated manner under normal day-to-day operating conditions. A system under test for SAVT shall mean respective RLDC/ SLDC with the Main and Backup control centers integrated with the RTUs (existing as well as new RTUs supplied) of the respective control centers. The system under test shall also be integrated to have data exchange with other control centers and other applications as mentioned in the technical specifications. The SAVT may be conducted on all/multiple RLDC/SLDCs in simultaneous manner. The test shall verify the reliability and integrity of the database, displays, report and all communication interfaces and, under these conditions. The system availability for RLDC and each SLDC shall be measured separately and availability of 99.99% shall be verified. |
|  | Vol. II Part-B, Section – 7, Clause no. –7.10 | SAVT Test Duration and Criteria for Acceptance After the elapse of 1000 hours of cumulative test time, the availability shall be calculated considering the downtime recorded. Should availability fall short of specified percentage, the contractor may either (a) Continue the test by moving the starting time of the test forward and continuing the test until the consecutive hours have been accumulated and the specified availability has been achieved subject to maximum of 75 days, or (b) the contractor may restart the test for 1000 hours, however, more than two such restart shall not be allowed. To establish that all failures have been satisfactorily repaired prior to the end of the SAVT, no downtime, intermittent (hold time) failures, or more than one commanded fail over shall have occurred within 240 hours of the test's conclusion. In the event of repeated unsuccessful reruns of the availability test, Employer/Owner may invoke the default provisions described in Volume I of the Specification. The successful completion of the availability test will lead to Operational Acceptance of the system. | SAVT Test Duration Replace with… After the elapse of 1000 hours of cumulative test time, the system availability for RLDC and each SLDC shall be measured separately and availability of 99.99% shall be verified considering the downtime recorded. Should availability fall short of specified percentage, the contractor may either (a) Continue the test by moving the starting time of the test forward and continuing the test until the consecutive hours have been accumulated and the specified availability has been achieved subject to maximum of 75 days, or (b) the contractor may restart the test for 1000 hours, however, more than two such restart shall not be allowed. To establish that all failures have been satisfactorily repaired prior to the end of the SAVT, no downtime, intermittent (hold time) failures, or more than one commanded fail over shall have occurred within 240 hours of the test's conclusion. In the event of repeated unsuccessful reruns of the availability test, Employer/Owner may invoke the default provisions described in Volume I of the Specification. The successful completion of the System availability test (SAVT) and completion of parallel operation of existing system with new system for up to 3 months will lead to Operational Acceptance of the system. SAVT and parallel operation of the new system and existing system may be started simultaneously, however successful completion of both shall be mandatory to issue Operational Acceptance of the system. |
|  | Vol. II Part-B, Section – 7, Clause no. –7.11 | Criteria for Successful Operation The system shall be designed to meet the total system availability of 99.9%. That is, the ratio of total operational time minus downtime to total operational time shall be equal to or greater than 0.999. Total operational time shall not include the hold time. | Criteria for Successful Operation Replace with The system shall be designed to meet the total system availability of 99.99%. That is, the ratio of total operational time minus downtime to total operational time shall be equal to or greater than 0.999. Also, the resource utilization (RAM, CPU) of the servers, workstations etc. shall not exceed the maximum utilization as specified in Part-B, appendix-D. Total operational time shall not include the hold time. …….. |
|  | Vol. II Part-B, Section – 7, Clause no. –7.13 |  | New Para Inserted at 7.13 Parallel Operation The parallel operation of the existing and new system shall commence after completion of SAT. The parallel operation shall be performed without disturbing the operation of the existing system. A minimum number of operator console and peripheral devices shall be installed as per owner requirement. Following minimum shall be verified during parallel operation - a). Data consistency between new and existing system for data from field (RTUs), other control center and IT applications. |
|  | Vol-II Part- B, Section 8, Clause 8.2.3 | Web Applications & Web Historian i) The Web-Portal shall provide the Access Control Management for Web and Mobile App. | Web Applications & Web Historian Replace with i) The Web-Portal shall provide the Access Control Management for Web Application. |
|  | Vol-II Part- B, Section 8, Clause 8.2.3 | Web Applications & Web Historian p) Real-time trend v/s past day trend of any data point shall be displayed in the web browser/mobile application. t) The Web Publishing shall be interfaced / co-ordinated as per cyber security policy. | Web Applications & Web Historian Replace with p) Real-time trend v/s past day trend of any data point shall be displayed in the web browser. t) The Web Application shall adhere to the cyber security policy. |
|  | Vol. II Part-B, Section-8, Clause No.-8.2.4 | Contractor shall take services of SMS service provider and integrate the SMS interface with SMS service provider services to achieve SMS delivering functionality. Contractor shall take the services of SMS service provider for entire contract period (including extension of contract, if any). The contractor shall also provide services of SMS service provider for testing purposes during FAT, SAT etc. at its own cost. The interface application shall be preferably hosted in web system to securely connect with SMS service provider services through use of encrypted APIs. However, the provided solution shall meet the cyber security related guidelines/policy envisaged in the technical specification. Keeping cyber security aspects in design, SMS services from govt. agencies such as NIC etc. shall be preferred. As a minimum, following functionality shall be provided by contractor in the SMS interface at RLDC and SLDCs: …………. | Replace with Contractor shall integrate the SMS interface with SMS services provided by the owner to achieve SMS delivering functionality. The owner shall provide SMS services before the site installation. However, the contractor shall provision SMS services during FAT at its own cost. The interface application shall be preferably hosted in web system to securely connect with SMS service provider services through use of encrypted APIs. However, the provided solution shall meet the cyber security related guidelines/policy envisaged in the technical specification. As a minimum, following functionality shall be provided by contractor in the SMS interface at RLDC and SLDCs: …………. |
|  | Vol. II Part-B, Section-8, Clause No.-8.2.4 | ●SMS Interface application shall be configured as redundant in Main Control Centre and Backup Control Centre utilizing the same SMS service provider as envisaged in BoQ. ● Any unused quota of yearly SMS service provider (as envisaged in BoQ) shall be carry forward to subsequent years for utilization. | Replace with - SMS Interface application shall be configured as redundant in Main Control Centre and Backup Control Centre - Deleted |
|  | Vol-II Part- B, Section 9, Clause 9.1.2 | Remote Diagnostic ….ISP will be provided and maintained by the owner however number of public IPs and bandwidth requirement to be indicated by the contractor. | Remote Diagnostic Replace with .…Public IP shall be provided by the owner. Inserted new para The new para is attached at Annexure-A. |
|  | Vol. II Part-B, Section-9, Clause No.- 9.1.9 | Database Development System (DDS)/Program Development System (PDS) as a test bench for Cyber Security Requirement A Test bench PDS i.e. (as specified in section 4.3.6) PDS shall be delivered by the Contractor. Along with functions defined in that section, this will be used for following purposes also- a) This system shall also be used as a Test bench for Cyber security and shall accordingly be equipped with firewall, antivirus and enable mode wherein threat scenarios can be tested with configured security elements before implementing on the main/production system. b) This Test bench for Cyber security shall also be used for VAPT (Vulnerability Assessment & Penetration Tests) e.g., OS fingerprinting, Port scanning, etc. | Replace with Test Bench for Cyber Security The revised para is attached at Annexure-A. |
|  | Vol. II Part-B, Section-9, Clause No.- 9.1.10 | Tool for VAPT | Tool for VAPT New Inserted The tool(s) shall have the following minimum features for Penetration Testing (Internal and External) - • Trusted System Scanning • Network Scanning for known Trojans • Administrator Privileges Escalation Testing • Services Probing • Attempt ARP poisoning • Attempt MAC flooding • Attempt DNS poisoning • Identification of Services • Short Listing of Crucial IPs • Identification of Operating System • Vulnerability Research and Verification • Password Cracking • IDS/IPS testing • Router, Switch & Firewall testing • DOS/DDOS Testing • IP spoofing |
|  | Vol. II Part-B, Appendix-B SAMPLE REPORTS & DISPLAY FORMATS | B6. Sample Trend Displays B27: Text Transfer in ICCP: | Replace with B6. Sample Trend Displays attached at Annexure A B27 Deleted |
|  | Vol. II Part-B, Appendix-C | Table 4 – DESIGN PARAMETERS FOR USER INTERFACE Name; Design Capacity; Execution Rate. TREND (Online) in SCADA. c) Samples per trend variable; 10,000. | Table 4 – DESIGN PARAMETERS FOR USER INTERFACE Name; Design Capacity; Execution Rate. TREND (Online). c) Samples per trend variable; - Minimum 1500 in real time - 10,000 in SCADA-Historian (auto refresh). |
|  | Vol. II Part-B, Appendix-C | Table 4 – DESIGN PARAMETERS FOR USER INTERFACE Name; Design Capacity; Execution Rate. ALARMS. Alarm priority levels; 16. Alarm Message Recording on auxiliary memory; 1,00,000. EVENTS. Event Message Recording on Auxiliary memory; 1,00,000. | Table 4 – DESIGN PARAMETERS FOR USER INTERFACE Replace with Name; Design Capacity; Execution Rate. ALARMS. Alarm priority levels; 8. Alarm Message; Minimum 20,000 Alarms on auxiliary memory 1,00,000 alarm to be displayed (auto refresh) either through SCADA or SCADA-Historian; Real time On-demand. EVENTS. Event Message; Minimum 20,000 Events on auxiliary memory 1,00,000 event to be displayed (auto refresh) either through SCADA or SCADA-Historian; Real time On-demand. |
|  | Vol. II Part-B, Appendix-C | TABLE 5 – Design Parameters for Configuration Characteristics (Specification Reference -Section 4 & 6) Server failover 60 sec Server Start-Up Hot Start 2 minutes Warm Start 3 minutes Cold Start 5 minutes Device failover 30 sec | TABLE 5 – Design Parameters for Configuration Characteristics (Specification Reference -Section 4 & 6) Replace with Server failover 30/120 sec for Server (Refer Section 6.6.1) and 60 sec for Historian Application restart a. 2 minute for all application (except EMS application) b. 3 minutes for EMS application c. 5 min for Historian application Server Restart (hard/soft reboot) 10 minutes Device Restart 5 minutes Device failover 30 sec |
|  | Vol. II, Part- B, Appendix – C: SYSTEM DESIGN PARAMETERS | Table 6: Design Parameters for DSA (Specification Reference- Section 2) | Revised Table 6: Design Parameters for DSA (Specification Reference- Section 2) is attached at Annexure-A. |
|  | Vol. II Part-B, Appendix-D | Table 1- PERFORMANCE REQUIREMENTS (iv) ¦ Display (including Trends) update rate ¦ Every 2 sec for 4 displays together to be completed in 0.5 secs. Added new point(xviii) | Table 1- PERFORMANCE REQUIREMENTS Replace with (iv) ¦ Display (including Trends) update rate ¦ Displays shall be updated every 2 sec (periodicity of update) and Callup of 4 displays together shall be completed in 0.5 secs. (execution time) xviii) ¦ Callup and Display of data in historian dashboard ¦ within 30 secs |
|  | Vol. II Part-B, Appendix-D | Table 1- PERFORMANCE REQUIREMENTS (x) ¦ Video projection system display update rate (Shall be performed during SAT) ¦ Every 2 sec for 4 displays together to be completed in 0.5 secs. | Table 1- PERFORMANCE REQUIREMENTS Replace with (x) ¦ Video projection system display update rate (Shall be performed during SAT) ¦ Displays shall be updated every 2 sec (periodicity of update) and Callup of 4 displays together to be completed in 0.5 secs. (execution time) |
|  | Vol. II Part-B, Appendix-D | Table 2- NORMAL LEVEL OF ACTIVITIES ….. (d) 80% of the analog values shall be changing in every scan…. | Table 2- NORMAL LEVEL OF ACTIVITIES Replace with ….. (d) 50% of the analog values shall be changing in every scan…. |
|  | Vol. II Part-B, Appendix-D | Table 3- PEAK LEVEL OF ACTIVITIES …. (i) 100% of the analog values shall be changing in every scan instead of 80% considered during the normal level of activities… | Table 3- PEAK LEVEL OF ACTIVITIES Replace with …. (i) 70% of the analog values shall be changing in every scan instead of 50% considered during the normal level of activities… |
|  | Vol. II, Part- B, Appendix – E: | Appendix – E: Questionnaire Question Nos: 17(d), 23, 26, 156, 157, 158, 164, 173 | Appendix – E: Questionnaire Q 17(d) Appendix C to be referred as Appendix F. Q 23. Appendix C to be referred as Appendix F. Q 26 Max display 25 to be referred as Max display 20 Q 156 Appendix B (B27) to be referred as Appendix B(B19). Q 157 Appendix B (B26) to be referred as Appendix B(B19). Q 158 Appendix B (B34-C) to be referred as Appendix M. Q 164 A sample display is attached in Appendix B(B41) to be considered as deleted. Q 173 (as per Sec 4.9.3 of Part B of Spec) to be considered as deleted. |
|  | Vol. II Part-B, Appendix-E, Q.130 | Appendix – E: Questionnaire Q.130 Provide an availability analysis for the proposed configurations to meet an availability goal of 99.9%. The analysis shall include the mean time between failures (MTBF) and mean time to repair (MTTR) of all components, and the historical, statistical basis for the analysis. Specific assumptions on availability of spare parts, maintenance responsibility etc. not in line with proposed contract shall be listed. The analysis shall also present the availability for individual devices. | Appendix – E: Questionnaire Replace with Q.130 Provide an availability analysis for the proposed configurations to meet an availability goal of 99.99%. The analysis shall include the mean time between failures (MTBF) and mean time to repair (MTTR) of all components, and the historical, statistical basis for the analysis. Specific assumptions on availability of spare parts, maintenance responsibility etc. not in line with proposed contract shall be listed. The analysis shall also present the availability for individual devices. |
|  | Vol. II, Part- B, Appendix – F | Appendix – F: System Sizing | Appendix – F: System Sizing Replace with Revised Vol-II, Part-B, Appendix-F: System Sizing is attached at Annexure- A. |
|  | Vol. II, Part- B, Appendix – G – Bill of Quantity | Appendix – G: Bill of Quantity | Appendix – G: Bill of Quantity Replace with Revised, Vol. II, Part- B, Appendix – G – Bill of Quantity for SCADA/EMS System are attached as Annexure-B. |
|  | Vol. II Part-B, Appendix-H, All the serves envisaged under the project and listed under Appendix-H | Sl no. 9: Interfaces 1. 2 x 10 Gbps Ethernet/FO ports 2. Dedicated 1 Gbps Management port 3. 2 x 16 Gbps FC port for SAN connectivity | Replace with Sl no. 9: Interfaces 1. 2 x 10 Gbps FO ports 2. Dedicated 1 Gbps Management port 3. 2 x 16 Gbps FC port for SAN connectivity |
|  | Vol. II Part-B, Appendix-H Hardware DRS | - Back-up Solution Sl. No. 3 The proposed appliance must be a purpose built backup appliance for long term data retention and disaster recovery. Sl. No. 9 The solution must support data protection of physical systems as well as virtual environments. Sl. No. 10 The solution shall take image backup of physical as virtual system. Sl. No. 13 The proposed backup solution should support restore a single VM, single file from a VM, a VMDK restore from the same management console for ease of use. Sl. No. 26: Proposed backup appliance should be sized appropriately for the backup of 40 TB of (File System, source data, mix of Databases, VM etc.) and shall maintain following copies of data. a. Daily Incremental Backup – retained for 1 weeks b. Weekly Full Backup – retained for 15 days. c. Monthly Full Backups – retained for 1 Month. d. Yearly Full Backups – retained for 1 year. Bidder must consider usable capacity to retain the data as per the scope of work specified in technical specification. Sl no. 27: Spare Disk Global hot spare to be provided. Sl no. 30: Dual Controller Storage must have two controllers and at least 16GB of DRAM cache. | - Back-up Solution Replace with Sl. No. 3 The Backup solution shall include backup appliance, any additional items such as backup software application, backup server required for achieving the functionality. The same is to be considered as part of Backup solution. The proposed appliance must be a purpose built backup appliance for long term data retention and disaster recovery. Sl. No. 9 The solution must support data protection of physical systems (including bare metal) as well as virtual environments. Sl. No. 10 The solution shall take image backup of physical (including bare metal) as virtual system. Sl. No. 13 The proposed backup solution should support restoration of single VM, physical/bare metal, single file from a VM, a VMDK restore from the same management console for ease of use. Sl. No. 26: Proposed backup appliance should be sized appropriately for the backup of 40 TB of (File System, source data, mix of Databases, image backup of physical and VM servers etc.) and shall maintain following copies of data. A. Daily Incremental Backup – retained for 1 week b. Weekly Full Backup – retained for 2 weeks c. Monthly Full Backups – retained for 2 Months d. Yearly Full Backups – retained for 2 years Bidder must consider usable capacity to retain the data as per the scope of work specified in technical specification. Sl no. 27: Spare Disk One hot spare to be provided. Sl no. 30: Dual Controller Deleted. |
|  | Vol-II Part- B, Appendix-H: Hardware Specification | 6. Storage System Added note for storage system | ** NOTE: Storage capacity of SAN and NAS doesn’t include the SIEM logs storage capacity (as per TS requirement). Log storage capacity of SIEM varies from OEM to OEM as per compression ratio, hence, storage space for SIEM log shall be considered additionally over and above the specified SAN storage capacity for the control centre without any additional cost to Owner. |
|  | Vol-II Part- B, Appendix-H: Hardware Specification s. 6.1. Storage Area Network (SAN), Sl. No. 4, Capacity | 6.1. Storage Area Network (SAN) …. Sl. No. 4: Minimum usable capacity of 50 TB to be provided using dual ported drives on RAID-5 (SSD and SAS) / 6(NLSAS). Following type disk shall be provided: a. 25% of required capacity on SSD b. 40% of required capacity on SAS c. 35% of required capacity on SAS/NLSAS … | 6.1. Storage Area Network (SAN) Replace with … Sl. No. 4: Minimum usable capacity of 50 TB to be provided using dual ported drives on RAID-5 (SSD and SAS) / 6(NLSAS). Following type disk shall be provided: a. 25% of required capacity on SSD b. 40% of required capacity on SAS c. 35% of required capacity on SAS/NLSAS Alternatively, the contractor may provide minimum usable capacity of 50 TB (RAID-5) using dual ported SSD drives. In this solution, functionality of auto tiering across drives mentioned at Sl. No. 3 above, is not applicable. …… |
|  | Vol-II Part- B, Appendix-H | 6.2 Network Attached Storage (NAS) Sl. No. 11 Interface ports: Minimum 4*10G Base T ports (two ports per controller) Sl. No. 12 Controller: Dual Controller | 6.2 Network Attached Storage (NAS) Replace with Sl. No. 11 Interface ports: Minimum 4*10G (either Base T ports or FO ports) Sl. No. 12 Controller: Deleted |
|  | Vol. II Part-B, Appendix-H Hardware DRS | 7. Router cum Firewall: ICCP and RTU Communication Point No. 3(b): Router should have minimum 4 GB of on-board/inbuilt DRAM/RAM for data plane + control plane processes and 8 GB Flash. Point No. 3€: Router should be IPv6/USGv6 Certified/IPv6 logo ready Point No. 7 Routing Protocol: Static Routes, OSPFv2, OSPFv3, BGP4, MP-BGP, BFD, IPCP, IP forwarding, Policy based routing, VLAN & MPLS etc. Point No. 13: The Router shall have capability to add on demand IPSec VPN tunnels dynamically established hub -to-spoke IPSEC tunnels Note: However, the no of ports in a router shall be as per the network architecture & requirement at site and shall have 50% spare ports. | 7. Router cum Firewall: ICCP and RTU Communication Replace with Point No. 3(b): Router should have minimum 4 GB of on-board/inbuilt DRAM/RAM for data plane + control plane processes and min 1 GB Flash Point No. 3(e): Router should be IPv6 ready from day one. Point No. 7 Routing Protocol: Static Routes, OSPFv2, OSPFv3, BGP4, MP-BGP, BFD, IP forwarding, Policy based routing, VLAN & MPLS etc. Point No. 13: The Router shall have capability to add on demand IPSec VPN tunnels established hub -to-spoke IPSEC tunnels Note: However, the no of ports in a router shall be as per the network architecture & requirement at site. |
|  | Vol. II Part-B, Appendix-H Hardware DRS | 8. Router cum Firewall for PDS, Remote Console, External World Connectivity and others Point No. 3(b): Router should have minimum 4 GB of on-board/inbuilt DRAM/RAM for data plane + control plane processes and 8 GB Flash. Point No. 3(e): Router should be IPv6/USGv6 Certified/IPv6 logo ready Point no. 7 Routing Protocol: Static Routes, OSPFv2, OSPFv3, BGP4, MP-BGP, BFD, IPCP, IP forwarding, Policy based routing, VLAN & MPLS etc. Point no. 13: The Router shall have capability to add on demand IPSec VPN tunnels dynamically established hub -to-spoke IPSEC tunnels Point no. 15(b) Interface Support: Shall have minimum 4 nos 1 Gbps Ethernet L3 ports Point no. 15 NOTE: Number of ports in router at control center for connecting remote consoles shall have sufficient number of L2 ports. to connect all the envisaged remote consoles Note: However, the no of ports in a router shall be as per the network architecture & requirement at site and shall have 20% spare ports. | Replaced with Point No. 3(b): Router should have minimum 2 GB of on-board/inbuilt DRAM/RAM for data plane + control plane processes and min 1GB Flash. Point No. 3(e): Router should be IPv6 ready from day one. Point no. 7 Routing Protocol: Static Routes, OSPFv2, OSPFv3, BGP4, MP-BGP, BFD, IP forwarding, Policy based routing, VLAN & MPLS etc. Point no. 13: The Router shall have capability to add on demand IPSec VPN tunnels established hub -to-spoke IPSEC tunnels. Point no. 15(b) Interface Support: Shall have minimum 2 nos 1 Gbps Ethernet L3 ports for remote console routers and other routers shall have minimum 4 nos 1 Gbps Ethernet L3 ports. Point no. 15 NOTE: Routers (Remote Console & External World Connectivity) shall have sufficient number of L2 ports to connect all the envisaged remote console devices. Note: However, the no of ports in a router shall be as per the network architecture & requirement at site. |
|  | Vol-II Part- B, Appendix-H: Hardware Specifications. | 9.LAN Switches: a. 48 Port L3- LAN switch for SCADA/EMS LAN b. 24 Port L3- LAN switch for Historian and Reporting LAN c. 24 Port L3- LAN switch for Internal & External DMZ LAN d. 24 Port L3- LAN Switch for ICCP & FEP LAN e. 24 Port L3- LAN Switch for Server Management LAN Point no. 4: General - Switch should have minimum 2 GB RAM and 2 GB Flash/SSD Memory. Point no. 8: Interface Ports: a. 24/48 nos of port b. 5 nos 10 Gbps FO ports c. 12 nos 1Gbps Ethernet ports Balance 1/10 Gbps as per site requirement and switch type. All pre-populated ports should have compatible transceivers along-with required FO cables. Switch shall have virtualization feature for HA (through FO Port), so that two different switches to appear as a single port channel | 9.LAN Switches: Replace with a. 48 Port L3- LAN switch for SCADA/EMS LAN b. 24 Port L3- LAN switch for Historian and Reporting LAN c. 24 Port L3- LAN switch for Internal & External DMZ LAN d. 24 Port L3- LAN Switch for ICCP & FEP LAN e. 48 Port L3- LAN Switch for Server Management LAN f. 24 Port L3- LAN Switch for Firewalls g. 24 Port L3- LAN Switch for Router Point no. 4: General (replaced) - Switch should have minimum 1 GB RAM and 1 GB Flash/SSD Memory. - Point no. 4: General (new point s.no. f. addef. Switch shall be non-blocking and shall have wire-speed. Point no. 8 Interface Ports: Switches; 10 Gbps FO ports; 1Gbps Ethernet ports. - SCADA/EMS LAN; 12; 24. - Historian and Reporting LAN; 10; 12. - Internal & External DMZ LAN; 10; 4. - ICCP & FEP LAN; 8; 4. - Server Management LAN; 6; 32. - Switch for firewalls; 6; 4. - Switch for router; 6; 4. Balance 1/10 Gbps as per site requirement and switch type. All pre-populated ports should have compatible transceivers along-with required FO cables. Switch shall have virtualization feature for HA (through FO Port), so that two different switches to appear as a single port channel |
|  | Vol-II Part- B, Appendix-H: Hardware Specifications | - 10.LAN Switca. 24 Port L3- LAN Switch for DCPC/Terminal Server LAN Point no. 4 : General - Switch should have minimum 2 GB RAM and 2 GB Flash/SSD Memory. | 10. LAN Switch - Replace wita. 24 Port L3- LAN Switch for DCPC/Terminal Server LAN Point no. 4: General (replaced) - Switch should have minimum 1 GB RAM and 1 GB Flash/SSD Memory. - Point no. 4: General (new point s.no. f. addef. Switch shall be non-blocking and shall have wire-speed. |
|  | Vol-II Part- B, Appendix-H: Hardware Specifications | 11. FC Switch for SAN Storage Point no. 4: Interface ports ** 16Gbps FC ports | 11. FC Switch for SAN Storage Replace with Point no. 4: Interface ports 32 **nos (16 Gbps FC ports) |
|  | Vol. II Part-B, Appendix-H Hardware DRS | 12. Link Load Balance Point No. 17: LLB shall be designed to run both IPv4 & IPv6 simultaneously (Dual Stack) from day one from day one and appliance should be IPV6 Ready logo certified from day one. | 12. Link Load Balance Replace with Point No. 17: LLB shall be designed to run both IPv4 & IPv6 simultaneously (Dual Stack) from day one. |
|  | Vol-II Part- B, Appendix-H: Hardware Specifications | 13. External Network Firewall with NIPS (For DMZ and RTU-ICCP Connectivity) S no. 22 Interface Requirement: - Minimum number of 1 Gbps LAN ports: 8 (DMZ) / 4(RTU& ICCP) - Minimum number of 10 Gbps FO ports – 4 (DMZ) /8 (RTU & ICCP) - Separate HA port All the SFP+ port should have compatible transceivers (short range transceiver) along-with required FO cables. | 13. External Network Firewall with NIPS (For DMZ and RTU-ICCP Connectivity) Replace with S no. 22 Interface Requirement: - Minimum number of 1 Gbps LAN ports: 6 (DMZ) / 6(RTU& ICCP) - Minimum number of 10 Gbps FO ports – 8 (DMZ) /8 (RTU & ICCP) - Separate HA port All the SFP+ port should have compatible transceivers (short range transceiver) along-with required FO cables. |
|  | Vol. II Part-B, Appendix-H, Hardware Specification, Table: 14, Internal Network Firewall with NIPS | Sr. No.; Description of the Features; Minimum Quantity of the features; Offered by the Contractor. 3; e. Firewall should have at least 1.5 Gbps of VPN throughput.. 4.; Sizing Parameters: - Should have Minimum NG Threat prevention throughput in real world/production environment (by enabling and measured with Application-ID/AVC, NGIPS, Anti-Virus, Anti-Spyware, Anti Malware, Anti-Bot, Zero-day attacks and logging security threat prevention features enabled – 6 Gbps real world/production environment/Application Mix. - Firewall should have at least 1 Gbps of VPN throughput. - Firewall should support at least 3000 new connections per second or more and shall support at-least 1Million concurrent session/ connection with all application control enabled. - No of VLANs – 100 - Minimum IPSec VPN peers – 1000 - Proposed solution should support minimum 6 Gbps or more IPS throughput. 20; Interface Requirement: a. Minimum number of 1 Gbps LAN ports: 8 b. Minimum number of 10 Gbps ports – 10 c. Separate HA port All the SFP+ port should have compatible transceivers (Short Range Transceiver) along-with required FO cables.. | Replace with Sr. No.; Description of the Features; Minimum Quantity of the features; Offered by the Contractor. 3; e. Firewall should have redundant fan.. 4.; Sizing Parameters: - Should have Minimum NG Threat prevention throughput in real world/production environment (by enabling and measured with Application-ID/AVC, NGIPS, Anti-Virus, Anti-Spyware, Anti Malware, Anti-Bot, Zero-day attacks and logging security threat prevention features enabled – 6 Gbps real world/production environment/Application Mix. - Firewall should support at least 3000 new connections per second or more and shall support at-least 1Million concurrent session/connection with all application control enabled. - No of VLANs – 100 - Minimum IPSec VPN peers – 1000 - Firewall should have at least 1.5 Gbps of VPN throughput.. 20; a. Minimum number of 1 Gbps LAN ports - 4 b. Minimum number of 10 Gbps ports – 12 c. Separate HA port All the SFP+ port should have compatible transceivers (Short Range Transceiver) along-with required FO cables.. |
|  | Vol-II Part- B, Appendix-H, Hardware DRS | 16. Anti-APT Sl no. 18: Number of’VM's/sandbox images should be more than 8 from day 1 and running simultaneously. Sl no. 21: Should have dual AC power supply. | 16. Anti-APT Sl no. 18: Number of’VM's/sandbox images should be 6 or more from day 1 and running simultaneously. Sl no. 21: Deleted |
|  | Vol. II Part-B, Appendix-H, Hardware Specification, Table 16: Anti-APT | Sr. No.; Minimum Required Specifications; Offered by the Contractor. 10.; The proposed solution should have the ability toanalyze, detect andblock malware in common file formats including but not limited to executables, JAVA, PDF, MS Office documents,. 11.; common multimedia contents such as HTML/FLASH/file etc and ZIP/RAR/7ZIP etc. archives to prevent advanced Malware and Zero-day attacks.. | Replaced with Sr. No.; Minimum Required Specifications; Offered by the Contractor. 10.; The proposed solution should have the ability to analyze, detect and block malware in common file formats including but not limited to executables, JAVA, PDF, MS Office documents, common multimedia contents such as HTML/FLASH/file etc. and ZIP/RAR/7ZIP etc. archives to prevent advanced Malware and Zero-day attacks.. |
|  | Vol. II Part-B, Appendix-H Hardware DRS | 18. Remote console (All-in-One) Point No. 3: Min 8 core latest processor (along with latest chipset), Clock Speed 3.0 GHz or more (minimum base frequency) | Replace with Point No. 3: Min 8 core latest processor (along with latest chipset), Clock Speed 2.4 GHz or more (minimum base frequency) |
|  | Vol. II Part-B, Appendix-H, Hardware Specification, Table. - 19, Laptops | a. For Maintenance b. For DTS c. For RTU Testing d. VAPT e. PCMT | Replace with a. For Maintenance b. For DTS c. For RTU Testing d. VAPT e. PCMT f. For Video Conferencing System |
|  | Vol. II Part-B, Appendix-H Hardware DRS | 20. Video Projection Syst–m - LASER (VPS) Point no. 14: Median Laser life – Minimum 80,000 Hours | 20. Video Projection Syst–m - LASER (VPS) Replaced with Point no. 14: Median Laser life – Minimum 1,00,000 Hours |
|  | Vol. II Part-B, Appendix-H Hardware DRS | 21. Video Wa–l - Floor / Wall Mounted (55’’ Diagonal) Point no 20: Internal Auxiliary memo–y - 300GB SSD | 21. Video Wa–l - Floor / Wall Mounted (55’’ Diagonal) Replaced with Point no 20: Internal Auxiliary Memory – 256GB SSD |
|  | Vol. II Part-B, Appendix-H Hardware DRS | 24. Weather Sensors for Server Room | New inserted 24. Weather Sensors for Server Room & Battery Room ….. 7. MODBUS TCP/IP support for integration with SCADA ¦ Yes ….. |
|  | Vol-II Part- B, Appendix-H: Hardware Specification | 26. PC for DCPC Point No. 6: RAM 2x16 GB delivered, expandable up to 64GB 2133Mhz ECC DDR4 or Above Point No. 9: Interfaces Two nos 1 Gbps Ethernet ports, 2xUSB Ports, HDMI Port, 2xSerial, 1xParallel Port | 26. PC for DCPC Replace with Point No. 6: RAM 2x16 GB delivered, expandable up to 64GB 2133Mhz DDR4 or Above Point No. 9: Interfaces Two nos 1 Gbps Ethernet ports, 2xUSB Ports,1xHDMI Port, 2xSerial |
|  | Vol. II Part-B, Appendix-H, Hardware Specification, Table:27, Color Laser Printer | Sr. No.; Description of the Features; Minimum Quantity of the features; Offered by the Contractor. 3.; Functions; Print, scan, email, fax. 15.; Interface; Dual 1GB internal LAN ports. | Replaced with Sr. No.; Description of the Features; Minimum Quantity of the features; Offered by the Contractor. 3.; Functions; Print, scan, email, copy. 15.; Interface; Dual 1GB internal LAN ports (2nd Port could be Print Server). |
|  | Vol. II Part-B, Appendix-H, Hardware Specification, Table:28, Black & White Laser Printer (Multifunction Device) | Sr. No.; Description of the Features; Minimum Quantity of the features; Offered by the Contractor. 3.; Functions; i) Print, ii) Scan iii) Copy iv)Fax. 11.; Paper handling capacity; Minimum 500 sheets for input tray & 500 sheets for output tray. Duplex Automatic document feeder for minimum 15 pages (scan/fax).. 15.; Interface; Dual 1GB internal LAN ports. | Replaced with Sr. No.; Description of the Features; Minimum Quantity of the features; Offered by the Contractor. 3.; Functions; i) Print, ii) Scan iii) Copy iv) Email. 11.; Paper handling capacity; Minimum 500 sheets for input tray & 500 sheets for output tray. Duplex automatic document feeder for minimum 15 pages (scan).. 15.; Interface; Dual 1GB internal LAN ports (2nd Port could be Print Server). |
|  | Vol-II Part- B, Appendix-H: Hardware Specifications | 31. Centralized Keyboard & Mouse Control Solution (CKMC) Point No. 12 It shall allow flexible interface combinations (PS/2, USB with VGA, DVI, HDMI and DisplayPort video interface, Sun and serial) to control all computer types. Point No. 15 Each set support at-least eight (8) sets of systems. | 31. Centralized Keyboard & Mouse Control Solution (CKMC) Replace with Point No. 12 It shall allow flexible interface combinations (USB, DVI, HDMI and DisplayPort video interface, Sun and serial) to control all computer types. Point No. 15 Each set support at-least twelve (12) sets of systems for RLDC & at-least 6 system for SLDCs. Add New Point No. as 16 Multi-viewer capabilities to show all sources in a big screen and can view as well as controlled using single Keyboard/ mouse in real-time. |
|  | Vol-II Part- B, Appendix-H: Hardware Specifications | 35. Hard Disk Sr. No.; Description of the Features; Minimum Quantity of the features; Offer by the Contractor. 3; Type; HDD. | 35. Hard Disk Replace with Sr. No.; Description of the Features; Minimum Quantity of the features; Offer by the Contractor. 3; Type; SSD. |
|  | Vol-II Part- B, Appendix-H: Hardware Specifications | 36. A4 sized Multi-Function Printer (Multifunction Device) Sr. No.; Description of the Features; Minimum Quantity of the features; Offer by the Contractor. A4 sized multi-function device having mono-Ink Tank Printing, Copying, Scanning and Fax capabilities with minimum 2.5” touch screen control panel. 9; No. of main paper tray (minimum); 10/100 Ethernet network port. 10; Connectivity Port; Heavy duty, 100000 pages per month. 13; Scanned file format; JPEG, TIFF, PDF. | Replace with 36. A4 sized Multi-Function Printer Ink – tank (Mono) Sr. No.; Description of the Features; Minimum Quantity of the features; Offer by the Contractor. A4 sized multi-function device having mono-Ink Tank Printing, Copying and Scanning capabilities with minimum 2.5” touch screen control panel. 9; No. of main paper tray (minimum); 2. 10; Connectivity Port; 1x USB 2.0 high speed port & 1 Gigabit Ethernet network port. 13; Scanned file format; JPEG, PDF. |
|  | Vol-II Part- B, Appendix-H: Hardware Specifications | 38. Splitter Revised specification requirement for splitter | 38. Splitter Replace with Revised DRS of Splitter attached at Annexure-A. |
|  | Vol-II Part- B, Appendix-H-1: Software Specifications | 3. SIEM Sl no. 12 Logs must be retained for at least three years (3 months online and remaining offline/ compressed) on centralized storage (SAN/NAS). All logs must get auto archived on centralized storage directly from Log management layer and archived logs must be readable from archival/ central storage directly. Sl No 22 The UEBA must be offered fully integrated within the proposed solution. | 3. SIEM Replace with Sl no. 12 Logs must be retained for at least one year (3 months online and remaining offline/ compressed) on centralized storage (SAN/NAS/Server). All logs must get auto archived on centralized storage directly from Log management layer and archived logs must be readable from archival/ central storage directly. Storage capacity of SAN and NAS doesn’t include the SIEM logs storage capacity (as per TS requirement). Log storage capacity of SIEM varies from OEM to OEM as per compression ratio, hence, storage space for SIEM log shall be considered additionally over and above the specified SAN storage capacity for the control centre without any additional cost to Owner. Sl No 22 The UEBA must be offered fully integrated within the proposed solution. All devices such as laptop, desktop, servers etc. being supplied under this project are to be covered under UEBA. |
|  | Vol-II Part- B, Appendix-H-1: Software Specifications | 4. Identity Management System Point no. 11. The solution should support risk-based policies be created in the solution to support notification/ alerting when user risk profiles change. Point no.13. The solution should detect and alert on role violations before assigning roles to users. Point no.16. The solution should provide out-of-the-box connectors for automatically pushing changes to enterprise IT systems. | 4. Identity Management System Replace with Point no. 11. The solution should support risk-based policies be created in the solution to support notification/ alerting when user risk profiles change (location of log in, type of browser, type of LAN, time). Point no.13. The solution should detect and alert on role violations before assigning roles to users such as role violations alert in case of assignment of network admin role and database admin role to a user. Point no. 16. The solution should provide out-of-the-box connectors for automatically pushing changes to IT systems (such as NMS, NAC etc. supplied in this project) |
|  | Vol-II Part- B, Appendix-H-1: Software Specifications | 7. Virtualization Software and Manageability 1. Solution should have a commercially available bare metal hypervisor with no dependency on General purpose OS and that should have all Virtualization benefits like High Availability and automated live migration of Virtual Machines from one physical server to another in case of any failure. 2. The solution should provide Zero downtime, zero data loss and continuous availability for the applications running in VM's in case of physical host failure without the need for clustering software. 3. Migration of VMs in case one server fails all the Virtual machines running on that server shall be able to migrate to another physical server running same virtualization software. 4. Hypervisor shall provide the ability to hot add vCPU and memory to live Guest VMs without any reboot or shutdown of Guest VM. Shall also allow to add hot‐plug disks and NICs (provided the same is supported by guest OS)….. . …. 6. Ability to move and copy virtual machines as easily as moving and copying files. Ability to provision or migrate any virtual machine from one physical server to another physical server (over LAN as well as WAN) with zero downtime, continuous service availability and complete transaction integrity. ……. | 7. Virtualization Software and Manageability Replace with 1. Solution should have a commercially available bare metal hypervisor with no dependency on General purpose OS. 2. Deleted 3. Migration of VMs in case one server fails all the Virtual machines running on that server shall be able to migrate to another physical server running same virtualization software on requirement. 4. Hypervisor shall provide the ability to hot add vCPU and memory to live Guest VMs without any reboot or shutdown of Guest VM. …. ……6. Deleted …… |
|  | Vol. II Part-B, Appendix-I | A.2 Minimum Information to be associated with an analog for Time block (for each 15 min) • Reactive Energy as per SEM philosophy | A.2 Minimum Information to be associated with an analog for Time block (for each 15 min) Replace with • Reactive Energy as per Owner provided SEM (Special Energy Meter) philosophy: |
|  | Vol. II Part-C, Section-2, Clause 2.5.2 | Display …Front Panel 7” or more Graphical Display: The UPS control panel shall provide a touch color graphic display for indication of UPS status, metering, battery status, alarm/event log, and advanced operational features….. | Display Replace with …The UPS control panel shall have front facia display etc for indication of UPS status, metering, battery status, alarm/event log, and advanced operational features…. |
|  | Vol-II Part- C, Section 2, Clause: 2.9 | Enclosures/Earthing ............ Modules and subassemblies shall be easily replaceable and maintainable with front access only. .......... | Enclosures/Earthing Replace with .......... Modules and subassemblies shall be easily replaceable and maintainable. ........... |
|  | Vol-II Part- C, Section 3, Clause: 3.0 | Introduction … The supplier, supplying the cells/batteries as per this document shall be responsible to replace/repair free of charge, the battery/cell becoming faulty, owing to defective workmanship or material. Contractor shall be responsible for the replacement of faulty battery cells during entire period of contract (including extension of contract, if any). Irrespective of the design/expected life of the supplied batteries, Replacement of faulty batteries and or entire battery bank up to the completion of one year DLP and 6 years AMC period including extension of contract, if any, shall be in the scope of the contractor, without any cost implication to the Owner. Batteries shall be tested and maintained as per the code mentioned in Indian Standard IS: 14782:2000. As per this standard, the Contractor shall periodically (quarterly) determine whether the rating of battery is holding up using capacity tests. Also, C10 Capacity test shall be done periodically (yearly), to determine whether the rating of battery is holding up using capacity test. If the battery capacity is less than 80% of its design value in any of the cases, the battery shall have to be replaced by contractor during entire period of contract (including extension of contract, if any) without any cost implications to owner. If number of cells replaced(cumulative) in battery bank exceeds more than 25% of total battery bank then contractor shall replace that entire battery bank without any additional cost to the Owner during entire period of contract (including extension of contract, if any). | Introduction Replace with ….The supplier, supplying the cells/batteries as per this document shall be responsible to replace/repair free of charge, the battery/cell becoming faulty, owing to defective workmanship or material during entire period of contract (including extension of contract, if any), without any cost implication to the Owner. Batteries shall be tested and maintained as per the code mentioned in Indian Standard IS: 14782:2000. Capacity test @ C10 shall be done periodically (yearly), for assessment of health of the battery bank to determine charge holding capacity of battery bank. The conditions for batteries/battery bank replacement shall be as per the provisions mentioned under Clause 1.10, Section 1, PART A of technical specifications along-with other scope of works specified under the contract. |
|  | Vol. II Part-C, Section-4, Clause No.-4.0 | Scope of Supply ….This net electrical output shall be measured after reducing all power consumptions for D.G. Set auxiliaries. …… (e) Base frame, mounting pads, foundation bolts etc (as required) | Scope of Supply Replace with ….This net electrical output shall be measured after reducing all power consumptions for D.G. Set auxiliaries. The Contractor shall supply the DG set as per the specifications given in this section. Also, the supplied DG Sets shall comply with the latest emission norms of CPCB..…… (e) Base frame, mounting pads, AVM pads and foundation bolts etc (as required) |
|  | Vol- II, PART-C, Section 4,Clause 4.4.1 | Diesel Engine p. Heat Exchanger system | Diesel Engine This point Deleted. |
|  | Vol- II, PART-C, Section 4, Clause 4.4.4 | Fuel and lubricating oil system D. All required piping, fittings valves, filters, strainers, lubricating oil heat exchangers, temperature and pressure gauges, by pass valves, pressure switches, alarm controls, thermostat, cooler accessories, hose pipes and other accessories, instruments, equipment needed for the above services are covered under the scope of the Contractor. | #### Fuel and lubricating oil system Replace with D. All required piping, fittings valves, filters, strainers, temperature and pressure gauges, by pass valves, pressure switches, alarm controls, thermostat, cooler accessories, hose pipes and other accessories, instruments, equipment needed for the above services are covered under the scope of the Contractor. |
|  | Vol- II, PART-C, Section 4, Clause 4.5 | Control and Instrumentation including AMF panel e) Locally mounted pressure and temperature gauges on the concerned piping on inlet and outlet of cooling water for heat exchanger | ### Control and Instrumentation including AMF panel This point Deleted. |
|  | Vol- II, PART-C, Section 4, Clause -4.4.12.2 | ##### Battery and Battery Charger Two nos. 12/24V batteries (maintenance free) complete with all leads, terminals and stand shall be provided. Each battery shall have sufficient capacity to give 10 nos. successive starting impulse to the diesel engine without recharging. The battery charger shall be complete with transformer, suitable rating (415 V, 3 Ph., 50 Hz/230V, 1Ph., 50 Hz) rectifier circuit, charge rate selector switch for “trickle”/’boost’ charge, D.C. ammeter & voltmeter, annunciation panel for battery charge indication / loading / failures. The charger shall float and Boost Charge the battery as per recommendation of manufacturer of battery. The charger shall be able to charge a fully discharged battery to a state of full charge in 8 Hrs. with 25% spare capacity. Manual control for coarse and fine voltage variation shall be provided. Float charger shall have built-in load limiting features. Ripple shall not be more than 1% (r.m.s) to get smooth DC voltage shall be provided. Charger shall be provided with Out-put Voltmeter & Ammeter. Changeover scheme for selecting battery and battery charger by changeover switch should be provided. Normally the float charger shall supply continuous DC requirements and trickle charge the battery floating on DC bus. The boost charger unit shall quick charge the battery as and when required. Battery charger using semi-conductor rectifier shall be provided with all accessories mounted in an enclosed sheet steel cubicle. Battery charger, which shall normally be used as trickle charger, shall have built in automatic voltage control to maintain output DC voltage within one percent of the voltage setting when input AC supply has voltage and frequency variation. When the battery has been substantially discharged, boost charger shall quick charge the battery. For quick charging, charger shall have a built in automatic constant current characteristic load-limiting feature. | ##### Battery and Battery Charger Replace with Two sets of 12/24V batteries (maintenance free) complete with all leads, terminals and stand along with battery chargers shall be provided. Each battery shall have sufficient capacity to give 10 nos. successive starting impulse to the diesel engine without recharging. The battery charger (230V, 1-Ph, 50 Hz) shall be SMPS based (rating as per Annexure-A) with provision for trickle/boost charge and complete with D.C. current & voltage display, battery charge status & loading indications, charger failures annunciation. Float charge mode shall have built-in current limiting features. One set of Battery & Battery Charger shall form an independent system, thus there will be two such systems i.e., Main + Standby systems for Engine Starting. In case of failure of main system, it should be possible to switchover the engine starting on the Standby system. |
|  | Vol- II, PART-C, Section 4,Clause 4.5 | Control and Instrumentation including AMF Panel e) Locally mounted pressure and temperature gauges on the concerned piping on inlet and outlet of cooling water for heat exchanger e) Low lube oil pressure ….All annunciations and DG parameters shall also be extended till Control Rooms and integrated with SCADA Systems through SNMP/MODBUS communication….. | Control and Instrumentation including AMF Panel e) This bullet deleted e) This bullet deleted ….All annunciations and DG parameters shall also be extended till Control Rooms and integrated with SCADA Systems through MODBUS TCP/IP protocol (either from directly or converter). The converter if required, shall be under the scope of contractor…. |
|  | Vol- II, Part-C, Section 4, Clause-4.10 | ANNEXURE-A, D.G. SET MAJOR TECHNICAL PARAMETERS | ANNEXURE-A, D.G. SET MAJOR TECHNICAL PARAMETERS Replace with Revised table is attached at Annexure-A. |
|  | Vol- II, Part-C, Section 6, Clause-6.1 | Power Cables All external power cables i.e., LT Panel to Input ACDB/UPS shall be stranded Aluminum conductor, armoured XLPE/PVC insulated and sheathed, 1100V grade as per IS 1554 Part-I. The conductor for the Neutral connection from UPS to Output ACDB shall be sized 1.8 times the size of the Phase conductors to take care of the non-linear loads. However, all other cables i.e., between UPS and Battery bank / UPS, ACDB to Distribution Box, Load /all inter-panel cabelling etc. shall be of copper conductor (Armoured/ flexible type, which will be decided by Employer/owner, wherever applicable). | Power Cables All external power cables i.e., LT Panel to Input ACDB/UPS shall be stranded Copper conductor, armoured XLPE/PVC insulated and sheathed, 1100V grade as per IS 1554 Part-I. The conductor for the Neutral connection from UPS to Output ACDB shall be sized 1.8 times the size of the Phase conductors to take care of the non-linear loads. All cables such as between UPS and Battery bank / UPS, ACDB to Distribution Box, Load /all inter-panel cabelling etc. shall be of copper conductor (Armoured/ flexible type, which will be decided by Employer/owner, wherever applicable). |
|  | Vol-II PART-C Section 8, Clause 8.2 | Scope of Work a) …….. . if not replenished/replaced immediately, shall be replenished /replaced within 15 Days at site. c) Monthly and quarterly report of routine and breakdown maintenance will be forwarded to Owner coordinator for review & comments. The report should be submitted so as to reach Owner office by 7th day of every month. d) Contractor shall repair/replace faulty cards/modules or equipment identified during the maintenance within fifteen (15) days. | Scope of Work Replace with a) ……. if not replenished/replaced immediately, shall be replenished /replaced within 45 Days at site. c) Monthly/Quarterly reports (as applicable) for Routine and Breakdown Maintenance will be forwarded to Owner coordinator for review & comments. The report should be submitted so as to reach Owner office within 7th day of each due month. d) Contractor shall repair/replace faulty cards/modules or equipment identified during entire contract period. |
|  | Vol. II Part-C, Section-8, Clause-8.4.1 | 8.4.1 Scope of Maintenance of Batteries & UPS Batteries shall be tested and maintained as per the code mentioned in Indian Standard IS: 14782:2000. As per this standard, the Contractor shall periodically (quarterly) determine whether the rating of battery is holding up using capacity tests. Contractor shall be responsible for the replacement of faulty battery cells during entire period of contract (including extension of contract, if any). Irrespective of the design/expected life of the supplied batteries, Replacement of faulty batteries and or entire battery bank up to the completion of one year DLP and 6 years AMC period including extension of contract, if any, shall be in the scope of the contractor, without any cost implication to the Owner. Also, C10 Capacity test shall be done periodically (yearly), to determine whether the rating of battery is holding up using above test. If the battery capacity is less than 80% of its design value in any of the cases, the battery shall have to be replaced by contractor during entire period of contract (including extension of contract, if any) without any cost implications to owner. If number of cells replaced(cumulative) in battery bank exceeds more than 25% of total battery bank then contractor shall replace that entire battery bank without any additional cost to the Owner during entire period of contract (including extension of contract, if any). | 8.4.1 Scope of Maintenance of Batteries & UPS Replace with ….. Batteries shall be tested and maintained as per the code mentioned in Indian Standard IS: 14782:2000. Capacity test @ C10 shall be done periodically (yearly), for assessment of health of the battery bank to determine charge holding capacity of battery bank. The supplier, supplying the cells/batteries as per this document shall be responsible to replace/repair free of charge, the battery/cell becoming faulty, owing to defective workmanship or material during entire period of contract (including extension of contract, if any), without any cost implication to the Owner. The conditions for batteries/battery bank replacement shall be as per the provisions mentioned under Clause 1.10, Section 1, PART A of technical specifications along-with other scope of works specified under the contract. |
|  | Vol. II Part-D, Section 1, Clause 1.5, Modem | 1.5 Modem The modems can be used for RTU communicating to master station. The Contractor shall supply two (2) number modems one at Control Centre/Stand alone and other at RTU end. …… | 1.5 Modem Replace with The modems can be used for RTU communicating to master station. The Contractor shall supply modems as per BPS. |
|  | Vol. II Part-D, Section-2, Clause-2.6 | Expected Battery Life ……However, irrespective of the design/expected life of the supplied batteries, Replacement of faulty batteries and or entire battery bank up to the completion of one-year DLP and 6 years AMC period, shall be in the scope of the contractor, without any cost implication to the Owner. | Replace with Expected Battery Life for DCPS ……Batteries shall be tested and maintained as per the code mentioned in Indian Standard IS: 14782:2000. Capacity test @ C10 shall be done periodically (yearly), for assessment of health of the battery bank to determine charge holding capacity of battery bank. The conditions for batteries/battery bank replacement shall be as per the provisions mentioned under Clause 1.10, Section 1, PART A of technical specifications along-with other scope of works specified under the contract. |
|  | Vol. II Part-D, Appendix-A | Sikkim RTU I/o Count | Deleted |
|  | Vol-II PART-E Section-1 | Video Conferencing Equipment | Video Conferencing Equipment Replace with Revised TS is attached at Annexure-A. |