## Sheet1
Clarification No I dated 18/06/2025 to the bidding documents for Package – I: National Unified Network Management System (N-UNMS) for Central Sector & State Sector Communication Network under Establishment of State-of-the-Art National Unified Network Management System N-UNMS for Central Sector & State Sector Communication Network. Spec. No: CC/NT/W-MISC/DOM/A06/25/06311
S. No | Clause No. | Section No. | Page No. | Existing Clause | Queries / Recommendation for Change | POWERGRID Reply
1 | 1.13 | Section 1 | 18 | 18. TEC GR No: TEC GR No TEC/GR/I/ESI-001/03/MAR12 for Mid-Tier Storage. | As PGCIL is looking for All NVMe storage. Some of the point of TEC GR may not be applicable to NVMe storage as TEC GR was made 10+ year back. We understand DRS requirement is final and supersede TEC GR. Kindly confirm. | Bidder to Comply TS
2 | 1.13 | Section 1 | 18 | TEC-GR No: GR/LSW-01/04 MAR-11 for LAN Switches | Modification: Request to kindly remove this clause Justification: Since the TEC-GR for Network Switches was published more than 10 years ago, hence most of the technical specifications mentioned in the TEC-GR for LAN Switches are not applicable in today's world. This restricts major Network switch OEMs from participation. Since the LAN Switch Specifications are already mentioned in the section "16. LAN Switch" on Page-307 of the RFP. Hence request to kindly remove the TEC-GR requirement for the same, in order to allow wider OEM participation. | Bidder to Comply TS
3 | 1.13 (18) | Section 1 | 18 | 18. TEC GR No: TEC GR No TEC/GR/I/ESI-001/03/MAR12 for Mid-Tier Storage. | Change To: TEC/GR/IT/DSI-001/04/DEC 2015 for Mid-Tier Storage. Query: As per the RFP page-308 section- "5.6 Storage Area Network (SAN) based Storage", All-Flash NVME storage has been envisaged. While the TEC-GR specification has been mentioned for Mid-Range Hybrid Storage. Kindly suggest if TEC-GR for Mid-Range Storage (section 3.5) needs to be considered, or if the "TEC GR for All Flash Arrays (Section 3.2)" to be considered? 1.Old TEC-GR number for Storage system has been mentioned in the RFP. Kindly mention the latest TEC-GR for wider participation from all the OEMs. 2. RFP specs are mentioned for All-Flash SAN Storage. While the TEC-GR are mentioned for Mid-Tier Hybrid Storage, which is contradictory. Request to kindly clarify if Mid-Tier Hybrid storage is envisaged Or if All-Flash Storage is envisaged? | TEC GR for All Flash Storage Shall be Applicable. Bidder to Comply TS.
4 | 1.0(b) | Section 1 | 3 | b) Network Configuration Planning - This shall enable user to Design, Assign, Activate/Provision/Configure (Through Regional UNMS), Network Planning & Capacity Optimization for the Communication system under the scope | What is expected in "Network Planning & Capacity Optimization for the Communication system under the scope" | Bidder is required to Plan Communication network and optimize the present capacity being used by the communication system
5 | 1.1.1.4 (a) | Section 1 | 5 | (a) A change of status of UNMS database is detected | Change suggested: (a) A change of status of UNMS is detected. The R-UNMS should send the "notification" when there is a "STATUS" change. | The point has been clarified at Vol-II Part B Section -2 Point 2.3.3. Bidder to Comply TS
6 | 1.1.1.4 (b) | Section 1 | 5 | (b) UNMS completion of a successful remote configuration action | N-UNMS will send activation details to corresponding R-UNMS and further R-UNMS will send the activation request to the underling network and to provide the activation status to N-UNMS. | The point has been clarified at Vol-II Part B Section -2 Point 2.3.3. Bidder to Comply TS
7 | 1.2.1 | Section 1 | 6 | The N-UNMS system shall acquire data of inter-regional links & cross-border links by exception from different Regional UNMS using different protocols. | Inter regional links should be loaded in N-UNMS & details shall be provided by PGCIL. Pl clarify | Details shall be provided during detailed Engineering. Bidder to Comply TS
8 |  | Section 1 | 7 | Software utilities shall be provided in the ISR System to back-up the Historian data to an auxiliary memory (e.g. SAN System) available on network. This software shall have the feature of automatic as well as the manual backup of data. | Query: It is mentioned that backup to an SAN systems. Where as Technical specifcation has requested for NAS/Purpose built backup appliance. Please clarify. | Backup shall be kept at SAN/NAS/Backup Appliance. Details shall be finalized during detailed engineering. Bidder to Comply TS
9 | 2.1 | Section 2 | 4 | N-UNMS applications shall facilitate centralized supervision & Monitoring of the Regional and State level Communication system being used for Power System Operation & Monitoring on round the clock basis. This system shall also assist in the operations and maintenance of the communication resources including detection of circuit failure and system performance, the diagnosis of problems, the implementation of system suggested remedial actions and the allocation or reallocation of communications resources. The database shall be available centrally at National-UNMS, N-UNMS shall have capability to Store all backup data of Regional UNMS system in case of failure of Regional UNMS system, Additional Storage shall be provided at National UNMS. | In case of R-UNMS failure, the N-UNMS will retain the last colledted data from R-UNMS N-UNMS shall have capability to store all backup data of Regional UNMS system in case of failure of Regional UNMS system, Additional Storage shall be provided at National UNMS DC & DR. Is our understanding correct? | Additional Storage Requirement is already mentioned in the technical specification. Bidder to comply TS
10 | 2.8 | Section 2 | 36 | RBAC f. Permission for resizing the instance. | Need clarification on this clause. | Role base access control should be available so that only designated users should be able to resize the instance so that there is no unintended changes in VM
11 | 2.8 | Section 2 | 36 | Credential Score The offered Hypervisor shall support both internal and external Credential store for securely pulling in the username and password, access and secret key along with key pair and SSH certificates. | Need clarification on this clause. | A credential store is needed to secure digital repository for storing sensitive information like usernames, passwords, and keys used for authentication. It is needed to manage and protect these credentials, preventing their exposure and unauthorized access and enable automated authentication.
12 | 2.9 | Section 2 | 38 | The email solution should support sandboxing integration to protect zero-day malware & APT. | Is this an ask to provide sandboxing solution or Email should integrate with Any Sandboxing solution ? | Email should integrate with Sandboxing solution that is part of this Project. Bidder to comply TS
13 | 2.9 | Section 2 | 38 | The email clients shall have features like email notification, Address books, user definable folders etc. | These features are part of MTA solution and not Email Security solution as the email management is done on the MTA | Bidder to Comply TS
14 | 2.2 (b) | Section 2 | 4 | b) The source codes /web-services based open APIs of the proposed N-UNMS application shall be provided to the Employer to allow integration with upper- layer or same layer management systems via WSDL or XML/SOAP/HTTPS etc. | Suggested change: b) The Web-services based open APIs of the proposed N-UNMS application shall be provided to the Employer to allow integration with upper- layer or same layer management systems via WSDL or XML/SOAP/HTTPS etc. | Bidder to Comply TS
15 | 2.2 (f) | Section 2 | 5 | f) It is responsibility of the contractor to tie up (commercially and technically) with existing Regional UNMS vendors for integration of regional UNMS system with National UNMS system. | It shall be the responsibility of R-UNMS supplier to provide details required for integration as part of Reginal UNMS contract. Why commerical tie up is required with R-UNMS supplier ? | Bidder to Comply TS
16 | 2.3.1 | Section 2 | 5 | The N-UNMS Application shall do Automatic Topology Discovery for complete network from regional UNMS and shall also create Regional and State/ Utility/ Area Communication Network Model for real time application and for study purpose. Appropriate Bridge/Agent/Adapter software for each Vendor technology shall communicate Existing UNMS systems. | Regional links will be shared by R-UNMS. Inter Regional links shall be loaded in the N-UNMS. N-UNMS will not communicate to any of the Regional network. Is our understanding correct? | N-UNMS will communicate with R-UNMS. Bidder to Comply TS
17 | 2.3.2 (28) | Section 2 | 7 | 28) Standard nomenclature tool for naming the Nodes, channels(Trails) and Physical links: System Should have Tool to provide additional alias name to all Nodes, Channels, Physical links and maintain the same in all modules of N-UNMS for the purpose of Planning Fault management , performance management All Database for implementing Naming convention tool is to be manually created by the contractor in coordination with the Users (RLDC’s,NLDC,CTU,CEA,States & POWERGRID) | N-UNMS shall provide the additional place holder for having the alias for Node, Port, Link, Channel | Bidder to Comply TS
18 | 2.3.2. (22) | Section 2 | 7 | 22) The system shall have the capability to expose the discovered data through standard NBI e.g. TMF 814 etc. to external 3rd party systems | What are the 3rd party systems available in existing ecosystem? Pl share list with interface/protocol supported. | Bidder to Comply TS
19 | 2.3.2. (23) | Section 2 | 7 | 23) The system shall have the capability to expand along with the network. The system shall be able to accommodate new vendor of UNMS System. | New vendor integration is part of the R-UNMS. Pl clarify | System should support any new System that has been integrated with R-UNMS or in future if any new R-UNMS system comes, System should have the capability to integrate that New R-UNMS into the N-UNMS. Bidder to comply TS
20 | 2.3.2. (27)(i) | Section 2 | 7 | i. The system should be capable of monitoring passive inventory (inventory in stores, issued to contractor for deployment or in transit etc.). Passive inventory needs to be manually discovered. As part of initial Inventory loading to the system, the contractor shall be responsible to consider all the existing Network Inventory for building database and configure the same and correlation of services with respect to allocated Network Services and Network resources. | What is the purpose of passive inventory functionality in N-UNMS ? | Bidder to Comply TS
21 | 2.3.3 (1) | Section 2 | 8 | 1) The purpose of Network Configuration & Planning System is to enable design, assign, and plan new services in the communications networks from a central location. A User enters the necessary information into system. Configuration Planning system Checks for the availability of bandwidth in the Node and best suitable available path in its database and create a virtual feasible link with alternate options for forwarding to regional UNMS team for execution/Configuration. | N-UNMS will send activation details to R-UNMS. | N-UNMS will send activation details to R-UNMS. R-UNMS then further send the Activation command to underlying NMS/NE. Bidder to Comply TS
22 | 2.3.3 (15) | Section 2 | 9 | 15) The system shall send planning transactions to the UNMS in the real time | Pl provide clarification on this clause? | All planning Transactions should be done in real time. Bidder to comply -TS
23 | 2.3.3 (2) | Section 2 | 8 | 2) The Configuration Planning tool shall interface with the inventory management system and update service and network inventory. | Is Configuration Planning tool referring to Service Design functionality. Pl clarify | Bidder to Comply TS
24 | 2.3.3 (3) | Section 2 | 8 | 3) The system shall be able to check that the requested service is provisioned on the required network elements/NMS by Regional team. | It shall be the responsibility of R-UNMS supplier to publish the activation results to N-UNMS. | The N-UNMS system should have functionality to get confirmation from R-UNMS about the request. Bidder to comply -TS
25 | 2.3.4 (14) | Section 2 | 12 | 14) The System shall provide a comprehensive alarm correlation facility which shall be used for following primary purposes: - | N-UNMS will show the alarms received from the R-UNMS. Similarly, the RCA computed by the R-UNMS will be shown in N-UNMS. Does it N-NMS needs to find the RCA ? Pl clarify. | Bidder to comply -TS
26 | 2.3.4 (19) | Section 2 | 13 | 19) The System should enable engineers to request suppression of alarms from a particular managed object, or a group of managed objects or an entire managed network element. Alarms from those objects that are marked as “suppress” should be logged but not passed on for handling. | R-UNMS shall raw alarms to N-UNMS and N-UNMS has to supress the alarms. Pl clarify | The N-UNMS should have the mentioned functionality. Bidder to comply -TS
27 | 2.3.4 (20) | Section 2 | 13 | 20) The System shall be able to recognize duplicate alarms by comparing incoming alarms to those already in the current problem list for the reporting object, based on one or more alarm attributes (for example, object name and notification identifier), and automatically suppress such alarms. | R-UNMS shall raw alarms to N-UNMS and N-UNMS has to supress the duplicate alarms. Pl clarify | The N-UNMS should have the mentioned functionality. Bidder to comply -TS
28 | 2.3.6 | Section 2 | 16 | The system shall be able to correlate alarms/ node performances such as signal strength of the node and generate link/channel/service availability status for region/state/network. The availability calculation and procedure shall be as per latest notification by CEA/CERC/MoP or any govt. organization. | N-UNMS will compute the channel availability only for the Inter regional channels. Pl clarify. | The N-UNMS should have the mentioned functionality. Bidder to comply -TS
29 | 2.3.6 (19) | Section 2 | 16 | 19. Owner Details need to be maintained for channels/Link | Owner details againts NE, link, Channel shall be expected from the R-UNMS. It shall be the responsibility of the R-UNMS supplier. Pl clarify. | The N-UNMS should have the mentioned functionality. Bidder to comply -TS
30 | 2.3.6 (20) | Section 2 | 17 | outage/outage due to Force measure. But latter during the meeting it was decided that exclusion due to planned outage/outage due to Force measure was only for 15 minutes. So there should be option to apply again for the exclusion and the same shall be approved vide a workflow. There should also be an option to change the time of exclusion for planned outage/outage due to Force measure. Suppose user has applied for exclusion due to planned outage/outage due to Force measure for 30 minutes for availability calculation of a particular channel. But approver (RLDC/SLDC) only approve exclusion for 15 minutes from availability calculation. So, there should be an option to change the period while approving for exclusion from availability for planned outage/outage due to Force measure. | Workflow/Guidelines shall be provided by PGCIL | Details shall be provided during detailed Engineering. Bidder to Comply TS
31 | 2.3.6 (21) | Section 2 | 17 | 21. OPGW data base needs to be created in N-UNMS and Forwarded to CBOTM. | Need clarification on this clause. | OPGW data base to be maintained in Cloud based outage and ticketing management system. Bidder to Comply TS
32 | 2.3.6 (21) | Section 2 | 17 | All Database for implementing Naming convention and availability calculation is to be automatically fetched from system database or manually created by the contractor in coordination with the Users (RLDC’s,NLDC,CTU,CEA,States & POWERGRID) | Need clarification on this clause. | Bidder to Comply TS
33 | 2.3.6 (21) | Section 2 | 17 | Any other modifications availability calculation methods needs to be incorporated by the contractor during the execution of the project and during AMC of the contract. Availability Calculation and report formats has been attached at Appendix-L. | Need clarification on this clause. | Bidder to Comply TS
34 | 2.6.3 (19) | Section 2 | 32 | The proposed solution should block malicious traffic from data exfiltration (data leakage) | Requesting to remove | Bidder to Comply TS
35 | 2.6.3 (23) | Section 2 | 32 | The solutions should support the Automated False Positive Reclassifications to Ability to automatically reclassify activity as false positives and prevent similar detections from occurring. | Modification: The solutions should have the ability reclassify False Positive and prevent similar detections from occurring. | Bidder to Comply TS
36 | 2.6.3 (25) | Section 2 | 32 | The proposed solution should have the ability to create Whitelist/Blacklist for the files based on their names, location (File Path), version, and provider | Modification: The proposed solution should have the ability to create Whitelist/Blacklist for the files based on their names, location (File Path). | Bidder to Comply TS
37 | 8.2.2 (b)(ix) | Section 2 | 39 | Option for adding cyber security elements like firewall etc. | What is expected from N-UNMS for this clause? | The planning tool should have the functionality to Add any cybersecurity element for representation. No functional emulation is required. Bidder to Comply TS
38 | 8.2.2 (b)(x) | Section 2 | 39 | Power map can also be superimposed on communication map so that new links creation lines can be shown as option | What is expected from N-UNMS for this clause? | Bidder to comply TS
39 | 8.2.3 (h) | Section 2 | 40 | h) Identification of SLA for Constraint Orders to Plan Generation. | Need clarification on this clause. | Bidder to comply TS
40 | 5.6 | Section 5 | 10 | The SAN to be supplied at N-UNMS must have inbuilt ransomware detection and protection. | Modification: The SAN to be supplied at N-UNMS must have ransomware/Anomaly detection and protection. Justification: 1. Ransomware is only one type of cyber threat, while there can be other kind of anomalies as well. Hence request to kindly allow anomaly detection instead of Ransomware Detection which covers wider range of Anomalies / Cyber atatcks. 2. Each OEM has a different architecture. Some OEMs provide anomaly/ransomware detection using native tools on the storage system which does not have latest industry trends on cyber attacks. While some OEMs provide SaaS/cloud-based analysis for Anomaly detection, which is better since it provides protection against latest cyber threats in the industry. Hence request to kindly remove "inbuilt" word, for allowing wider OEM participation. | Bidder to Comply TS
41 | 5.6 | Section 5 | 10 | Backup from SAN storage at Main Control center of NR-UNMS, NERUNMS, ER-UNMS, WR-UNMS and SR-UNMS must be kept at SAN of N-UNMS. Any additional Software/hardware required for taking backup of existing UNMSs system to SAN at National UNMS system must be supplied by contractor without any additional cost to employer. | Query: Does this refers to replicating data from SAN storage at Main Control center of NR-UNMS, NERUNMS, ER-UNMS, WR-UNMS and SR-UNMS to SAN at N-UNMS or does this mean taking backup of data on SAN at NR-UNMS, NERUNMS, ER-UNMS, WR-UNMS and SR-UNMS and replicate it to SAN storage at N-UNMS. Current backup software at different UNMS Project is as below: NR-UNMS, NER UNMS & WR-UNMS (M/s STL) : Micro Focus. SR-UNMS (M/s NMSWork) : Veeam. ER-UNMS (M/s NMSWorks) : Networker Cross backup software replication is not supported by any OEM. So what and how do you want to achieve this? Also Existing Backup at UNMS locations is being taken on the tape drives. Hence it is not possible to replicate the backups from these locations, unless PGCIL invests in backup appliances at these main Control centers as well. | Bidder to Comply TS
42 | 5.7 (15) | Section 5 | 12 | The solution should protect the endpoints against advanced threats including zero-day attacks, which target application vulnerabilities that have yet to be discovered or patched. | Kindly remove. End point protection is features provided by EDR | Bidder to Comply TS
43 | 5.7 (25) | Section 5 | 13 | Traffic Learning to be based full packet analysis | Solution works on NetFlow and SPAN basic. Baselining is created based on the packet header information and with added AI/ML engine that is running. | Bidder to Comply TS
44 | 5.7 (3) | Section 5 | 12 | The Solution must be capable of scanning files in seconds without transmitting any data to the cloud, ensuring fast and secure on-premises processing. | Modification: "The Solution must be capable of scanning network telemetry isng SPAN/NetFlow in seconds without transmitting any data to the cloud, ensuring fast and secure on-premises processing." | Kindly Refer Amendment No III
45 | 5.7 (8) | Section 5 | 12 | The proposed solution shall have the ability to stop the first malware download through inline blocking by integrating with the perimeter security solution such as NGFW itself (using API) | Modification: The proposed solution shall have the ability to stop the first malware download by integrating with solutions such as NGFW / Proxy / SOAR solution using Webhooks. | Bidder to Comply TS
46 |  |  | 1 | LAN Switch Qty for State | Total State LAN Switches Qty is 12 as per SOR but there are only 3 state locations. Hence, Qty should be 6. Kindly confirm the LAN Switches Qty | Bidder to Bid as Per BPS.
47 |  |  | 1 | Data Diode Qty | Data diodes will be placed at both the Regional UNMS Control Center and the National UNMS Control Center to facilitate the forwarding of logs to I3SOC, as well as updates and patch downloads. As per SOR, Total Diode Qty is 19 and location is as follows: National UNMS Project in ER-2 3 National UNMS Project in NER 3 National UNMS Project in NR-1 7 National UNMS Project in SR-2 3 National UNMS Project in WR-2 3 Please clarify for why only in one regional location, Data Diode quantity is mentioned? | Bidder to Comply TS
48 |  |  | 1 | NDR Qty | As per RFP: The contractor is required to install Network Detection and Response (NDR) systems at the main and backup control centers of the following: - National UNMS - NRUNMS - NER-UNMS - ER-UNMS - SR-UNMS - WR-UNMS It is noted that NER-UNMS does not have a backup location. Therefore, a total of 8 NDR systems are required for the other regional data canters. Additionally, 4 NDR systems are required for the main and backup control centres of the National Load Dispatch Center (NLDC). In summary, a total of 13 NDR systems are required, considering that NER-UNMS does not have a backup location. Pl clarify | Bidder to Bid as Per BPS.
49 | 1 |  | 3 | Servers for Network Resource Management, Design, Activation, Configuration Planning , Fault Management, Performance Management, Trouble Ticking, Reporting & Dash boarding, Data Historian, PDS Cum Test Bench, Data Replica, Web server and any other server except that mentioned at Point 2 etc.: 11. Server should support min. six PCI-Express 5.0 x16 slots | 5th Gen server offer high bandwidth PCIe 5.0 slots. To get maximum benefit of Gen 5 server Request to modify clause as "Server should support min. Eight PCI-Express 5.0 x16 slots and should be configured with min. six PCI-Express 5.0 x16 slots" | Bidder to Comply TS
50 | 1 |  | 4 | Servers for Network Resource Management, Design, Activation, Configuration Planning , Fault Management, Performance Management, Trouble Ticking, Reporting & Dash boarding, Data Historian, PDS Cum Test Bench, Data Replica, Web server and any other server except that mentioned at Point 2 etc.: 12.  Secure Recovery - recover critical firmware to known good state on detection of compromised firmware  Security Dashboard for Server to detect possible security vulnerabilities.  Should help to proactively identify out-of- date BIOS, drivers, and Server Management agents and enable the remote update of system software/firmware components.  Offered server should be listed on spec.org  It should support historical reporting and should have support for multifactor authentication | To reduce exposure to vlunerabilities system should have validation mechanism in run time as well. Also many time system expose to vunerability due to manual process of firmware updates and all system are not at the same baseline firmware level. To strengthen server security, request to add following clause: " For firmware security, system should support remote management chip creating a fingerprint in the silicon, preventing servers from booting up unless the firmware matches the fingerprint. This feature should be immutable. Should have encrypted virtual media Should maintain repository for firmware and drivers recipes to aid rollback or patching of compromised firmware. Should also store Factory Recovery recipe preloaded to rollback to factory tested secured firmware Should have dashboard for firmware baselines while performing minimum required firmware checks and highlighting out-of-compliance devices for updates with the selected firmware baseline Server should have runtime firmware validation Management software should be from same server OEM" | Bidder to Comply TS
51 | 1 |  | 4 | Servers for Network Resource Management, Design, Activation, Configuration Planning , Fault Management, Performance Management, Trouble Ticking, Reporting & Dash boarding, Data Historian, PDS Cum Test Bench, Data Replica, Web server and any other server except that mentioned at Point 2 etc.: 13. Bidder to offer server with Operating system and Virtualization software with OEM support as per total CPU cores/ socket configured and specifications defined for unlimited VMs. | To have smooth integration and support experience, Please add following in the specification: "OEM should be present in India for Min 5 year. OEM should provide unlimited ticket support." Also specify PGCIL would required 9x5 or 24 x 7 support. | Bidder to Comply TS
52 | 2 |  | 5 | Servers for Configuration Management Cum CMC, EDR, Identity & Patch Management : 10. Server should support min. six PCI-Express 5.0 x16 slots | 5th Gen server offer high bandwidth PCIe 5.0 slots. To get maximum benefit of Gen 5 server Request to modify clause as "Server should support min. Eight PCI-Express 5.0 x16 slots and should be configured with min. six PCI-Express 5.0 x16 slots" | Bidder to Comply TS
53 | 2 |  | 5 | Servers for Configuration Management Cum CMC, EDR, Identity & Patch Management : 11.  Secure Recovery - recover critical firmware to known good state on detection of compromised firmware  Security Dashboard for Server to detect possible security vulnerabilities.  Should help to proactively identify out-of- date BIOS, drivers, and Server Management agents and enable the remote update of system software/firmware components.  Offered server should be listed on spec.org  It should support historical reporting and should have support for multifactor authentication | To reduce exposure to vlunerabilities system should have validation mechanism in run time as well. Also many time system expose to vunerability due to manual process of firmware updates and all system are not at the same baseline firmware level. To strengthen server security, request to add following clause: " For firmware security, system should support remote management chip creating a fingerprint in the silicon, preventing servers from booting up unless the firmware matches the fingerprint. This feature should be immutable. Should have encrypted virtual media Should maintain repository for firmware and drivers recipes to aid rollback or patching of compromised firmware. Should also store Factory Recovery recipe preloaded to rollback to factory tested secured firmware Should have dashboard for firmware baselines while performing minimum required firmware checks and highlighting out-of-compliance devices for updates with the selected firmware baseline Server should have runtime firmware validation Management software should be from same server OEM" | Bidder to Comply TS
54 | 2 |  | 6 | Servers for Configuration Management Cum CMC, EDR, Identity & Patch Management : 13. Bidder to offer server with Operating system and Virtualization software with OEM support as per total CPU cores/ socket configured and specifications defined for unlimited VMs. | To have smooth integration and support experience, Please add following in the specification: "OEM should be present in India for Min 5 year. OEM should provide unlimited ticket support." Also specify PGCIL would required 9x5 or 24 x 7 support. | Bidder to Comply TS
55 | 3 |  | 7 | Workstation consoles with dual/ single monitor: 10. 10 Gbps dual LAN Ports (Minimum) for connecting on dual LAN, USB Ports, HDMI Ports. Use of external converters are allowed. | Kindly amend HDMI post as HDMI/DP For wider OEM participation. Current clause is restricting major OEMs. | Kindly Refer Amendment No III
56 | 4 |  | 8 | Remote console: 9. 10 Gbps dual LAN Ports (Minimum) for connecting on dual LAN, USB Ports, HDMI Ports. Use of external converters are allowed. | Kindly amend HDMI post as HDMI/DP For wider OEM participation. Current clause is restricting major OEMs. | Kindly Refer Amendment No III
57 | 9 |  | 10 | 4. Each VPS module size | Mainly as the specs calls in for DLP Technology this comes in standard 70" size only & not 55" as 55 inches only comes in LCD. Please clarify whether projection system or LED based Display is required. | Bidder to Comply TS
58 | 9 |  | 10 | 24. Types of video signal to be supported by VPS Controller | These are quiet old signals like PAL ,SECAM. Please see if it can be made optional | Bidder to Comply TS
59 | 12 |  | 15 | Firewall Features/Characteristics required of Internal Firewall/UTM: 5. Support NAT, PAT & Policy based NAT/PAT, Mapped IP(MIP), Virtual IP(VIP) & MIP/VIP grouping | We understand that MIP is to configure static NAT where a public IP is permanently mapped to an internal private IP and similarly VIP for a single external IP/port forwards traffic to internal servers. Please clarify if our understanding is correct or any different use-case is expected? | Bidder to Comply TS
60 | 12 |  | 15 | Firewall Features/Characteristics required of Internal Firewall/UTM: 10. System management - Using web UI, Command Line interface (console/telnet/SSH). | Different OEM have different deployment architecture, hence, requesting this minor change without diluting functional requirement. Change Requested: System management Using web UI/Command Line interface/Central Management (console/telnet/SSH). | Bidder to Comply TS
61 | 12 |  | 16 | Firewall Features/Characteristics required of Internal Firewall/UTM: 23. Antivirus, Anti-worm, anti-spam and anti-spyware protection | Anti-spam is a mail-layer function and best handled by email security gateways, which is also asked part of the RFP. Hence, we are requesting this minor modification for widder participation to make the bid more competitive and without diluting functional requirement. Change Requested: Antivirus, Anti-worm and anti-spam/anti-spyware protection | Bidder to Comply TS
62 | 13 |  | 16 | 13. Sizing Parameters Internal Firewall/UTM: Additional Point | Modification: The proposed hardware should have dual redunant hotswappable Power supply Justification: Redundant power supplies to ensure minimal downtime in operations | Kindly Refer Amendment No III
63 | 13 |  | 16 | 13. Sizing Parameters Internal Firewall/UTM: Additional Point | Modification: The proposed hardware should have dual redunant Fan Module Justification: Redundant fans to ensure minimal downtime in operations | Kindly Refer Amendment No III
64 | 13 |  | 16 | 13. Sizing Parameters Internal Firewall/UTM: Additional Point | Modification: The proposed hardware should have local storage of logs upto 900 Gb | Bidder to comply TS
65 | 13 |  | 16 | 13. Sizing Parameters Internal Firewall/UTM: Additional Point | Modification: The proposed solution should have minimum 32Gb of RAM Justification: Adequate RAM capacity to ensure optimal capacity for operating system, configurations, and data processing capabilities | Bidder to comply TS
66 | 15 |  | 17 | 11. a. Data Encryption supported DES (56bits) 3DES (168 bits) and hashing algorithm like MD5 and SHA-1 b. Filtering of packets based on source address, destination address, protocol type, user, port number, URL | Modification: a. Data Encryption supported DES (56bits) 3DES (168 bits) and hashing algorithm like MD5 and SHA-1 b. Filtering of packets based on source address, destination address, protocol type, user, port number, URL, DDoS and IPS Justification: Router is WAN facing devices and its important to have DOS protection and IPS function with the routing capability | Bidder to comply TS
67 | 15 |  | 17 | 5. Layer -2 & Layer-3 routing & Dynamic discovery of routing | Modification:Layer -2 & Layer-3 routing & Dynamic discovery of routing. Router must be configured in Routing Mode. Justification: ensuring that only Routing core platform are allowed | Bidder to comply TS
68 | 15 |  | 17 | 4. High performance Routing for data exchange between data centres and remote. | Modification:High performance Routing for data exchange between data centres and remote. Router must have Redundent Hot Swappable Power Supply and Modular Multi-Core Processor Justification: routing as multi-core and having redundencies at Power Supply considering the core devices | Bidder to comply TS
69 | 15 |  | 18 | 8. IS-IS, OSPF, BGP**, ARP, IPCP, IP forwarding, VLAN & MPLS etc. | Modification: IS-IS, OSPF, BGP**, ARP, IPCP, IP forwarding, VLAN etc Justification:Request to kindly remove MPLS as the device won't be installed in a Service provider environmernt. It will merely take a handoff from Service provider over an IGP protocol ( OSPF, BGP etc) or via Static route/ default route. | Bidder to comply TS
70 | 15 |  | 18 | Additional Point | Modification:Router must be NDcPP/EAL3+ and IPV6 Logo ready Certified Justification: Requesting to add, this is as per CEA guidelines and other devices are also asked with such certification | Kindly Refer Amendment No III
71 | 16 |  | 19 | 7. 10 Gbps Fibre Optic Ports for Connecting dual Fibre Optic LAN Minimum 8x10 Gbps Fibre Optic Ports and 16x1 Gbps Ethernet ports at main and backup control centre Minimum 4x10 Gbps Fibre Optic Ports and 8x1 Gbps Ethernet ports at remaining location | Change to: 10 Gbps Fibre Optic Ports for Connecting dual Fibre Optic LAN Minimum 2x 100G ports for MC-LAG/VPC/MLAG setup, 8x10 Gbps Fibre Optic Ports and 16x1 Gbps Ethernet ports at main and backup control centre Minimum 2x 100G ports for MC-LAG/VPC/MLAG, 4x10 Gbps Fibre Optic Ports and 8x1 Gbps Ethernet ports at remaining location 2x100G ports are to ensure redundancy towards any downstream devices or third-party switches | Bidder to comply TS
72 | 16 |  | 19 | New Point | Modification:All switches should have a minimum support for 200K MAC addresses, 160K IPv4 routes and 64K IPv6 routes Justification:The addition of the scale number ensures that the switches have certain minimal capability to handle extra MACs and routes | Bidder to comply TS
73 | 16 |  | 19 | New Point | Modification:All switches must be ONIE (Open Network Install Environment) capable, which allows for disaggregation of hardware and software to allow third-party network OS to be installed on the switch Justification:With ONIE capability, the switch becomes more open, which can allow a customer to have a different OS from another vendor on the same hardware provided that OS is interoperable. OS can be changed without needing to throw away the hardware | Bidder to comply TS
74 | 16 |  | 19 | 12. Router should support 1 GB, 10 GB Minimum 16 no. - 1 GB Ethernet ports, 8x10 Gbps Fibre optic ports At main and Backup Control Centre | Modification: Router should support 1 GB, 10 GB Minimum 16 no. - 1 GB Ethernet ports, 5x10 Gbps Fibre optic ports At main and Backup Control Centre | Bidder to comply TS
75 | 16 |  | 19 | 16. LAN Switch Additional Point | Modification:Switch should redundant hot swappable power supply and redundant Fans Justification:Redundant power supplies and fans to ensure minimal downtime in operations | Kindly Refer Amendment No III
76 | 16 |  | 19 | 16. LAN Switch Additional Point | Modification:Switch should support MacSec ( 802.1ae) to ensure encryption of layer 2 traffic from Day 1 Justification:MacSec is an industry standard, support by all leading switch vendors and a must have feature to ensure security and encyption of Layer 2 traaic | Bidder to comply TS
77 | 16 |  | 19 | 16. LAN Switch Additional Point | Modification:Switch should be Ipv6 logo certified from Day1 Justification:IPv6 logo certification ensures a tested and certified product is proposed which supports full IPv6 functionalty. | Bidder to comply TS
78 | 17 |  | 20 | SAN Storage: Request to add clause | Storage system data availability is not defined in the DRS. Request to add " Storage should have 100% data availability gurantee from OEM" | Bidder to comply TS
79 | 17 |  | 20 | SAN Storage: Request to add clause | Drive scalability is missing in the specification. Please specify "storage should be scalable to minimum 300 NVMe drives" | Bidder to comply TS
80 | 17 |  | 20 | SAN Storage: Request to add clause | Storage backend bandwidth is missing in the specification. Please specify "The offered storage inter-controller communication and disk enclosures connectivity shall via at-least 4 x 100Gbps Ports or 50GB/sec bandwidth per controller. | Bidder to comply TS
81 | 17 |  | 20 | SAN (Storage Area Network) based storage or any other specialized storage solution: 19. All NVMe System (min Gen 4 ) | Change To: All NVMe System (min TLC/MLC Grade ) Justification: Drive endurance (which defines frequency of drive failures) is missing in the Storage specifications. Request to kindly mention atleast TLC/MLC grade NVME SSD to avoid any inferior storage systems with QLC/PLC Drives that will have lower edurance (or higher failure rates). Otherwise PGCIL may end up in procuring sub-standard storage with QLC Drives having higher drive failure rates, which will ultimately pose risk to data and organizational reputation as well. | Bidder to comply TS
82 | 17 |  | 20 | SAN (Storage Area Network) based storage or any other specialized storage solution: 7. I TB (Total) | Change To: 768GB (Total) Justification: Requested capacity and performance scalability can easily be met by 768GB Cache as well. Please note that 1TB Cache is available with only few OEMs, and hence demotivates other major storage OEMs from participation. | Bidder to comply TS
83 | 17 |  | 20 | SAN (Storage Area Network) based storage or any other specialized storage solution: 22. Four Active – Active Controller to be provided. Every logical disk is striped across all offered drives and all drives shall be able to contribute the IOs to all four controllers simultaneously. | Change To: Two Active – Active Controller to be provided. Every logical disk is striped across all offered drives and all drives shall be able to contribute the IOs to all proposed controllers simultaneously. Justification: Four Controllers, 1 TB Cache and I/O striping to four controllers, are features that are available with only one OEM and hence restricts all the other OEMs from participation. Please note that requested performance and scalability can be easily met by dual active-active controllers, 768GB DRAM which is available with majority of storage OEMs. As per the TEC-GR for Storage Systems, Dual Controller Storage Systems are allowed. | Bidder to comply TS
84 | 17 |  | 20 | SAN (Storage Area Network) based storage or any other specialized storage solution: 23. Build in ransomware detection and protection | Change to: Ransomware/Anomaly protection Ransomware/anomaly detection and protection Justification: 1. Ransomware is only one type of cyber threat, while there can be other kind of anomalies as well. Hence request to kindly allow anomaly detection instead of Ransomware Detection which covers wider range of Anomalies / Cyber atatcks. 2. Each OEM has a different architecture. Some OEMs provide anomaly/ransomware detection using native tools on the storage system which does not have latest industry trends on cyber attacks. While some OEMs provide SaaS/cloud-based analysis for Anomaly detection, which is better since it provides protection against latest cyber threats in the industry. Hence request to kindly remove "inbuilt" word, for allowing wider OEM participation. | Bidder to comply TS
85 | 17 |  | 20 | SAN (Storage Area Network) based storage or any other specialized storage solution: 11. Fibre Channel, NVMe-oF/FC, NVMe-oF/TCP, and remote replication | Change To : Fibre Channel, NVMe-oF/FC, NVMe-oF/TCP, iSCSI, SMB, NFS and remote replication Justification: Major Storage protocols including iSCSI, SMB and NFS have been missed which could be a threat to investment protection of PGCIL. Request to kindly mention iSCSI, NFS and SMB protocols, otherwise PGCIL will have to procure additional storage system if the need for these protocols arise in future. | Bidder to comply TS
86 | 17 |  | 20 | SAN (Storage Area Network) based storage or any other specialized storage solution: CPU / Processor | Please Add: Proposed Storage must have atleast 64 x 2 Ghz or higher CPU Cores using redundant processors in each controller. Justification: While cache/ memory has been mention, but CPU has been missed. Please note that CPU Cores are a major driver of Storage Performance. Hence requesting to mention atleast 64 CPU cores with 768GB Cache/Memory to protect PGCIL's investments and to ensure that PGCIL does not get a sub-standard storage system. | Bidder to comply TS
87 | 17 |  | 20 | SAN (Storage Area Network) based storage or any other specialized storage solution: Additional Features | Please Add: Proposed Storage must have licenses for maximum storage capacity for Thin Provisioning, Inline Deduplication, Hardware Assisted Compression, Data at Rest Encryption, Application Consistent Snapshots (for major applications like VMware, MS SQL, Oracle, MS Exchange etc.), Thin Clones, Immutable snapshots, WORM (Write Once Read Many), Sync and Async Replication. If hardware Assisted Compression is not available, then 1.5 times of requested CPU and Cache resources must be provided. Data Reduction must be supported for both Block and File data types, with capability to show compressible/non-compressible capacity in Storage GUI. 1. Major Storage featues like Thin Provisioning, Inline Deduplication, compression, replication, data at rest encryption, snapshots, clones, WORM etc. Otherwise PGCIL shall up in procuring sub-standard storage system. | Bidder to comply TS
88 | 19 |  | 21 | Network Attached Storage (NAS): 3.Purpose Built Backup Appliance | Change suggested: Purpose built backup appliance/solution | Kindly Refer Amendment No III
89 | 19 |  | 21 | Network Attached Storage (NAS): 8.NFS, CIFS and VTL | Change suggested: NFS,CIFS/VTL, FC,iSCSI | Kindly Refer Amendment No III
90 | 19 |  | 21 | Network Attached Storage (NAS): 15. dual authorization for preventing disruptive operations so that hackers shall not be able to execute or complete all critical operations like deletion of backup store, changing system time etc. | Change suggested: dual authorization for preventing disruptive operations so that hackers shall not be able to execute or complete all critical operations like deletion of backup store, changing system time etc. Methods like WORM, immutable snapshots should be used. | Bidder to comply TS
91 | 19 |  | 21 | Network Attached Storage (NAS): Backup from SAN storage at Main Control center of NR-UNMS, NERUNMS, ER-UNMS, WR-UNMS and SR-UNMS must be kept at SAN of N-UNMS. | Query: As per the RFP, section 19. Network Attached Storage (NAS) on page-309, Purpose Built Backup Appliance has been envisaged for backups. However as per the mentioned specification under section 5.6, backup has been asked on SAN Storage. Please confirm the final destination for the Backups (SAN Storage or Purpose Built Backup Appliance)? | Kindly Refer Amendment No III
92 | 19 |  | 21 | Network Attached Storage (NAS): 4. 10 TB in RAID 6 | Change To: Please share how 10TB capacity appliance sizing is done? Please share the workload details & break up in below format (e.g. size & type of Database, HyperVisor type, size and number of VM & backup retention policies). Justification: Proposed backup appliance should be sized appropriately for the backup of xx TB of (File System, source data, mix of Databases, image backup of physical and VM etc.) and shall maintain following copies of data. a. Daily Incremental Backup – retained for 1 week b. Weekly Full Backup – retained for 2 weeks c. Monthly Full Backups – retained for 2 Months d. Yearly Full Backups - retained for 2 years | Kindly Refer Amendment No III
93 | 19 |  | 21 | Network Attached Storage (NAS): 11. 10TB /Hr | Query: Please share how much data to be backed up and what shall be the full backup window? | Kindly Refer Amendment No III
94 | 19 |  | 21 | Network Attached Storage (NAS): 8. Protocols NFS, CIFS and VTL | Requesting to make below change "Proposed backup appliance should be offered with protocols like OST, CIFS, NFS. Solution shall also support NDMP protocols. The protocols should be available to use concurrently with global / optimized deduplication for data ingested across all of them." Justification: CIFS and NFS protocol are not secure and can put data at risk if backup server is comproised. OST protocol is more secure compared to CIFS, NFS. OST is also important because it allows backup environments to maximize deduplication, automate data protection workflows, and reduce infrastructure complexity—leading to better performance, lower costs, and simplified management in enterprise data protection. | Kindly Refer Amendment No III
95 | 19 |  | 21 | Network Attached Storage (NAS): 10. De duplication : Source and target based | Requesting to make below change : Should support inline data duplication using automated variable block length deduplication technology and should support source and target based deduplication Justification: Inline deduplication : Inline deduplication is critical for maximizing storage and network efficiency, improving performance, enabling cost savings Variable Length Deduplication: Variable length deduplication detects more redundancy, leading to greater data reduction and more efficient use of disk space. Variable length deduplication provides superior storage efficiency and deduplication accuracy, especially for backup and data protection use cases where data is highly variable and frequently modified. | Kindly Refer Amendment No III
96 | 19 |  | 21 | Network Attached Storage (NAS): 12. Low bandwidth | Requesting to make below change " Must support Low bandwidth for deduplicated Replication of data over Local or Wide Area Networks. It should also support data encryption natively." Justification: For securing data, encrypted replication is necessary. | Bidder to comply TS
97 | 19 |  | 21 | Network Attached Storage (NAS): 13. 4 x 10Gb Ports | Requesting to make below change "The appliance should be offered with Min.4 x10 Gbps SFP+. If Fiber Ethernet ports are provided then SFPs to be supplied for all ports. The appliance should also have minimum 2 x 16 Gbps FC." To make a provision to backup hosts over FC, FC ports should be added. | Kindly Refer Amendment No III
98 | 19 |  | 21 | Network Attached Storage (NAS): 15. Dual authorization for preventing disruptive operations so that hackers shall not be able to execute or complete all critical operations like deletion of backup store, changing system time etc. | Requesting to make below change "dual authorization for preventing disruptive operations so that hackers shall not be able to execute or complete all critical operations like deletion of backup store and support against NTP time drift attacks and to protect the backup data till retention expires to help against ransomware attacks." From adding resiliency against ransomware and destructive malware, the system needs to be equipped with highest security controls. Therefore, requesting to make suggested change. | Bidder to comply TS
99 | 19 |  | 21 | Network Attached Storage (NAS): New Point | Requesting to add below point "The offered purpose-built backup appliance must have an inbuilt mechanism to defend the backup data against data integrity issues, it should also have a mechanism that check and validate the backup data residing on the appliance against any corruption without any human intervention." Its critical to ensure data ingrity of backup data stored on Storage system to leverage on reliable backup cppy in the event of recovery. Therefore, requesting to include this requirement. | Bidder to comply TS
100 | 19 |  | 21 | Network Attached Storage (NAS): New Point | Requesting to add below point "Replication should support bi-directional, many-to-one, one-to-many, and one-to-one replication." Supporting different replication methods are require in Enterise class Backup appliance. | Bidder to comply TS
101 | 19 |  | 21 | Network Attached Storage (NAS): New Point | Requesting to add below point "Proposed purpose-built backup appliance should support industry leading backup software like Networker, NetBackup, Commvault, NetVault and Data Protector, etc. and should support deduplication at backup server/ host / application level so that only changed blocks travel through network to backup device." Supporting different backup appliancations is require to avoid vendor lock-in situation. | Bidder to comply TS
102 | 19 |  | 21 | Network Attached Storage (NAS): New Point | Requesting to add below point "Proposed purpose-built backup appliance should support 256bit AES encryption for data at rest and data-in-flight during replication. It should offer internal and external key management for encryption." Supporting strong encryption method at rest and during replication is important to safeguard/secure backup data. | Kindly Refer Amendment No III
103 | 19 |  | 21 | Network Attached Storage (NAS): New Point | Requesting to add below point "Proposed backup appliance should be offered with battery backed up RAM /NVRAM for protection against data loss in power failure scenario and continuous automated file system check to ensure data integrity" This is require to protect backup & ensure data integrity against data loss in power failure scenario. | Kindly Refer Amendment No III
104 | 19 |  | 21 | Network Attached Storage (NAS): New Point | Proposed backup appliance should be sized appropriately for the backup of xx TB of (File System, source data, mix of Databases, image backup of physical and VM etc.) and shall maintain following copies of data. a. Daily Incremental Backup – retained for 1 week b. Weekly Full Backup – retained for 2 weeks c. Monthly Full Backups – retained for 2 Months d. Yearly Full Backups - retained for 2 years This is require for Appliance capacity sizing. As every vendor use different data redcution/deduplication technology, defining retention policy will help PGCIL to get adequate capacity and it will also make OEM/solution provider accountable for proposed capacity. | Kindly Refer Amendment No III
105 | 19 |  | 21 | Network Attached Storage (NAS): New Point | Requesting to add below point "The proposed solution must have the ability to reduce network bandwidth and source side compute overheads by only transferring the changed blocks to the backup target" This is require to achieve higher backup efficiency without overloading application or VM performance.This also helps to optimize local and WAN bandwidth needed for backup & replication respectively. | Bidder to comply TS
106 | 20 |  | 22 | Tape Library: SAS | As SAN Switch is already asked in RFP. Tape library can also be connected to SAN switch. Request to amend clase as "SAS or FC" | Kindly Refer Amendment No III
107 | 20 |  | 22 | Tape Library: 4. LTO-5 or Latest | Modification: Tape Libraries are getting obsolete. Hence kindly request for additional capacity either in Backup Appliance or in Archival (Object Storage) for backups instead of Tape Library for keeping long-term backup copies. (Section 3.8 Object Based Storage Details as per TEC-GR). Tape Libraries are getting obsolete due to the following reasons. Hence kindly request for same capacity in Archival (Object Storage) for backups instead of Tape Library. 1. Tape Corruptions. This may lead to penalties, data loss and reputational damage. 2. Higher RTO (time to restore). 3. Operational challenges due to handling, off-siting etc. 4. No way for the automated backup integrity check. 5. Only Compression (no deduplication). While Object Storages are capable of storing the backup copies in deduplicated and compressed format (that is higher Data Reduction ratios). 6. Challenges to migrate backup due to Tape Library generation changes. 7. Reputational damage due to Tape Corruptions and higher recovery times. | Bidder to comply TS
108 | 5.7 (14) | Section 5 | 12 | The proposed solution should support SMB / CIFS / NFS protocol for sharing and transferring files. | Requesting to remove point. | Bidder to comply TS
109 | 5.7 (15) | Section 5 | 12 | The solution should protect the endpoints against advanced threats including zero-day attacks, which target application vulnerabilities that have yet to be discovered or patched. | This can be covered with EDR, will the solution have internet connectivity via Proxy solution ? | Bidder to comply TS
110 | 5.7 (3) | Section 5 | 12 | The Solution must be capable of scanning files in seconds without transmitting any data to the cloud, ensuring fast and secure on-premises processing. | Modification: "The Solution must be capable of scanning network telemetry isng SPAN/NetFlow in seconds without transmitting any data to the cloud, ensuring fast and secure on-premises processing." Justification: Scanning of files is APT / Firewalls features. | Kindly Refer Amendment A
111 | 5.7 (8) | Section 5 | 12 | The proposed solution shall have the ability to stop the first malware download through inline blocking by integrating with the perimeter security solution such as NGFW itself (using API) | Modification: The proposed solution shall have the ability to stop the first malware download by integrating with solutions such as NGFW / Proxy / SOAR solution using Webhooks. Justification: NDR solution works OOB on NetFlow and SPAN traffic. Its not inline with the Firewall. Any traffic from N-S flow would first be checked on Firewalls and then Firewalls sends the Netflow to NDR solution. Can integrate with SOAR using Webhooks and using that it can intimate Firewalls. | Bidder to comply TS
112 | 5.7 (25) | Section 5 | 13 | Traffic Learning to be based full packet analysis | Solution works on NetFlow and SPAN basic and does not look into the payload of the traffic. Baselining is created based on the packet header information and with added AI/ML engine that is running. | Bidder to comply TS
113 | 5.5.3 |  | 10 | Router and firewall shall be provided with necessary license support till the completion of maintenance period. There shall be 50% spare ports | Change: Router and firewall shall be provided with necessary license support till the completion of maintenance period. Justification: Wider Participation | Kindly Refer Amendment A
114 | 2.9 |  | 37 | The email clients shall have features like email notification, Address books, user definable folders etc. | These features are part of MTA solution and not Email Security solution as the email management is done on the MTA | Bidder to comply TS
115 | 2.9 |  | 38 | The email solution should support sandboxing integration to protect zero-day malware & APT. | Is this an ask to provide sandboxing solution or Email should integrate with Any Sandboxing solution ? | It should integrate with sandboxing solution provided as a part of this project.
116 | 1 |  | 3 | 7. 480 GB NVMe (min Gen 4) delivered expandable up to 1TB | Modification:2x 960 GB NVMe (min Gen 4) hot swappable drives Justification:Every OEM architecture is different, Cisco does not support 480 gb nvme drives. Kindly change for wider participation | Bidder to comply TS
117 | 1 |  | 3 | 11. Server should support min. six PCI-Express 5.0 x16 slots | Modification:Server should support min. 4 PCI-Express 5.0 x16 slots Justification:Every OEM architecture is differen. Kindly change for wider participation | Kindly Refer Amendment A
118 | 1 |  | 4 | 14. Dual AC Power Supply | Modification:Hot pluggable Dual AC Power Supply Justification:For better operational cabability kindly modify the clause. | Bidder to comply TS
119 | 2 |  | 5 | 7. 480 GB NVMe (min Gen 4) delivered expandable up to 1TB | Modification:2x 960 GB NVMe (min Gen 4) hot swappable drives Justification:Every OEM architecture is different, Cisco does not support 480 gb nvme drives. Kindly change for wider participation | Bidder to comply TS (RAID 1)
120 | 2 |  | 5 | 10. Server should support min. six PCI-Express 5.0 x16 slots | Modification:Server should support min. 4 PCI-Express 5.0 x16 slots Justification:Every OEM architecture is differen. Kindly change for wider participation | Kindly Refer Amendment A
121 | 2 |  | 6 | 14. Dual AC Power Supply | Modification:Hot pluggable Dual AC Power Supply Justification:For better operational cabability kindly modify the clause. | Bidder to comply TS
122 | Volume 2_Technical Specifications Scope Of work | 1.6 | 1.6 | Auditing of Cyber Security implementation by CERT-In listed Auditors during AMC from the party finalized by Employer. | a) While employer will finalize the party, please confirm that the payment for such audits would be borne by Employer. b) Please confirm number of Audits and number of days required on yearly basis. | Item is available in the BOQ. Bidder to quote as per BPS.
123 | Volume 2_Technical Specifications Teaming Agreement of bidder with OEM | 1.8.1 | 1.8.1 | OEM(s) shall provide required skill sets to the Contractor to enable them to execute the project deliverables (Network/ System Design, Deployment (I & C), Testing, Operational Support, Future network Augmentation, New Service Deployment for customers & Contingencies situations) | a) Please confirm that if Bidder has necessary skills, still he needs to include OEM Efforts ? B) If yes, please confirm the exact deliverables from OEM so that there is no disconnect between bidders. | Bidder to Comply TS
124 | Volume 2_Technical Specifications Teaming Agreement of bidder with OEM | 1.8.1 | 1.8.1 | A minimum number of SME(s) shall be made available for entire implementation duration till Take over by Employer/Owner. The same shall be covered contractually between Contractor & OEM(s). | Please confirm the deliverables expectation from OEMs and mandays of effort envisaged so that bidder can contract with OEM and accordingly come up with commercials. | Bidder to Comply TS
125 | Volume 2_Technical Specifications Contractor’s Responsibilities and Obligations | 1.9.2 | 1.9.2 | Contractor has to do necessary co-ordination with existing UNMS Contractor for installation, commissioning an integrating EDR, NDR and Data diodes at existing UNMS control center without any additional cost to the employer. | Please clarify that any cost on the part of existing UNMS Contractor, to make any changes at their end, will be borne by them. | Necessary Commercial and technical Tie-up to be taken up by the N-UNMS Contractor. Bidder to Comply TS
126 | Volume 2_Technical Specifications Contractor’s Responsibilities and Obligations | 1.9.2 | 1.9.2 | Provide a Quality Assurance Plan and access to the manufacturing process. | Please clarify what access is expected to the manufacturing process. | Bidder to Comply TS
127 | Volume 2_Technical Specifications Contractor’s Responsibilities and Obligations | 1.9.2 | 1.9.2 | Training of the Employer/owner’s personnel | Please clarify the training requirements : a) Is training required onsite or online? | Physical Classroom training at any specified location. Bidder to Comply TS
128 | Volume 2_Technical Specifications Service Levels | 3.4.9 | 3.4.9 | Sev 1 Problem Resolution in 2 Hours. | 2 Hours resolution time is very aggressive, request for change to at least 4 Hours. | Bidder to Comply TS
129 | Volume 2_Technical Specifications Penalty Clause | 3.4.9.3 | 3.4.9.3 | Deduction of 2% of the apportioned price of the apportioned quarterly AMC for every 0.5% or part there of decrease in availability under 99.9%. (Maximum amount of deduction is limited to 100% of AMC charges) | Penalty cap is very high / stringent, request that ths be brought down considerably to below 15% | Kindly Refer Amendment No III
130 | Volume 2_Technical Specifications .Design Requirements for N-UNMS Applications | 2.2 | 2.2 | The N-UNMS system application shall have capability of integration with Regional UNMS of Multiple Vendors. N-UNMS system shall ensure seamless operation & management of Communication network viz. Configuration Planning, fault Management, Inventory management, Performance monitoring etc. | Please share the details of Regional UNMS of various vendors including interface details. | Details are provided in the Technical Specification. Bidder to Comply TS
131 | Volume 2_Technical Specifications General |  |  |  | Please clarify if bidder can provide hybrid Delivery model i.e combination of onsite (for L1 support) and remote delivery from bidder shared Delivery Centre (for L2/L3 support). | Bidder to comply TS, Remote access not allowed.
132 | Volume 2_Technical Specifications General |  |  |  | Can the bidder leverage shared AIOPS platform for central view of parameters ? | Bidder to Comply TS
133 | VOLUME II, APPENDIX D, S No 14 (Anti-APT) - Page 17 of 25 |  |  | Anti APT/Sandboxing must be supplied for all firewalls installed at main and Backup Control Center | Request deletion of this clause | Bidder to Comply TS
134 | VOLUME II, PART- B, SECTION-4, S No 4.5.3 (Network based Intrusion Prevention System - NIPS) - Page 9 of 15 |  |  | Not Applicable | Request to add following technical specifications: • The IPS solution must be a purpose-built dedicated appliance not a subset of a firewall or UTM appliance. Its firmware should be dedicated firmware and should not be the same or shared with any other blades i:e: Firewall, DDoS, UTM Etc. The solution should also not use the same firmware/underlying OS for NGFW and IPS offerings. • IPS should offer latency of less 60 microseconds with IMIX(internet mix) traffic and information should be publicly documented and available • The Proposed solution must have more than 20,000 IPS signatures and it also support to import SNORT signatures • The offered I/O modules must have a power failure bypass capability which allows traffic to bypass in the event of appliance hardware failure and in an event wherein I/O modules get unplugged out of IPS box during the RMA procedure. • The solution shall consist of OEM's own threat intelligence and is not dependent only on information available in the public domain. • The IPS Device should provide Zero-Day attack protection automatically without human intervention and should be contributing at least 30 zero-day vulnerabilities to Microsoft/Linux continuously for the past 5 years. Report Validation from a third party or Microsoft or Linux on their website • The proposed solution should be able to integrate with the VA scanners like Tenable, Qualys, etc to fine-tune the IPS policies to shield against the vulnerabilities and related attacks | Bidder to Comply TS
135 | VOLUME II, PART- B, SECTION-2, S No 2.6 (IT Setup) - Page 2 of 53 |  |  | Not Applicable | Request to add HIPS (Host Intrusion Prevention System) component with relevant technical specifications in this section. | Kindly refer Amendment No III
136 | VOL-II Appendix Appendix-D Page13 of 25 10. Firewall Features/Characteristics required of External Firewall: |  | 16 | DoS & DDoS prevention | We request department to change modify the clause "DoS/DDoS prevention" | Bidder to Comply TS
137 | VOL-II Appendix Appendix-D Page13 of 25 10. Firewall Features/Characteristics required of External Firewall: |  | 24 | Antivirus, Anti-worm, anti-spam and anti-spyware protection | We request department to change modify the clause "Antivirus, Anti-worm/anti-spam and anti-spyware protection" | Bidder to Comply TS
138 | VOL-II Appendix Appendix-D Page13 of 25 10. Firewall Features/Characteristics required of External Firewall: |  | 33 | Prevention of Dodos & Dos-added | We request department to change modify the cluase as "Prevention of Dodos or Dos-added" | Bidder to Comply TS
139 | VOL-II Appendix Appendix-D Page13 of 25 10. Firewall Features/Characteristics required of External Firewall: |  | 4 | 10 million for Type-I (20 GBPS Threat prevention throughput Firewall) and for Type-II (any other external Firewall)- 1Million | We request to change modify the cluase "10 million for Type-I (20 GBPS Threat prevention throughput Firewall) and for Type-II (any other external Firewall)- 1 million L4 or 900k L7 | Bidder to Comply TS
140 | VOL-II Appendix Appendix-D Page13 of 25 10. Firewall Features/Characteristics required of External Firewall: |  | 7 | Minimum 3DES/AES VPN throughput/20 Gbps for Type-I (20 GBPS Threat prevention throughput Firewall) and for Type-II (any other external Firewall)- 4.5 GBPS | We request to change modify the cluase "20 Gbps for Type-I (20 GBPS Threat prevention throughput Firewall) and for Type-II (any other external Firewall)- 4 GBPS" | Bidder to Comply TS
141 | VOL-II Appendix Appendix-D Page13 of 25 10. Firewall Features/Characteristics required of External Firewall: |  | 15 | 5 DoS & DDoS prevention | We request to change modify the clause as "DoS / DDoS prevention" | Bidder to Comply TS
142 | VOL-II Appendix Appendix-D Page13 of 25 10. Firewall Features/Characteristics required of External Firewall: |  | 4 | Minimum number of concurrent sessions 1 Million | We request to change modify the clause as " Minimum number of concurrent sessions 1 Million Layer4 or 900K Layer 7 Concurrent sessions | Bidder to Comply TS
143 | VOL-II Appendix Appendix-D Page13 of 25 10. Firewall Features/Characteristics required of External Firewall: |  | 20 | 1.TEC GR no. GR/FWS-01/02 SEP 2006 for Firewall | We request department to change modify the clause as " TEC GR no. GR/FWS-01/02 SEP 2006/NDPP/NDCPP for Firewall | Bidder to Comply TS
144 | Volume II_Technical Specifications: Under Workstation consoles with dual/ single monitor: Interfaces Ports |  | 295 | HDMI Ports | Kindly amend HDMI post as HDMI/DP | Kindly refer Amendment No III
145 | Volume II_Technical Specifications: Under 4. Remote console: |  | 295 | HDMI Ports | Kindly amend HDMI post as HDMI/DP | Kindly refer Amendment No III
146 | Volume II_Technical Specifications: Under Processor Terminal (Laptop): |  | 297 |  | Country of Origin of the product meeting the compliance shall be China. Is it acceptable? | Country of Origin shall be as per GOI Policy and Guidelines.
147 | Volume II_Technical Specifications: Under Processor Terminal (Laptop): Processor |  | 297 | Min 8 Core, base freq 2.0 GHz | Min Performance Cores available in the latest gen mobile processors are 6 & Efficient Cores is 8. both put together is 16 Cores. Is this accaptable? | Minimum Number of cores mentioned in the technical specification for Servers, Workstations and remote console must be performance cores.
148 | Volume II_Technical Specifications: Under 1. Servers 5. No. of CPUs & Cores and Processor Clock frequency |  | 291 | Min 16 core, Base Frequency 2.4 GHz 5th gen or higher | Kindly change to: 2 x Min 16 core, Base Frequency 2.4 GHz 5th gen or higher | Kindly refer Amendment No III
149 | Volume II_Technical Specifications: Under 1. Servers 11. PCIe Slots |  | 291 | Server should support min. six PCI-Express 5.0 x16 slots | Kindly change to: Server should support min. six PCI-Express x16 slots(with minimum 2 x Gen 5.0 slots) | Bidder to Comply TS
150 | Volume II_Technical Specifications: Under 2. Servers 5. No. of CPUs & Cores and Processor Clock frequency |  | 293 | Min 16 core, Base Frequency 2.4 GHz 5th gen or higher | Kindly change to: 2 x Min 16 core, Base Frequency 2.4 GHz 5th gen or higher | Kindly refer Amendment No III
151 | Volume II_Technical Specifications: Under 2. Servers 10. PCIe Slots |  | 293 | Server should support min. six PCI-Express 5.0 x16 slots | Kindly change to: Server should support min. six PCI-Express x16 slots(with minimum 2 x Gen 5.0 slots) | Bidder to Comply TS
152 | Volume II_Technical Section: 1.13 Applicable Standards |  | 22 | 18. TEC GR No: TEC GR No TEC/GR/I/ESI-001/03/MAR12 for Mid-Tier Storage | Change To: TEC/GR/IT/DSI-001/04/DEC 2015 for Mid-Tier Storage. Query: As per the RFP page-308 section- "5.6 Storage Area Network (SAN) based Storage", All-Flash NVME storage has been envisaged. While the TEC-GR specification has been mentioned for Mid-Range Hybrid Storage. Kindly suggest if TEC-GR for Mid-Range Storage (section 3.5) needs to be considered, or if the "TEC GR for All Flash Arrays (Section 3.2)" to be considered? | TEC-GR for All flash System mentioned in TEC-GR no TEC/GR/I/ESI-001/03/MAR12 or any latest revision, need to be considered. The clause is mentioned in the Technical specification " Specifications and codes shall be the latest version, inclusive of revisions, which are in force". Bidder to Comply TS
153 | Volume II_Technical Section: 5.6 Storage Area Network (SAN) based Storage |  | 170 | The SAN to be supplied at N-UNMS must have inbuilt ransomware detection and protection. | Modification: The SAN to be supplied at N-UNMS must have ransomware/Anomaly detection and protection. | Bidder to Comply TS
154 | Volume II_Technical Section: 17. SAN (Storage Area Network) based storage or any other specialized storage solution |  | 308 | Solid State Drive - All NVMe System (min Gen 4 ) | Change To: All NVMe System (min TLC/MLC Grade ) | Bidder to Comply TS
155 | Volume II_Technical Section: 17. SAN (Storage Area Network) based storage or any other specialized storage solution |  | 308 | Cache / Memory - 1 TB (Total) | Change To: 768GB (Total) | Bidder to Comply TS
156 | Volume II_Technical Section: 17. SAN (Storage Area Network) based storage or any other specialized storage solution |  | 308 | Controller Four Active – Active Controller to be provided. Every logical disk is striped across all offered drives and all drives shall be able to contribute the IOs to all four controllers simultaneously. | Change To: Two Active – Active Controller to be provided. Every logical disk is striped across all offered drives and all drives shall be able to contribute the IOs to all proposed controllers simultaneously. | Bidder to Comply TS
157 | Volume II_Technical Section: 17. SAN (Storage Area Network) based storage or any other specialized storage solution |  | 308 | 23. Ransomware protection Built in ransomware detection and protection | Change to: Ransomware/Anomaly protection Ransomware/anomaly detection and protection | Kindly refer Amendment No III
158 | Volume II_Technical Section: 17. SAN (Storage Area Network) based storage or any other specialized storage solution |  | 308 | Protocol Support : Fibre Channel, NVMe-oF/FC, NVMe-oF/TCP, and remote replication | Change To : Fibre Channel, NVMe-oF/FC, NVMe-oF/TCP, iSCSI, SMB, NFS and remote replication | Kindly refer Amendment No III
159 | Volume II_Technical Section: 17. SAN (Storage Area Network) based storage or any other specialized storage solution |  | 308 | CPU / Processor | Please Add: Proposed Storage must have atleast 64 x 2 Ghz or higher CPU Cores using redundant processors in each controller. | Bidder to Comply TS
160 | Volume II_Technical Section: 17. SAN (Storage Area Network) based storage or any other specialized storage solution |  | 308 | Additional Features | Please Add: Proposed Storage must have licenses for maximum storage capacity for Thin Provisioning, Inline Deduplication, Hardware Assisted Compression, Data at Rest Encryption, Application Consistent Snapshots (for major applications like VMware, MS SQL, Oracle, MS Exchange etc.), Thin Clones, Immutable snapshots, WORM (Write Once Read Many), Sync and Async Replication. If hardware Assisted Compression is not available, then 1.5 times of requested CPU and Cache resources must be provided. Data Reduction must be supported for both Block and File data types, with capability to show compressible/non-compressible capacity in Storage GUI. | Bidder to Comply TS
161 | Volume II_Technical Section 5.6 Storage Area Network (SAN) based Storage |  | 170 | Backup from SAN storage at Main Control center of NR-UNMS, NERUNMS, ER-UNMS, WR-UNMS and SR-UNMS must be kept at SAN of N-UNMS. | Query: As per the RFP, section 19. Network Attached Storage (NAS) on page-309, Purpose Built Backup Appliance has been envisaged for backups. However as per the mentioned specification under section 5.6, backup has been asked on SAN Storage. Please confirm the final destination for the Backups (SAN Storage or Purpose Built Backup Appliance)? | Kindly refer Amendment No III
162 | Volume II_Technical Section 20. Tape Library |  | 310 | LTO5 or latest tape library | Modification: Tape Libraries are getting obsolete. Hence kindly request for additional capacity either in Backup Appliance or in Archival (Object Storage) for backups instead of Tape Library for keeping long-term backup copies. (Section 3.8 Object Based Storage Details as per TEC-GR). | Bidder to Comply TS
163 | Volume II_Technical Specifications Section: 19. Network Attached Storage Specification No. 4: Capacity |  | 309 | Capacity: 10 TB in RAID 6 | Change To: Please share how 10TB capacity appliance sizing is done? Please share the workload details & break up in below format (e.g. size & type of Database, HyperVisor type, size and number of VM & backup retention policies). Proposed backup appliance should be sized appropriately for the backup of xx TB of (File System, source data, mix of Databases, image backup of physical and VM etc.) and shall maintain following copies of data. a. Daily Incremental Backup – retained for 1 week b. Weekly Full Backup – retained for 2 weeks c. Monthly Full Backups – retained for 2 Months d. Yearly Full Backups - retained for 2 years | Kindly refer Amendment No III
164 | Volume II_Technical Section: 19. Network Attached Storage Specification No. 11 |  | 309 | 11. 10TB /Hr | Query: Please share how much data to be backed up and what shall be the full backup window? | Kindly refer Amendment No III
165 | Volume II_Technical Specifications Section: 19. Network Attached Storage Specification No. 8: Protocols |  | 309 | 8. Protocols NFS, CIFS and VTL | Requesting to make below change "Proposed backup appliance should be offered with protocols like OST, CIFS, NFS. Solution shall also support NDMP protocols. The protocols should be available to use concurrently with global / optimized deduplication for data ingested across all of them." | Kindly refer Amendment No III
166 | Volume II_Technical Specifications 19: Networker Attached Storage |  | 309 | 10. De duplication : Source and target based | Requesting to make below change : Should support inline data duplication using automated variable block length deduplication technology and should support source and target based deduplication | Kindly refer Amendment No III
167 | Volume II_Technical Specifications Section: 19. Network Attached Storage Specification No. 12: Replication |  | 309 | Low bandwidth | Requesting to make below change " Must support Low bandwidth for deduplicated Replication of data over Local or Wide Area Networks. It should also support data encryption natively." | Kindly refer Amendment No III
168 | Volume II_Technical Specifications Section: 19. Network Attached Storage Specification No. 13: Port |  | 309 | 4 x 10Gb Ports | Requesting to make below change "The appliance should be offered with Min.4 x10 Gbps SFP+. If Fiber Ethernet ports are provided then SFPs to be supplied for all ports. The appliance should also have minimum 2 x 16 Gbps FC." | Kindly refer Amendment No III
169 | Volume II_Technical Specifications Section: 19. Network Attached Storage Specification No. 15: Security |  | 309 | Dual authorization for preventing disruptive operations so that hackers shall not be able to execute or complete all critical operations like deletion of backup store, changing system time etc. | Requesting to make below change "dual authorization for preventing disruptive operations so that hackers shall not be able to execute or complete all critical operations like deletion of backup store and support against NTP time drift attacks and to protect the backup data till retention expires to help against ransomware attacks." | Bidder to Comply TS
170 | 1.4.1 Configuration of the ISR System at Main and Backup Control Centres |  | 71 | Software utilities shall be provided in the ISR System to back-up the Historian data to an auxiliary memory (e.g. SAN System) available on network. This software shall have the feature of automatic as well as the manual backup of data. | Query: It is mentioned that backup to an SAN systems. Where as Technical specifcation has requested for NAS/Purpose built backup appliance. Please clarify. | Backup shall be kept at SAN/NAS/Backup Appliance. Details shall be finalized during detailed engineering. Bidder to Comply TS
171 | 2.8 Virtualization - Data Protection |  | 111 | 1. The offered Hyper-visor Shall have in-built data backup solution which shall be able to protect VM and Hosts to Target Storage provider. 2. Native backup engine shall be able to use at least CIFS, NFS, S3 from Storage providers as a backup target. 3. In case vendor Hypervisor doesn’t have in-built data backup solution then vendor shall provide additional backup software for the complete hardware and software configuration asked in the Technical Specification. 4. The offered integrated backup software shall be deeply integrated into the instances / VM provisioning window so that all newly created instances / VMs are protected and backed up automatically. 5. The offered integrated backup software shall support critical features like Scheduling of backup, backup retention counts, on-demand backup etc. | As project involves data protection from VM's running on Hyper-Visor and other systems that comprises of files systems, applications and databases, configuration of the ISR systems at Main and BCC, using single/ centralized backup software to protect all these virtual, physical instances is more appropriate from management perspective. So we request to request to bidder to propose proper backup software.Refer backup software specifications in attached sheet. | Bidder to Comply TS
172 | Volume II_Technical Specifications Section: 19. Network Attached Storage |  | 309 | New Point | Requesting to add below point "The offered purpose-built backup appliance must have an inbuilt mechanism to defend the backup data against data integrity issues, it should also have a mechanism that check and validate the backup data residing on the appliance against any corruption without any human intervention." | Bidder to Comply TS
173 | Volume II_Technical Specifications Section: 19. Network Attached Storage |  | 309 | New Point | Requesting to add below point "Replication should support bi-directional, many-to-one, one-to-many, and one-to-one replication." | Bidder to Comply TS
174 | Volume II_Technical Specifications Section: 19. Network Attached Storage |  | 309 | New Point | Requesting to add below point "Proposed purpose-built backup appliance should support industry leading backup software like Networker, NetBackup, Commvault, NetVault and Data Protector, etc. and should support deduplication at backup server/ host / application level so that only changed blocks travel through network to backup device." | Bidder to Comply TS
175 | Volume II_Technical Specifications Section: 19. Network Attached Storage |  | 309 | New Point | Requesting to add below point "Proposed purpose-built backup appliance should support 256bit AES encryption for data at rest and data-in-flight during replication. It should offer internal and external key management for encryption." | Kindly refer Amendment No III
176 | Volume II_Technical Specifications Section: 19. Network Attached Storage |  | 309 | New Point | Requesting to add below point "Proposed backup appliance should be offered with battery backed up RAM /NVRAM for protection against data loss in power failure scenario and continuous automated file system check to ensure data integrity" | Kindly refer Amendment No III
177 | Volume II_Technical Specifications Section: 19. Network Attached Storage |  | 309 | New Point | Proposed backup appliance should be sized appropriately for the backup of xx TB of (File System, source data, mix of Databases, image backup of physical and VM etc.) and shall maintain following copies of data. a. Daily Incremental Backup – retained for 1 week b. Weekly Full Backup – retained for 2 weeks c. Monthly Full Backups – retained for 2 Months d. Yearly Full Backups - retained for 2 years | Kindly refer Amendment No III
178 | Volume II_Technical Specifications Section: 19. Network Attached Storage |  | 309 | New Point | Requesting to add below point "The proposed solution must have the ability to reduce network bandwidth and source side compute overheads by only transferring the changed blocks to the backup target" | Bidder to Comply TS
179 | Volume II_Technical Specifications 5.6 Storage Area Network (SAN) based Storage |  | 170 | Backup from SAN storage at Main Control center of NR-UNMS, NERUNMS, ER-UNMS, WR-UNMS and SR-UNMS must be kept at SAN of N-UNMS. Any additional Software/hardware required for taking backup of existing UNMSs system to SAN at National UNMS system must be supplied by contractor without any additional cost to employer. | Query: Does this refers to replicating data from SAN storage at Main Control center of NR-UNMS, NERUNMS, ER-UNMS, WR-UNMS and SR-UNMS to SAN at N-UNMS or does this mean taking backup of data on SAN at NR-UNMS, NERUNMS, ER-UNMS, WR-UNMS and SR-UNMS and replicate it to SAN storage at N-UNMS. | Bidder to Comply TS
180 | Volume II_Technical Specifications Section: 16. LAN Switch |  | 307 | 10 Gbps Fibre Optic Ports for Connecting dual Fibre Optic LAN Minimum 8x10 Gbps Fibre Optic Ports and 16x1 Gbps Ethernet ports at main and backup control centre Minimum 4x10 Gbps Fibre Optic Ports and 8x1 Gbps Ethernet ports at remaining location | Change to: 10 Gbps Fibre Optic Ports for Connecting dual Fibre Optic LAN Minimum 2x 100G ports for MC-LAG/VPC/MLAG setup, 8x10 Gbps Fibre Optic Ports and 16x1 Gbps Ethernet ports at main and backup control centre Minimum 2x 100G ports for MC-LAG/VPC/MLAG, 4x10 Gbps Fibre Optic Ports and 8x1 Gbps Ethernet ports at remaining location | Bidder to Comply TS
181 | Volume II_Technical Specifications Section: 16. LAN Switch |  | 307 | New Point | All switches should have a minimum support for 200K MAC addresses, 160K IPv4 routes and 64K IPv6 routes | Bidder to Comply TS
182 | Volume II_Technical Specifications Section: 16. LAN Switch |  | 307 | New Point | All switches must be ONIE (Open Network Install Environment) capable, which allows for disaggregation of hardware and software to allow third-party network OS to be installed on the switch | Bidder to Comply TS
183 | Volume II_Technical Specifications 1.13 Applicable Standards |  | 22 | TEC-GR No: GR/LSW-01/04 MAR-11 for LAN Switches | Modification: Request to kindly remove this clause | Bidder to Comply TS
184 | 19 | 2.6.3 EDR |  | The proposed solution should block malicious traffic from data exfiltration (data leakage) | Requesting to remove | Bidder to comply TS
185 | 23 | 2.6.3 EDR |  | The solutions should support the Automated False Positive Reclassifications to Ability to automatically reclassify activity as false positives and prevent similar detections from occurring. | The solutions should have the ability reclassify False Positive and prevent similar detections from occurring. | Bidder to comply TS
186 | 25 | 2.6.3 EDR |  | The proposed solution should have the ability to create Whitelist/Blacklist for the files based on their names, location (File Path), version, and provider | The proposed solution should have the ability to create Whitelist/Blacklist for the files based on their names, location (File Path). | Bidder to comply TS
187 | 27 | 2.6.3 EDR |  | Solution shall have the ability to restore encrypted files to their previous unencrypted state on detection of ransomware based on behavior | Requesting to remove this point | Bidder to comply TS
188 | 3 | 5.7 Network Detection and Response (NDR) |  | The Solution must be capable of scanning files in seconds without transmitting any data to the cloud, ensuring fast and secure on-premises processing. | "The Solution must be capable of scanning network telemetry isng SPAN/NetFlow in seconds without transmitting any data to the cloud, ensuring fast and secure on-premises processing." | Kindly refer Amendment No III
189 | 8 | 5.7 Network Detection and Response (NDR) |  | The proposed solution shall have the ability to stop the first malware download through inline blocking by integrating with the perimeter security solution such as NGFW itself. (using API) | The proposed solution shall have the ability to stop the first malware download by integrating with solutions such as NGFW / Proxy / SOAR solution using Webhooks. | Bidder to comply TS
190 | 14 | 5.7 Network Detection and Response (NDR) |  | The proposed solution should support SMB / CIFS / NFS protocol for sharing and transferring files. | Requesting to remove this point | Bidder to comply TS
191 | 15 | 5.7 Network Detection and Response (NDR) |  | The solution should protect the endpoints against advanced threats including zero-day attacks, which target application vulnerabilities that have yet to be discovered or patched. |  | Bidder to comply TS
192 | 25 | 5.7 Network Detection and Response (NDR) |  | Traffic Learning to be based full packet analysis | Requesting to remove this point | Bidder to comply TS
193 | VOL-II PART-B Sec-2, Page 38 | 2.9. Email Server |  | The email solution should support sandboxing integration to protect zero-day malware & APT. |  | The ESS Solution should integrated with sandbox solution supplied under this project.
194 | VOL-II PART-B Sec-2, Page 37 | 2.9. Email Server |  | The email clients shall have features like email notification, Address books, user definable folders etc. |  | Bidder to comply TS
195 | 12. Interface support (IPV4 and IPV6 –Compliant) | 15. Router ( WAN Router Cum Firewall) |  | Router should support 1 GB, 10 GB Minimum 16 no. - 1 GB Ethernet ports, 8x10 Gbps Fibre optic ports At main and Backup Control Centre | Router should support 1 GB, 10 GB Minimum 16 no. - 1 GB Ethernet ports, 5x10 Gbps Fibre optic ports At main and Backup Control Centre | Bidder to comply TS
196 | 5.5.3 WAN Routers | PART- B SECTION-5 N-UNMS HARDWARE SPECIFICATIONS |  | Router and firewall shall be provided with necessary license support till the completion of maintenance period. There shall be 50% spare ports | Request to kindly remove this clause | Kindly refer Amendment No III
197 |  | 16. LAN Switch |  | Switch should redundant hot swappable power supply and redundant Fans |  | Kindly refer Amendment No III
198 |  | 16. LAN Switch |  | Switch should support MacSec ( 802.1ae) to ensure encryption of layer 2 traffic from Day 1 |  | Bidder to comply TS
199 |  | 16. LAN Switch |  | Switch should be Ipv6 logo certified from Day1 |  | Bidder to comply TS
200 | 7. Internal Auxiliary memory | Servers for Network Resource Management, Design, Activation, Configuration Planning |  | 480 GB NVMe (min Gen 4) delivered expandable up to 1TB | 2x 960 GB NVMe (min Gen 4) hot swappable drives | Bidder to comply TS
201 | 11. PCIe Slots | Servers for Network Resource Management, Design, Activation, Configuration Planning |  | Server should support min. six PCI-Express 5.0 x16 slots | Server should support min. 4 PCI-Express 5.0 x16 slots | Kindly refer Amendment No III
202 | 14. Power Supply (Watts) | Servers for Network Resource Management, Design, Activation, Configuration Planning |  | Dual AC Power Supply | Hot pluggable Dual AC Power Supply | Bidder to comply TS
203 | 7. Internal Auxiliary memory | Servers for Configuration Management Cum CMC, Identity & Patch Management |  | 480 GB NVMe (min Gen 4) delivered expandable up to 1TB | 2x 960 GB NVMe (min Gen 4) hot swappable drives | Bidder to comply TS
204 | 11. PCIe Slots | Servers for Configuration Management Cum CMC, Identity & Patch Management |  | Server should support min. six PCI-Express 5.0 x16 slots | Server should support min. 4 PCI-Express 5.0 x16 slots | Kindly refer Amendment No III
205 | 14. Power Supply (Watts) | Servers for Configuration Management Cum CMC, Identity & Patch Management |  | Dual AC Power Supply | Hot pluggable Dual AC Power Supply | Bidder to comply TS
206 |  | 13. Sizing Parameters Internal Firewall/UTM: |  | The proposed hardware should have dual redunant hotswappable Power supply |  | Kindly refer Amendment No III
207 |  | 13. Sizing Parameters Internal Firewall/UTM: |  | The proposed hardware should have dual redunant Fan Module |  | Kindly refer Amendment No III
208 |  | 13. Sizing Parameters Internal Firewall/UTM: |  | The proposed hardware should have local storage of logs upto 900 Gb |  | Bidder to comply TS
209 |  | 13. Sizing Parameters Internal Firewall/UTM: |  | The proposed solution should have minimum 32Gb of RAM |  | Bidder to comply TS
210 | 1.6 Scope of Work | VOL-II PART-A Sec - 1 | 8 | c) Supply and Installation of clients for accessing Cloud Based Ticketing and Outage Management at CEA, CTUIL, NLDC, RLDCs, SLDCs, and RPCs including hardware & software for workstation. | We understand that the Ticketing and Outage Management Tool will be operated separately from the N-UNMS. As the requirement is for a Cloud based Ticketing Solution, licensing will be SAAS / Subscription model. Kindly confirm / clarify our understanding. | Bidder need to provide both the solution. On-premise Ticketing module and Cloud based outage management and ticketing Solution. Bidder to Comply TS
211 | 1.6 Scope of Work | VOL-II PART-A Sec - 1 | 9 | t) Contractor shall supply necessary interface (Hardware and software) for sniffing/tapping the existing UNMS for parallel operation of new system with existing system. | Please elaborate on this point, we need more details to understand the requirement. | Integration with existing UNMS system is separate line item , Bidder need to connect with Regional UNMS in with all security compliances as per project requirement as a whole
212 | 8.1. Cloud Based ticketing Portal and outage Management (CBTOM) | VOL-II PART B Sec - 8 | 36 | s) The proposed ticketing system vendor should be certified with at least below standards and compliances: a. ISO 27001, ISO/IEC 27017:2015, ISO 27018 b. SOC 1 & SOC 2 c. Empaneled with the Ministry of Electronics & Information Technology (MEITY) or equivalent cloud services in Government/enterprise settings. | We understand that the ISO 27017, ISO 27018 certifications and MEITY empannelment are required from to the Cloud Service Provider and Ticketing tool vendor should be Iso27001 and SOC2 certified. Kindly confirm / clarify our understanding. | Kindly Refer Amendment No III
213 | 18 | VOL-II PART-A Section 1, pg 18 |  | 18. TEC GR No: TEC GR No TEC/GR/I/ESI-001/03/MAR12 for Mid-Tier Storage. | As PGCIL is looking for All NVMe storage. Some of the point of TEC GR may not be applicable to NVMe storage as TEC GR was made 10+ year back. We understand DRS requirement is final and supersede TEC GR. Kindly confirm. | The clause is mentioned in the Technical specification " Specifications and codes shall be the latest version, inclusive of revisions, which are in force". Bidder to Comply TS
214 | 11 | 1. Server Type 1 DRS 2. Server Type 2 DRS | VOL-II Appendix | Server should support min. six PCI-Express 5.0 x16 slots | 5th Gen server offer high bandwidth PCIe 5.0 slots. To get maximum benefit of Gen 5 server Request to modify clause as "Server should support min. Eight PCI-Express 5.0 x16 slots and should be configured with min. six PCI-Express 5.0 x16 slots" | Bidder to Comply TS
215 | 12 | 1. Server Type 1 DRS 2. Server Type 2 DRS | VOL-II Appendix |  Secure Recovery - recover critical firmware to known good state on detection of compromised firmware  Security Dashboard for Server to detect possible security vulnerabilities.  Should help to proactively identify out-of- date BIOS, drivers, and Server Management agents and enable the remote update of system software/firmware components.  Offered server should be listed on spec.org  It should support historical reporting and should have support for multifactor authentication | To reduce exposure to vlunerabilities system should have validation mechanism in run time as well. Also many time system expose to vunerability due to manual process of firmware updates and all system are not at the same baseline firmware level. To strengthen server security, request to add following clause: " For firmware security, system should support remote management chip creating a fingerprint in the silicon, preventing servers from booting up unless the firmware matches the fingerprint. This feature should be immutable. Should have encrypted virtual media Should maintain repository for firmware and drivers recipes to aid rollback or patching of compromised firmware. Should also store Factory Recovery recipe preloaded to rollback to factory tested secured firmware Should have dashboard for firmware baselines while performing minimum required firmware checks and highlighting out-of-compliance devices for updates with the selected firmware baseline Server should have runtime firmware validation Management software should be from same server OEM" | Bidder to Comply TS
216 | 13 | 1. Server Type 1 DRS 2. Server Type 2 DRS | VOL-II Appendix | Bidder to offer server with Operating system and Virtualization software with OEM support as per total CPU cores/ socket configured and specifications defined for unlimited VMs. | To have smooth integration and support experience, Please add following in the specification: " OEM should be present in India for Min 5 year. OEM should provide unlimited ticket support." Also specify PGCIL would required 9x5 or 24 x 7 support. | Bidder to Comply TS
217 |  | 17. SAN Storage DRS | VOL-II Appendix | Request to add clause | Storage system data availability is not defined in the DRS. Request to add " Storage should have 100% data availability gurantee from OEM" | Bidder to Comply TS
218 |  | 17. SAN Storage DRS | VOL-II Appendix | Request to add clause | Drive scalability is missing in the specification. Please specify "storage should be scalable to minimum 300 NVMe drives" | Bidder to Comply TS
219 |  | 17. SAN Storage DRS | VOL-II Appendix | Request to add clause | Storage backend bandwidth is missing in the specification. Please specify "The offered storage inter-controller communication and disk enclosures connectivity shall via at-least 4 x 100Gbps Ports or 50GB/sec bandwidth per controller. | Bidder to Comply TS
220 | 8 | 20. Tape Library DRS | VOL-II Appendix | SAS | As SAN Switch is already asked in RFP. Tape library can also be connected to SAN switch. Request to amend clase as "SAS or FC" | Bidder to Comply TS
221 |  | Volume 2/16. LAN Switch | 307 | 10 Gbps Fibre Optic Ports for Connecting dual Fibre Optic LAN Minimum 8x10 Gbps Fibre Optic Ports and 16x1 Gbps Ethernet ports at main and backup control centre Minimum 4x10 Gbps Fibre Optic Ports and 8x1 Gbps Ethernet ports at remaining location | Switch should support minimum 24x10 Gbps Fibre Optic Downlink Ports and 4x 50G uplink ports. The downlink ports to be utilized for Connecting dual Fibre Optic LAN and transceivers to be populated as below- Minimum 8x10 Gbps Fibre Optic Ports and 16x1 Gbps Ethernet ports at main and backup control centre Minimum 4x10 Gbps Fibre Optic Ports and 8x1 Gbps Ethernet ports at remaining location | Bidder to Comply TS
222 |  | Volume 2/16. LAN Switch | 307 | 10 Gbps Fibre Optic Ports for Connecting dual Fibre Optic LAN Minimum 8x10 Gbps Fibre Optic Ports and 16x1 Gbps Ethernet ports at main and backup control centre Minimum 4x10 Gbps Fibre Optic Ports and 8x1 Gbps Ethernet ports at remaining location | Kindly clarify on the transceiver type to be multimode or single mode. | The SFP requirement shall be finalized by the bidder as per the requirement of the solution. Bidder to comply TS
223 |  | Volume 2/16. LAN Switch | N/A | N/A- Additional Clause Requested | Switch should support minimum 880Gbps switching capacity, 650Mpps forwarding rate. | Bidder to Comply TS
224 |  | Volume 2/16. LAN Switch | N/A | N/A- Additional Clause Requested | Switch should support stacking of upto 10km and 10 switches in a single stack. | Bidder to Comply TS
225 |  | Volume 2/16. LAN Switch | N/A | N/A- Additional Clause Requested | The Switch should support trusted platform module (TPM) for platform integrity to ensures the boot process started from a trusted combination of switches. | Bidder to Comply TS
226 |  | Volume 2/16. LAN Switch | N/A | N/A- Additional Clause Requested | The Switch should support time series database apart from configuration database. | Bidder to Comply TS
227 |  | Volume 2/16. LAN Switch | N/A | N/A- Additional Clause Requested | Proposed switch should provide built-in enhanced visibility and troubleshooting. Switch should automatically interrogate and analyzes events that can impact a networks health. | Bidder to Comply TS
228 |  | Volume II 1.6 Scope of Work (f) | 12 | Import and Adaption of database & displays made by Employer/Owner for existing regional UNMS including import of historical data stored in existing servers for integration in new system. | Kindly suggest the duration of historical data to be exported from existing regional UNMS to proposed N-UNMS | All hourly historical data need to integrated. Bidder to Comply TS
229 |  | Volume II 1.6 Scope of Work (i) | 12 | Installation and commissioning of EDR, NDR, Data Diodes in existing UNMS system and national UNMS system. Contractor has to do necessary co-ordination with existing UNMS Contractor for installation, commissioning an integrating EDR, NDR and Data diodes at existing UNMS control center without any additional cost to the employer. | Request to please share region-wise count of endpoints for EDR, network traffic (north-south, east-west traffic), number of network inputs to size the TAP | Presently 1 LOT has been specified for 1000 Licenses or EDR agent. If Additional Licenses shall be required, same shall be provided at proportional rate. Bidder to Comply TS.
230 |  | Volume II 1.7 General Requirements | 14 | The Bidder's proposal shall clearly identify all features described in the specifications or in any supporting reference material that will not be implemented; otherwise, those features shall become binding as part of the final contract. | Kindly elaborate the aforesaid clause / statement | Bidder to Comply TS
231 |  | Volume II PART- A SECTION-3 3.3 Duration of Maintenance Services | 49 | The maintenance services shall be carried out during Defect Liability Period and for a period of Six (6) years after the end of the defect liability period. r) Comprehensive Maintenance of the supplied system for seven (7) years including one (1) year defect liability period as per specification including future UNMS Integrations, Database configurations, Maintaining Spare inventory etc. | Request to please clarify the project maintenance time period i.e., Seven (7) years or Six (6) years as the mentioned clause are ambiguous. | Bidder to Comply TS
232 |  | Volume II 2.11. SIEM (21) | 116 | The UEBA must be offered fully integrated within the proposed solution. All devices such as laptop, desktop, servers etc. being supplied under this project are to be covered under UEBA. | Kindly share the number of users to be considered for UEBA. Do we consider users & entities onboarded in N-UNMS or all users from regional UNMS along with N-UNMS users. | Bidder to Comply TS
233 |  | Volume II 4.6 Cyber Security | 156 | All the proposed cyber security products OEMs shall have their own threat intelligence platform. | Threat intelligence platform is dedicated solution provided by specific OEMs. Hence request PGCIL to admend the clause as below. "All the proposed cyber security products OEMs shall have their own threat intelligence / feeds." | All the proposed cyber security products OEMs shall have their own threat intelligence platform. Bidder to Comply TS
234 |  | Volume II 1.6 Scope of Work (o) | 13 | Additional Hardware, software and services necessary to ensure compatibility with existing equipment. | To ensure seamless integration with the new infrastructure, we kindly request you to share the following details of the existing infrastructure: 1. Make and Model of the existing equipment 2. Software Type and Version currently in use 3. Product Support Details, including support level and validity | If required, survey may be done by the bidder for any information required about the existing system. Bidder to Comply TS.
235 |  | Volume II 1.8.1 Teaming Agreement of bidder with OEM (f) | 15 | Availability of Subject Matter Expertise (SME) on site from OEM shall be ensured in case Contractor is not able to resolve the problem. i. A minimum number of SME(s) shall be made available for entire implementation duration till Take over by Employer/Owner. The same shall be covered contractually between Contractor & OEM(s). ii. Identified SME(s) to be attached with respective contractors for the period of delivery and up to an identified milestone. iii. Designated OEM(s) representatives shall be available for all Project Steering committee meetings. | To ensure accurate planning and alignment with the RFP requirements, we kindly request clarification on the following points: OEM Implementation Requirement: Please confirm whether OEM implementation is mandatory for each technology mentioned in the RFP, or if the bidder is permitted to carry out the implementation independently. Man-Days Estimation: Kindly specify the exact number of man-days required for each technology across the entire project. Your clarification on the above will help us prepare a compliant and optimized proposal. | Bidder to Comply TS
236 |  | Volume II 1.8.1 Teaming Agreement of bidder with OEM (H) | 15 | For all third-party equipment (Hardware & Software) Contractor shall have back-toback support & warranty along with supply of spare with appropriate response time from OEM and these Back-to-Back contracts will be shared with owner before start of defect liability period. | To avoid any potential conflicts in SLA commitments, we recommend specifying the highest level of support available from the proposed product in the RFP. This will help ensure that all OEMs are aligned and operating under the same expectations.. | Bidder to Comply TS
237 |  | Volume II 1.9.3 Exclusions from contractor’s Scope: | 19 | 1.9.3 Exclusions from contractor’s Scope: | Please clarify the number of racks to be considered at both locations. Additionally, kindly share the maximum load capacity per rack for device placement. These details are essential to ensure proper planning and accurate placement of devices across the project. | Bidder to Comply TS
238 |  | Volume II 3.4.4.1.Preventive Maintenance, Updates & Upgrades (iii) | 52 | The Contractor shall supply and install the new Software Upgrade Releases( both minor & major), Software Updates and/or Service Packs for N-UNMS system including Operating System and latest versions as generally made available by the The Contractor shall supply and install the new Software Upgrade Releases( both minor & major), Software Updates and/or Service Packs for N-UNMS system including Operating System and latest versions as generally made available by the Contractor from time to time during the entire period of this maintenance services. | Please clarify the preventive maintenance schedule or duration to be considered, so that appropriate costing can be factored in for the entire project. | Bidder to Comply TS
239 |  | Volume II 3.4.6 Spares Management (3) | 54 | Contractor shall submit a location wise list of spare items being maintained by them, indicating the total number of such items required to meet the performance criteria as stipulated in the specifications. However, minimum requirement list does not absolve the Contractor in meeting performance requirement under this maintenance services agreement due to non-availability of spares. Contractor shall on its own increase the spare items above the minimum list, if the situation demands so, to meet the performance parameters. | Kindly clarify the details of spare parts along with the required quantity for each technology product, so that all bidders can consider the same and ensure consistency across the entire project, avoiding any potential conflicts. | Bidder to Comply TS
240 |  | Volume II 4.1.2 Operating System | 149 | The operating system of all the equipments of N-UNMS system including network equipments shall be latest version. The operating system shall be hardened to provide robust security. In order to facilitate cyber security requirements including patch management, common operating system is preferable to be used by all server nodes within the N-UNMS System. All workstations supplied should have MS office installed and licensed for the whole duration of project without any additional cost to employer. | Please clarify whether Microsoft licenses are required to be considered with Software Assurance or without, to ensure accurate compliance with project requirements. Kindly clarify. | For Operating System, Software Assurance must be taken by the contractor for the system supplied under the project. Bidder to Comply TS
241 |  | Volume II 8 | 170 | A SAN (Storage Area Network) based storage shall be provided, along with SAN Switch, which shall be sized adequately and shall be used for online storage and all online data backup. Historian shall be connected to the servers through dedicated Fiber optic using SAN Switch. The historian system shall facilitate Owner’s Application data storage also. The sizing of the same shall be suitably sized by the contractor to meet the specification requirements. There shall not be anysingle point failure i.e. there shall be zero down time with single element failure It shall be possible to take and store image backup of all servers & workstations on it. The SAN shall facilitate Employer’s Application Data Storage also. The SAN Storage in N-UNMS project is 350 TB in Raid 6/DP from Day 1. Backup from SAN storage at Main Control center of NR-UNMS, NERUNMS,ER-UNMS, WR-UNMS and SR-UNMS must be kept at SAN of N-UNMS. Any additional Software/hardware required for taking backup of existing UNMSs system to SAN at National UNMS system must be supplied by contractor without any additional cost to employer. | To ensure we propose an appropriate and compliant backup solution, we kindly request your clarification on the following points: Existing Infrastructure Details: Please provide details of the existing infrastructure that should be considered while sizing the backup license. Backup License Type: Please confirm whether the backup license should be based on the total backup capacity or the total number of VMs. Backup Storage Capacity: We understand that the required backup storage is 350TB, sized as per the project timeline. Kindly confirm if the bidder is expected to provision exactly this capacity. | Detail of SAN storage and backup software has been mentioned in the technical specification. The SAN storage Capacity mentioned in TS is to be consider at Day-1. If higher capacity of storage is required by the bidder for the solution offered under the project, same may be considered by the Bidder without any additional cost to employer. Bidder to comply TS.
242 |  | Volume II Appendix -C BoQ of N-UNMS (16-28)(123-135) | 284 | Supply-Software for Main CC +Supply-Hardwares for Backup CC | We kindly request your clarification on the following points to ensure accurate solution design and compliance with the RFP: 1. Solution Category: Please confirm which category of product solution PGCIL is looking for: 1.1Virtualization-based solution - Please specifiy technology product required virtualization Standalone server-based solution 1.2 Server Configuration Flexibility: Please specifiy technology product required virtualization Standalone server. 2. Please clarify whether bidders are allowed to: Upgrade the minimum specifications (e.g., Server, RAM, Storage) to a higher configuration to minimize the server count. or Increase the number of servers while keeping the base configuration as specified in the RFP | The Servers mentioned in The BPS are minimum numbers of physical servers to be provided with the minimum configuration mentioned in technical specification. If higher Number/higher configuration servers are required to meet the requirement mentioned in the technical specification, same may be provided by the bidder without any additional cost to employer. Bidder to Comply TS.
243 |  | Volume II 20. Tape Library (4,8) | 309 | Drive technology - LTO-5 or Latest | As LTO-5 is no longer available with the OEM, we kindly request you to consider revising the specification to LTO-9 or higher for compatibility with currently available technology. | Bidder to Comply TS
244 |  | Volume II |  | Interface- SAS | As there is
245 |  | Volume II 19. Network Attached Storage (NAS) (4,13) | 309 | Capacity -10 TB in RAID 6 | Storage Capacity: Please confirm whether the specified capacity is usable or raw. Drive Type for 10TB Capacity: Kindly clarify whether the required 10TB capacity should be provisioned using SATA, NL-SAS, or SSD drives. | Kindly Refer Amendment No III
246 |  | Volume II 19. Network Attached Storage (NAS) | 309 | Ports - 4 x 10 Gbps ports | Port Type Requirement: Please confirm whether the required network connectivity should be provisioned using copper ports or fiber ports | Kindly Refer Amendment No III
247 |  | Volume II 17. SAN (Storage Area Network) based storage or any other specialized storage solution | 308 | Ports | We kindly request your clarification on the following to ensure accurate configuration of the SAN storage solution: Number of Fibre Channel Ports required Number of Ethernet Ports required | Bidder to Comply TS
248 |  | Volume II 1. Servers for Network Resource Management, Design, Activation, Configuration Planning , Fault Management, Performance Management, Trouble Ticking, Reporting & Dash boarding, EDR, Data Historian, Data Replica, Web server and any other server except that mentioned at Point 2 etc. (9) | 291 | Interfaces Ports 1. 10 Gbps dual Fibre Optic Ports (Minimum) for connecting on dual Fibre optic LAN in each server at Main & Backup Control Centre 2. 16/32 Gbps dual FC Ports (Minimum) for connecting on dual FC SAN in each server at Main & Backup Control Centre | Please confirm whether the requirement is for: 1 x Dual 10Gbps SFP 1 x Dual 32Gbps FC or 2 x Dual Port 10Gbps SFP Ethernet Cards 2 x Dual Port 32Gbps FC HBA Cards | Bidder to Comply TS
249 |  | Volume II 3.9 Patch Management | 62 | The contractor shall also be responsible for providing updates/patches for the software products supplied under the project. All other patches of third-party product like Operating System and Anti-virus shall be tested by the Contractor prior to installing in the supplied system. Subsystems/ Devices like IPS, Network IPS, Host based IPS, Firewalls shall also be provided with secure patch management. | As per our understanding, PGCIL requires a patch management solution. Therefore, we kindly request you to provide the necessary license details for patching, as well as the operating system Flavors involved. Please correct our understanding. | Bidder to Comply TS
250 |  | Volume II 4.9 Database development tools | 158 | The Contractor shall provide all necessary software tools for the development and maintenance of the N-UNMS system, Historian and other databases at UNMS Centre. This tool shall be capable of managing the entire system database. The database development software tool delivered with the N-UNMS system shall be used to generate, integrate and test the database. | AS per our understanding, PGCIL requires database with its development tools. Please correct our understanding. | Bidder to Comply TS
251 |  | Volume II 8.1.3. BoQ | 211 | i. There should be 100 Admin (Resolver license) and 2500 User (Ticket initiator) for 7 Years | Request you to please help on license type required ( subscription base or perceptual) | Bidder to provide license for 7 Years. Bidder to comply TS
252 |  | Volume II 2.8.1 Training Requirement for UNMS System | 41 | The training course requirements are described below in terms of the contents of each course to be provided. Training for the complete N-UNMS SYSTEM (Hardware and software) shall be provided for Computer System Hardware, Service Fulfilment, Service assurance, Reporting & Dash Boarding System, Incident Management System and Web Portal, supplied N-UNMS system database for the application software course, database, display building and Auxiliary Power Supply System etc. A tentative training schedule for a specified duration is described below | We request your guidance on the preferred mode of training Remote for all location or Onsite. | training Shall be Onsite. Bidder to comply TS
253 |  | Volume II 2.6.3 EDR |  | The proposed solution should block malicious traffic from data exfiltration (data leakage) | Requesting to remove | Bidder to Comply TS
254 |  | Volume II 2.6.3 EDR |  | The solutions should support the Automated False Positive Reclassifications to Ability to automatically reclassify activity as false positives and prevent similar detections from occurring. | The solutions should have the ability reclassify False Positive and prevent similar detections from occurring. | Bidder to Comply TS
255 |  | Volume II 2.6.3 EDR |  | The proposed solution should have the ability to create Whitelist/Blacklist for the files based on their names, location (File Path), version, and provider | The proposed solution should have the ability to create Whitelist/Blacklist for the files based on their names, location (File Path). | Bidder to Comply TS
256 |  | Volume II 2.6.3 EDR |  | Solution shall have the ability to restore encrypted files to their previous unencrypted state on detection of ransomware based on behavior | Requesting to remove this point | Bidder to Comply TS
257 |  | Volume II 13. Sizing Parameters Internal Firewall/UTM: |  | The proposed hardware should have dual redunant hotswappable Power supply | Request to kindly ask for redundant power supplies to ensure minimal downtime in operations | Kindly Refer Amendment No III
258 |  | Volume II 13. Sizing Parameters Internal Firewall/UTM: |  | The proposed hardware should have dual redunant Fan Module | Request to kindly ask for redundant fans to ensure minimal downtime in operations | Kindly Refer Amendment No III
259 |  | Volume II 13. Sizing Parameters Internal Firewall/UTM: |  | The proposed hardware should have local storage of logs upto 900 Gb | Request to kindly ask for adequate Log Storage capacity which is missing in the RFP | Bidder to Comply TS
260 |  | Volume II 13. Sizing Parameters Internal Firewall/UTM: |  | The proposed solution should have minimum 32Gb of RAM | Request to kindly ask for adequate RAM capacity to ensure optimal capacity for operating system, configurations, and data processing capabilities | Bidder to Comply TS
261 |  | Volume II 5.7 Network Detection and Response (NDR) |  | The Solution must be capable of scanning files in seconds without transmitting any data to the cloud, ensuring fast and secure on-premises processing. | "The Solution must be capable of scanning network telemetry isng SPAN/NetFlow in seconds without transmitting any data to the cloud, ensuring fast and secure on-premises processing." | Kindly Refer Amendment No III
262 |  | Volume II 5.7 Network Detection and Response (NDR) |  | The proposed solution shall have the ability to stop the first malware download through inline blocking by integrating with the perimeter security solution such as NGFW itself. (using API) | The proposed solution shall have the ability to stop the first malware download by integrating with solutions such as NGFW / Proxy / SOAR solution using Webhooks. | Bidder to Comply TS
263 |  | Volume II 5.7 Network Detection and Response (NDR) |  | The proposed solution should support SMB / CIFS / NFS protocol for sharing and transferring files. | Requesting to remove this point | Bidder to Comply TS
264 |  | Volume II 5.7 Network Detection and Response (NDR) |  | The solution should protect the endpoints against advanced threats including zero-day attacks, which target application vulnerabilities that have yet to be discovered or patched. |  | Bidder to Comply TS
265 |  | Volume II 5.7 Network Detection and Response (NDR) |  | Traffic Learning to be based full packet analysis | Requesting to remove this point | Bidder to Comply TS
266 |  | Volume II 2.9. Email Server |  | The email solution should support sandboxing integration to protect zero-day malware & APT. |  | The ESS Solution should integrated with sandbox solution supplied under this project.
267 |  | Volume II 2.9. Email Server |  | The email clients shall have features like email notification, Address books, user definable folders etc. |  | Bidder to Comply TS
268 |  | Volume II 15. Router ( WAN Router Cum Firewall) |  | Router should support 1 GB, 10 GB Minimum 16 no. - 1 GB Ethernet ports, 8x10 Gbps Fibre optic ports At main and Backup Control Centre | Router should support 1 GB, 10 GB Minimum 16 no. - 1 GB Ethernet ports, 5x10 Gbps Fibre optic ports At main and Backup Control Centre | Bidder to Comply TS
269 |  | Volume II PART- B SECTION-5 N-UNMS HARDWARE SPECIFICATIONS |  | Router and firewall shall be provided with necessary license support till the completion of maintenance period. There shall be 50% spare ports | Router and firewall shall be provided with necessary license support till the completion of maintenance period. | Kindly Refer Amendment No III
270 |  | Volume II 16. LAN Switch |  | Switch should redundant hot swappable power supply and redundant Fans |  | Kindly Refer Amendment No III
271 |  | Volume II 16. LAN Switch |  | Switch should support MacSec ( 802.1ae) to ensure encryption of layer 2 traffic from Day 1 |  | Bidder to Comply TS
272 |  | Volume II 16. LAN Switch |  | Switch should be Ipv6 logo certified from Day1 |  | Bidder to Comply TS
273 |  | Volume II Servers for Network Resource Management, Design, Activation, Configuration Planning |  | 480 GB NVMe (min Gen 4) delivered expandable up to 1TB | 2x 960 GB NVMe (min Gen 4) hot swappable drives | Bidder to Comply TS
274 |  | Volume II Servers for Network Resource Management, Design, Activation, Configuration Planning |  | Server should support min. six PCI-Express 5.0 x16 slots | Server should support min. 4 PCI-Express 5.0 x16 slots | Kindly Refer Amendment No III
275 |  | Volume II Servers for Network Resource Management, Design, Activation, Configuration Planning |  | Dual AC Power Supply | Hot pluggable Dual AC Power Supply | Bidder to Comply TS
276 |  | Volume II Servers for Configuration Management Cum CMC, Identity & Patch Management |  | 480 GB NVMe (min Gen 4) delivered expandable up to 1TB | 2x 960 GB NVMe (min Gen 4) hot swappable drives | Bidder to Comply TS
277 |  | Volume II Servers for Configuration Management Cum CMC, Identity & Patch Management |  | Server should support min. six PCI-Express 5.0 x16 slots | Server should support min. 4 PCI-Express 5.0 x16 slots | Kindly Refer Amendment No III
278 |  | Volume II Servers for Configuration Management Cum CMC, Identity & Patch Management |  | Dual AC Power Supply | Hot pluggable Dual AC Power Supply | Bidder to Comply TS
279 |  | Volume II 18. Applicable Standards |  | 18. TEC GR No: TEC GR No TEC/GR/I/ESI-001/03/MAR12 for Mid-Tier Storage. | As PGCIL is looking for All NVMe storage. Some of the point of TEC GR may not be applicable to NVMe storage as TEC GR was made 10+ year back. We understand DRS requirement is final and supersede TEC GR. Kindly confirm. | The clause is mentioned in the Technical specification " Specifications and codes shall be the latest version, inclusive of revisions, which are in force". Bidder to Comply TS
280 |  | Volume II 11. PCIe Slots | VOL-II Appendix | Server should support min. six PCI-Express 5.0 x16 slots | 5th Gen server offer high bandwidth PCIe 5.0 slots. To get maximum benefit of Gen 5 server Request to modify clause as "Server should support min. Eight PCI-Express 5.0 x16 slots and should be configured with min. six PCI-Express 5.0 x16 slots" | Bidder to Comply TS
281 |  | Volume II 12. Security & Management Features | VOL-II Appendix |  Secure Recovery - recover critical firmware to known good state on detection of compromised firmware  Security Dashboard for Server to detect possible security vulnerabilities.  Should help to proactively identify out-of- date BIOS, drivers, and Server Management agents and enable the remote update of system software/firmware components.  Offered server should be listed on spec.org  It should support historical reporting and should have support for multifactor authentication | To reduce exposure to vlunerabilities system should have validation mechanism in run time as well. Also many time system expose to vunerability due to manual process of firmware updates and all system are not at the same baseline firmware level. To strengthen server security, request to add following clause: " For firmware security, system should support remote management chip creating a fingerprint in the silicon, preventing servers from booting up unless the firmware matches the fingerprint. This feature should be immutable. Should have encrypted virtual media Should maintain repository for firmware and drivers recipes to aid rollback or patching of compromised firmware. Should also store Factory Recovery recipe preloaded to rollback to factory tested secured firmware Should have dashboard for firmware baselines while performing minimum required firmware checks and highlighting out-of-compliance devices for updates with the selected firmware baseline Server should have runtime firmware validation Management software should be from same server OEM" | Bidder to Comply TS
282 |  | Volume II 13. Operating System and Virtualization | VOL-II Appendix | Bidder to offer server with Operating system and Virtualization software with OEM support as per total CPU cores/ socket configured and specifications defined for unlimited VMs. | To have smooth integration and support experience, Please add following in the specification: " OEM should be present in India for Min 5 year. OEM should provide unlimited ticket support." Also specify PGCIL would required 9x5 or 24 x 7 support. | Bidder to Comply TS
283 |  | Volume II | VOL-II Appendix | Request to add clause | Storage system data availability is not defined in the DRS. Request to add " Storage should have 100% data availability gurantee from OEM" | Bidder to Comply TS
284 |  | Volume II | VOL-II Appendix | Request to add clause | Drive scalability is missing in the specification. Please specify "storage should be scalable to minimum 300 NVMe drives" | Bidder to Comply TS
285 |  | Volume II | VOL-II Appendix | Request to add clause | Storage backend bandwidth is missing in the specification. Please specify "The offered storage inter-controller communication and disk enclosures connectivity shall via at-least 4 x 100Gbps Ports or 50GB/sec bandwidth per controller. | Bidder to Comply TS
286 |  | Volume II Protocols |  | NFS, CIFS and VTL | As the primary use case of device is backup, request to add OST/Catalyst which are backup aware protocols. It allows backup applications to communicate directly with storage devices, offering various benefits like improved performance and feature integration. Request to amend clause as "NFS, CIFS, OST/Catalyst and VTL"
287 |  | Volume II 8. Interface | VOL-II Appendix | SAS | As SAN Switch is already asked in RFP. Tape library can also be connected to SAN switch. Request to amend clase as "SAS or FC" | Kindly Refer Amendment No III
288 |  | Volume II 7 | 307 | 10 Gbps Fibre Optic Ports for Connecting dual Fibre Optic LAN Minimum 8x10 Gbps Fibre Optic Ports and 16x1 Gbps Ethernet ports at main and backup control centre Minimum 4x10 Gbps Fibre Optic Ports and 8x1 Gbps Ethernet ports at remaining location | Switch should support minimum 24x10 Gbps Fibre Optic Downlink Ports and 4x 50G uplink ports. The downlink ports to be utilized for Connecting dual Fibre Optic LAN and transceivers to be populated as below- Minimum 8x10 Gbps Fibre Optic Ports and 16x1 Gbps Ethernet ports at main and backup control centre Minimum 4x10 Gbps Fibre Optic Ports and 8x1 Gbps Ethernet ports at remaining location | Bidder to Comply TS
289 |  | Volume II 7 | 307 | 10 Gbps Fibre Optic Ports for Connecting dual Fibre Optic LAN Minimum 8x10 Gbps Fibre Optic Ports and 16x1 Gbps Ethernet ports at main and backup control centre Minimum 4x10 Gbps Fibre Optic Ports and 8x1 Gbps Ethernet ports at remaining location | Kindly clarify on the transceiver type to be multimode or single mode. | The SFP requirement shall be finalized by the bidder as per the requirement of the solution. Bidder to comply TS
290 |  | N/A | N/A | N/A- Additional Clause Requested | Switch should support minimum 880Gbps switching capacity, 650Mpps forwarding rate. | Bidder to Comply TS
291 |  | N/A | N/A | N/A- Additional Clause Requested | Switch should support stacking of upto 10km and 10 switches in a single stack. | Bidder to Comply TS
292 |  | N/A | N/A | N/A- Additional Clause Requested | The Switch should support trusted platform module (TPM) for platform integrity to ensures the boot process started from a trusted combination of switches. | Bidder to Comply TS
293 |  | N/A | N/A | N/A- Additional Clause Requested | The Switch should support time series database apart from configuration database. | Bidder to Comply TS
294 |  | N/A | N/A | N/A- Additional Clause Requested | Proposed switch should provide built-in enhanced visibility and troubleshooting. Switch should automatically interrogate and analyzes events that can impact a networks health. | Bidder to Comply TS