|  |  |  |  |
| --- | --- | --- | --- |
| **Sl. No.** | **Reference Clause** | **Bidder’s Query** | **POWERGRID's Reply** |
| 1. | Scope of SITC of Power Cable / Control Cable / Special Cable between Transformer MB/CCC to RTCC Panel /ACDB DCDB / SAS | We would like to bring in your kind notice that in the section project scope is not defined for the SITC of Power Cable / Control Cable / Special Cable between Transformer MB/CCC to RTCC Panel /ACDB DCDB / SAS.In this regard, we understand that the cables between Transformer MB/CCC to RTCC Panel /ACDB DCDB / SAS is excluded from bidder’s scope.Please Confirm. | Scope in bidding document is ample clear.Clause 2.1(c) of the Section –project may bereferred to.Bidder to comply the requirement of Technical specification. |
| 2. | Overall Layout | If Cable will be in the scope of bidder, request you to please provide the overall layout for the estimation of cable quantity. | Bidder is requested to assess the requirement in line with bidding document, for the estimation of cable quantity. |
| 3. | Parallel Operation | We understand that ICT’s under present scope will be operated as standalone. No need to consider parallel operation with existing ICTs.Please Confirm. | Impedance and other parameters for parallel operation of offered Transformer under present scope shall be as per Annexure-A of technical specification section-Transformer (Upto 400KV class) Rev13. However, Note-1 under Annexure-A shall not be referred to. |
| 4. | Transformer Earthing | We understand that connection of transformer to grounding mat is not in the scope of bidder.Please confirm. | Provision for Transformer earthing including connection to the grounding mat shall be as per clause 6.14.4 of technical specification section-Transformer (Up to 400KV class) Rev13 is under present scope. |
| 5. | Section Project/ Specific Exclusion/ Clause no.3 / Sl No: (iv) / Page no. 3 of 5Civil works for Road within the boundary of all substations. | We would like to inform you that there is no road within the boundary of substation. In this regard, we understand that the Internal Access Roads Until the Site / Plot (including necessary maintenance / clearance from obstructions due to natural or local events or weather or any strengthening of roads or modification of any culverts/drains/firefighting pipe line/street lighting system / road/fence, to make the road accessible / motorable/ making of any difference in FGL) are made available by the Owner (or by Owner through relevant authorities) to the Contractor for the Project Works i.e. Movement of Heavy Vehicles / Construction Vehicles, Transportation of project Personnel, Equipment etc.Please Confirm. | Specification is amply clear. In line with Clause 3 of Section Project, Civil works for Road within the boundary of all substations is under specific exclusion.Bidders are also to refer to Clause no. 8.3.19 of Technical Specification: GTR & Quote accordingly. |

|  |  |  |  |
| --- | --- | --- | --- |
| 6. | Section Project/ Scope/ Clause no. 2.1. a/Page no. 3 of 5 Design, engineering, manufacture, testing at manufacturers works, supply, transportation, unloading and delivery at site including insurance & storage, erection, testing and commissioning at site for 400/220/33kV, 3-phase Transformers, as per BPS&Section Project/ Specific Exclusion/ Clause no.3 / Sl No: (i)/Page no. 3 of 5“Storage platform/Foundation Block & associated civil works.” | With reference to the scope, we understand that bidder has to store the accessories at storage area subject to PCC platform for storage arrangement shall be provided by customer.Please Confirm. | Technical requirement of storage platform is ample clear in Bidding documents.Storage platform/Foundation Block & associated civil works are not envisaged under present scope. |