| Sl. No. | Clause Ref. No. | Existing provision | Amended as |
| --- | --- | --- | --- |
|  | 2.0 Scope of Work, Table 1: Project Requirements, Technical Specification: Section-Project Rev-00 | Sr. No.; Attribute; Value. Location of Battery Energy Storage System for Base Capacity / Interconnection Point; 400/220KV SS Kalikiri. Output/Input Power Rating of BESS at the delivery point (Power Capacity of Project)#; 150 MW. Initial Design Output Energy Capacity of BESS at the delivery point*; 300 MWh. Approx. land allocation in sq. meters; 18,000. Charge/Discharge (C-Rate); 0.5. Rated Duration of BESS Discharge; 2 Hours. Recovery Time (Maximum allowed cooling time between Complete Charge to Complete Discharge or Complete Discharge to Complete charge); The maximum cooling time permitted between complete charge to complete discharge, or complete discharge to complete charge, shall be 1 hour. For one complete operating cycle, the total recovery time shall not exceed 2 hours. For partial cycle operation, the recovery time shall be proportionate to the extent of charging or discharging involved and shall not exceed the corresponding limit specified for a complete cycle.. Energy content value at the end of the duty cycle; As per design of Contractor. Rated DoD / Min. SOC level; As per design of Contractor. Nominal Energy Capacity; As per design of Contractor. Input and output power rating; As per design of Contractor. AC to AC Roundtrip efficiency; Minimum 87%. Nos. of Cycles (Charging/Discharging) /Per day##; 2 operational cycles/day (i.e. 2 complete charge-discharge cycles per day) for a period of 12 years.. Interconnection Voltage level of BESS; 33 kV. Delivery Point; Measurement/Metering Point of APTRANSCO/Employer at 33 kV. Term and definitions of terminology related to BESS; IEC 62933-2-1.. ## SLDC/DISCOM, at its discretion, may split the charging and discharging of each block of BESS into one or more sessions, with a minimum session duration of 15 minutes, depending on system requirements. The total time required to complete each full depth charge-discharge cycle shall be proportionately adjusted according to the number of sessions. Furthermore, if the BESS transitions from charging to discharging, or vice versa, before reaching full depth charge or discharge (i.e., during intermediate stage), such partial cycles shall also be considered to count as Full Cycle for the purpose of contract. | Sr. No.; Attribute; Value. Location of Battery Energy Storage System for Base Capacity / Interconnection Point; 400/220KV SS Kalikiri. Output/Input Power Rating of BESS at the delivery point (Power Capacity of Project)#; 150 MW. Initial Design Output Energy Capacity of BESS at the delivery point*; 300 MWh. Approx. land allocation in sq. meters; Please refer to Annexure-A to this Amendment. Charge/Discharge (C-Rate); 0.5. Rated Duration of BESS Discharge; 2 Hours. Recovery Time (Maximum allowed cooling time between Complete Charge to Complete Discharge or Complete Discharge to Complete charge); The maximum cooling time permitted between complete charge to complete discharge, or complete discharge to complete charge, shall be 1 hour. For one complete operating cycle, the total recovery time shall not exceed 2 hours. For partial cycle operation, the recovery time shall be proportionate to the extent of charging or discharging involved and shall not exceed the corresponding limit specified for a complete cycle.. Energy content value at the end of the duty cycle; As per design of Contractor. Rated DoD / Min. SOC level; As per design of Contractor. Nominal Energy Capacity; As per design of Contractor. Rated Short-circuit current at 33 KV; 31.5 kA for one (1) sec duration. AC to AC Roundtrip efficiency; Minimum 87%. Nos. of Cycles (Charging/Discharging) /Per day##; 2 operational cycles/day (i.e. 2 complete charge-discharge cycles per day) for a period of 12 years.. Interconnection Voltage level of BESS; 33 kV. Delivery Point; Measurement/Metering Point of APTRANSCO/Employer at 33 kV. Term and definitions of terminology related to BESS; IEC 62933-2-1.. ## SLDC/DISCOM, at its discretion, may split the charging and discharging of each block of BESS into one or more sessions, with a minimum session duration of 15 minutes, depending on system requirements. The total time required to complete each full depth charge-discharge cycle shall be proportionately adjusted according to the number of sessions. Furthermore, any transition of the BESS from charging to discharging, or vice versa, prior to achieving full depth of charge or discharge (i.e., partial cycles), shall be cumulatively accounted on the basis of energy throughput with reference to the rated usable energy of the BESS. |
|  | 2.1 Battery Energy Storage System, Technical Specification: Section-Project Rev-00 | ….. s) Submission of engineering drawings, design calculations, performance test procedures, single line diagrams, electrical layouts, Equipment layout, Drawings/Data sheets of bought out items, Civil Drawings, Operation & Maintenance manuals/instruction manuals etc. to POWERGRID for review/approval. Further, submission of list of sub-vendors, manufacturing quality plans and Field quality plans/ material quality plan for approval of POWERGRID. ….. w) All preventive and annual maintenance activities, up to and including the 33 kV pooling switchgear, shall be in the Contractor’s scope for the entire contract period. … | ….. s) Submission of engineering drawings, design calculations, performance test procedures, single line diagrams, electrical layouts, Equipment layout, Drawings/Data sheets of bought out items, Civil Drawings, Operation & Maintenance manuals/instruction manuals etc. to POWERGRID/Employer for review/approval. Further, submission of list of sub-vendors, manufacturing quality plans and Field quality plans/ material quality plan for approval of POWERGRID. …. w) All preventive and annual maintenance activities under this project shall be in scope of the contractor for the entire contract period. … |
|  | 2.9.4 Guaranteed Roundtrip Efficiency, Technical Specification: Section-Project Rev-00 | … MDn-1 refers to minimum guaranteed dispatchable energy at the end of the previous year (as a % of Capacity at the COD specified in Clause 2.11.3 above); … | … MDn-1 refers to minimum guaranteed dispatchable energy at the end of the previous year (as a % of Capacity at the COD specified in Clause 2.9.3 above); … |
|  | 2.9.7.1 LD Calculation w.r.t. Guaranteed Monthly System Availability, Technical Specification: Section-Project Rev-00 | Liquidated damages on account of shortfall in meeting the Guaranteed System Availability mentioned in Clause 2.11.2 shall be calculated as follows: ….. | Liquidated damages on account of shortfall in meeting the Guaranteed System Availability mentioned in Clause 2.9.2 shall be calculated as follows: …..…. |
|  | 7.14 Auxiliary System Technical Specification: Section-Project Rev-00 | Employer shall draw power from interconnection point/separate feeder for the Auxiliary Power load of BESS. For this purpose, separate meter would be arranged by Contractor to measure Auxiliary consumption and that would be billed by DISCOMs as per prevailing tariff; applicable electricity bill shall be paid by Employer to DISCOM during O&M period. However, during construction phase, the Contractor shall make their own arrangements or may avail power supply from DISCOMs on chargeable basis as per applicable rules/procedure. Contractor shall provide necessary transformer, HT Cable and other associated switchgear equipment required for utilizing this supply for BESS. Contractor shall design & construct facilities for auxiliary supply with N-1 level contingency at 33 kV transformer for full load with provision of dual power supply for PCS transformer, battery container, PCS, lighting transformer etc. for ensuring reliability, availability, redundancy and continuous performance of BESS as required in this specification. 2 Nos. of auxiliary power feeder at LT level shall also be sourced from BESS AC Distribution Board. Auxiliary supply arrangement shall be finalized during detailed engineering as per the contractor’s design. | The dual (redundant) auxiliary power for BESS shall be provided through the 33kV system (one source from 33kV switchyard of APTRANSCO and other source from 33kV Indoor switchgear being provided under present scope). Contractor shall provide necessary LT transformers (min. 2 nos.), HT Cable and other associated equipment required for the above. Contractor shall also provide separate meters, as per the DISCOM requirements, for measurement of Auxiliary consumption. The electricity charges, during O&M period, shall be paid by the Employer. Detailed arrangement of reliable auxiliary supply to BESS shall be finalized during detailed engineering based on the offered design. During the construction phase, the Contractor shall make their own arrangements or may avail auxiliary power supply from DISCOM on chargeable basis as per applicable rules/procedure. |
|  | 5 Monitoring, Protection & Control, Technical Specifications for Power Conditioning System, Rev – 00 | • Monitoring a. Local Display unit for viewing important parameters, configuration and troubleshooting purpose shall be provided. | • Monitoring a. Local Display unit/Equivalent Solution for viewing important parameters, configuration and troubleshooting purpose shall be provided. |
|  | 5 Monitoring, Protection & Control, Technical Specifications for Power Conditioning System, Rev – 00 | • Monitoring … g. String Monitoring facility:- PCS shall be provided with current monitoring transducer at incoming DC cables from each battery array. The current transducers used for this purpose shall have accuracy of 1.0 class or better. | • Monitoring … g. String Monitoring facility:- PCS shall be provided with current monitoring transducer at incoming DC cables. The current transducers used for this purpose shall have accuracy of 1.0 class or better. |
|  | 7.1.7 LT Switchgear for BESS Auxiliaries Technical Specification: Section-Project Rev-00 | The Contractor shall provide LT switchgear and associated systems for powering all auxiliary loads of the BESS, including battery cooling system, fire detection and suppression, lighting, control systems, communication systems, and other ancillary loads. The complete auxiliary power supply for the BESS installation shall be sourced through BESS Tie Transformer itself with no dependency on external auxiliary supply. ….. | The Contractor shall provide LT switchgear and associated systems for powering all auxiliary loads of the BESS, including battery cooling system, fire detection and suppression, lighting, control systems, communication systems, and other ancillary loads. The complete auxiliary power supply for the BESS installation shall be sourced through auxiliary transformer. ….. |
|  | 1.0 General, Technical Specification: Section-Project Rev-00 | Power Grid Corporation of India Limited (POWERGRID), a Govt. of India Enterprise, is responsible for Bulk Power Transmission of electrical energy from various central Govt. Power Projects to various utilities/ beneficiaries and interconnecting regional grids, operating and maintaining the National Electrical Grid of India. It is established with mission of “We will become a Global Transmission Company with Dominant Leadership in Emerging Power Markets with World Class Capabilities by: ▪ World Class: Setting superior standards in capital project management and operations for the industry and ourselves ▪ Global: Leveraging capabilities to consistently generate maximum value for all stakeholders in India and in emerging and growing economies. ▪ Inspiring, nurturing and empowering the next generation of professionals. ▪ Achieving continuous improvements through innovation and state-of-the-art technology. ▪ Committing to highest standards in health, safety, security and environment. | Power Grid Corporation of India Limited (POWERGRID), a Govt. of India Enterprise, is responsible ….. … … ▪ Committing to highest standards in health, safety, security and environment POWERGRID Energy Services Limited (a wholly owned subsidiary of POWERGRID) is working in the power and energy areas; namely, Energy Storage System, Renewable Energy Generation, Electricity Distribution business, Smart Metering, Electric Vehicle charging infrastructure etc. POWERGRID Energy Services Limited (PESL) is the Employer for this project. |
|  | 7.1.5.2 Storage & System Hardware Technical Specification: Section-Project Rev-00 | Sr. No.; Parameter; Time Interval; Duration. 1; Real and reactive power generation, Current, voltage, frequency, Main Meter and Back up Meter Readings; 15 Minutes; 36 Months. 2; Digital data including alarm, event; 15 Minutes; 36 Months. 3; Active power, reactive power, frequency, event logger, disturbance recorder and triggering data of low voltage ride through and high voltage ride through, during tripping and protection operation at plant level; 1 ms; 90 days. 4; Battery Management System Data; As per OEM requirement; As per OEM requirement. 5; Chart & printout of event loggers, if any, for system disturbances /outages; 15 minutes; 36 Months. | Sr. No.; Parameter; Time Interval; Duration. 1; Real and reactive power generation, Current, voltage, frequency, Main Meter and Back up Meter Readings; 15 Minutes; O&M Period. 2; Digital data including alarm, event; 15 Minutes; O&M Period. 3; Active power, reactive power, frequency, event logger, disturbance recorder and triggering data of low voltage ride through and high voltage ride through, during tripping and protection operation at plant level; 1 ms; 90 days. 4; Battery Management System Data; As per OEM requirement; O&M Period. 5; Chart & printout of event loggers, if any, for system disturbances /outages; 15 minutes; O&M Period. |
|  | 2.2 Civil works Technical Specification: Section-Project Rev-00 | 6. Civil, structural and architectural works associated with RCC framed control room building including substructure, superstructure and all other related works like internal cable trench etc., complete as per system requirement and technical specification. Control room building shall be provided for the BESS installation, which shall accommodate Battery Management Systems (BMS), Energy Management System (EMS), SCADA, communication equipment, UPS and other common auxiliary systems required for operation and monitoring… .. 7. Overground ladder type cable tray system /underground cable trenches along with covers, road crossings, sump pits etc. shall be provided by contractor as per design requirement and technical specification. All pipes required in cable laying work shall deemed to be included under the Contractor’s scope. Cable trenches route to be finalized in consultation with Employer/Beneficiary. | 6. Civil, structural and architectural works associated with RCC framed control room building including substructure, superstructure and all other related works like internal cable trench etc., complete as per system requirement and technical specification. Control room building shall be provided for the BESS installation, which shall accommodate Energy Management System (EMS), SCADA, communication equipment, UPS and other common auxiliary systems required for operation and monitoring… .. … 7. Overground ladder type cable tray system /underground cable laying with or without trenches along with covers, road crossings, sump pits etc. shall be provided by contractor as per design requirement and technical specification. All pipes required in cable laying work shall deemed to be included under the Contractor’s scope. Type of Cable laying & its route to be finalized in consultation with Employer/Beneficiary during detailed engineering. The methods of cable laying and installation shall conform to IS 1255 for laying directly in ground, drawing in ducts, laying on racks in air, laying on racks inside a cable tunnel and Laying along buildings or structures, etc. |
|  | 2.7 System Design, Engineering and Studies Technical Specification: Section-Project Rev-00 | 2.7 System Design, Engineering and Studies ….. The employer presently uses PSSE Version 36 & PSCAD version 5. The contractor shall provide data & model compatible in these formats along with detailed descriptive manual detailing how to configure & utilize the model so that employer can perform further studies. | 2.7 System Design, Engineering and Studies ….. The employer presently uses PSSE Version 36 & PSCAD version 5. The contractor shall provide data & model compatible in these formats along with detailed descriptive manual detailing how to configure & utilize the model so that employer can perform further studies. Following studies is to be conducted (not limited to below) by Contractor in this regard as per requirement of STU/APTRANSCO/Employer: - Harmonic studies considering network and BESS system along with flicker studies - Transient and dynamic studies - Small signal stability studies - Sub-Synchronous Oscillations/ Sub-Synchronous Resonance / Sub- Synchronous Torsional Interaction studies - Sub-synchronous control interactions studies between different converters-based equipment. - Any other studies stipulated by STU/APTRANSCO/Employer. |
|  | 2.8 Spares Technical Specification: Section-Project Rev-00 | 2.8.1 General … Contractor shall make necessary arrangements at site to store the spares in such an environment that the spares shall be readily available/usable during their service life. Contractor shall store the spare batteries in OEM specified environment with an adequate charger to charge the batteries during storage period. PCS transformer & PCS shall be stored on proper foundation. | 2.8.1 General … Contractor shall make necessary arrangements to store the spares in such an environment that the spares shall be readily available/usable during their service life. Contractor shall store the spare batteries in OEM specified environment with an adequate charger to charge the batteries during storage period. PCS transformer & PCS shall be stored on proper foundation. |
|  | 2.9.3 Guaranteed Dispatchable Capacity Technical Specification: Section-Project Rev-00 | Periodic Checking … The test should confirm that the measured value matches or higher than the desired available energy of the system. Calculations in this regard shall be performed by the Contractor and validated by Employer. In detailed Engineering all such calculation procedure shall be provided by the Contractor and shall be approved by Employer. It shall be the responsibility of the contractor to make periodic replacements/replenishments of system capacities to ensure annual guaranteed system ratings, if and when required, up to the Term of the Contract. Outage time as a result of replacement will also be counted as an “Accountable BESS Outage” for the purpose of computing BESS Availability. | Periodic Checking … The test should confirm that the measured value matches or higher than the desired available energy of the system. Calculations in this regard shall be performed by the Contractor and validated by Employer. In detailed Engineering all such calculation procedure shall be provided by the Contractor and shall be approved by Employer. |
|  | - General, Technical Specification: Section-Project Rev-00 | …. m) Insurance and other requirements for the BESS in accordance with the provisions of general conditions of contract of the bidding document. | …. m) Insurance and other requirements for the BESS. n) Operation and comprehensive maintenance of complete BESS part under its scope from date of commissioning of full project capacity. |
|  | 7.15.1 Third Party Verification Technical Specification: Section-Project Rev-00 | …APTRANSCO / DISCOMs / SLDC /CEA /MoP/MNRE and/or their designated third party may verify the construction works/operation of the Project being carried out by the contractor and if it is found that the construction works/operation of the Project is not as per the Prudent Utility Practices, POWERGRID may seek clarifications from contractor or require the works to be stopped or to comply with the instructions of such third party. | …APTRANSCO / DISCOMs / SLDC /CEA /MoP/MNRE and/or their designated third party may verify the construction works/operation of the Project being carried out by the contractor and if it is found that the construction works/operation of the Project is not as per the Prudent Utility Practices, Employer may seek clarifications from contractor or require the works to be stopped or to comply with the instructions of such third party. |
|  | 7.16.2 Synchronization & Trial Run Technical Specification: Section-Project Rev-00 | … II. Copy of Connectivity Details Installation report duly signed by the POWERGRID. … VII Affidavit certifying that the Contractor has obtained all the necessary approvals for commencement of power supply from the Project, and indemnifying POWERGRID, APTRANSCO and DISCOMs against any discrepancies in the above details. … | … II. Copy of Connectivity Details Installation report duly signed by the Employer. … VII Affidavit certifying that the Contractor has obtained all the necessary approvals for commencement of power supply from the Project, and indemnifying Employer, APTRANSCO and DISCOMs against any discrepancies in the above details. … |
|  | 10.0 Grid Compliance Requirements | …. vi) Bidder should submit Dynamic model of Grid studies including IBR (Inverter Based Resources) for approval of POWERGRID prior to submission to RLDC/SLDC. Bidder shall submit above documents within 3 months from LoA. However, the final requirement or any other requirement shall be as per RLDC/SLDC. The simulation study has to be carried out as per POI data (like SCR, X/R etc.) by bidder based on data shared by POWERGRID/RLDC/SLDC/CTU. … viii) Bidder shall measure harmonic content, DC injection and flicker at least once in a year in line with the provisions mentioned as per CEA Technical Standards for Connectivity to the Grid, 2007. Bidder shall ensure that the power quality values at POI are within the limit specified as per CEA Technical Standards for Connectivity to the Grid, 2007. This measurement shall be done every year till the completion of O&M and report shall be submitted to RLDC/SLDC/POWERGRID for verification to ensure compliance. | …. vi) Bidder should submit Dynamic model of Grid studies including IBR (Inverter Based Resources) for approval of Employer prior to submission to RLDC/SLDC. Bidder shall submit above documents within 3 months from LoA. However, the final requirement or any other requirement shall be as per RLDC/SLDC. The simulation study has to be carried out as per POI data (like SCR, X/R etc.) by bidder based on data shared by Employer/RLDC/SLDC/CTU. … … viii) Bidder shall measure harmonic content, DC injection and flicker at least once in a year in line with the provisions mentioned as per CEA Technical Standards for Connectivity to the Grid, 2007. Bidder shall ensure that the power quality values at POI are within the limit specified as per CEA Technical Standards for Connectivity to the Grid, 2007. This measurement shall be done every year till the completion of O&M and report shall be submitted to RLDC/SLDC/Employer for verification to ensure compliance. |

***