## Sheet1
Amendment No.- II to the Bidding Documents for Package Substation Package SIK-SS01 for (i) 220/132kV Legship Pool (New) s/s, (ii) 132/66/11kV Dikchu pool (new) s/s, (iii) 66/11kV Makha (New) s/s, (iv) 66/11kV Temi (New) s/s, (v) 66/11kV Khamdong (New) s/s, (vi) 66/11kV Kumrek (New) s/s, (vii) 66/11kV Namthang (New) s/s, (viii) 66/11kV Rorathang (New) s/s & (ix) 66/11kV Mamring s/s Extn. associated with Comprehensive Scheme for Strengthening of Transmission and Distribution System in Sikkim. [Spec. No.: CC-CS/93-NER/SS-4007/3/G2]
Sl. No. | Clause No. /Doc. Ref. | Existing Provisions of the Bidding Documents | Amended as
1 | LD&C Section Section 2.3.1.1, Vol -II Part-11 | LD&C Section Section 2.3.1.1 Functional Requirement There is a requirement for different types of equipment under this project which are described in this section. The BOQ is provided in the appendices. For the purpose of BOQ, the SDH Equipment is considered to be divided in three parts i.e. Optical interface/SFP, Tributary Cards (Electrical tributaries such as E1 & Ethernet 10/100 Mbps) and Base Equipment (Consisting of Common Cards, Control Cards, Optical base card, Power supply cards, sub-rack, cabinet, other hardware and accessories required for installation of equipment i.e. everything besides optical interface/SFP and tributary cards). If bidder is offering equipment with multifunction cards such as cross-connect or control card with optical interface/SFP or tributary interface, such type of multifunction card shall be considered as Common control card and shall be the part of base equipment. In case optical interface/SFP is embedded with control card, the adequate number of optical interface/SFPs shall be offered to meet the redundancy requirements of the specifications. Further, control card and optical base card shall not be equipped with more than two optical interface/SFPs. The equipment shall be configurable either as Terminal Multiplexer (TM) as well as MADM (Multi Add-drop multiplexer) with software settings only. | LD&C Section Section 2.3.1.1 Functional Requirement There is a requirement for different types of equipment under this project which are described in this section. The BOQ is provided in the appendices. For the purpose of BOQ, the SDH Equipment is considered to be divided in three parts i.e. Optical interface/SFP, Tributary Cards (Electrical tributaries such as E1 & Ethernet 10/100 Mbps) and Base Equipment (Consisting of Common Cards, Control Cards, Optical base card, Power supply cards, sub-rack, cabinet, other hardware and accessories required for installation of equipment i.e. everything besides optical interface/SFP and tributary cards). If bidder is offering equipment with multifunction cards such as cross-connect or control card with optical interface/SFP or tributary interface, such type of multifunction card shall be considered as Common control card and shall be the part of base equipment. In case optical interface/SFP is embedded with control card, the adequate number of optical interface/SFPs shall be offered to meet the redundancy requirements of the specification Further, main & protection Channel shall be terminated on separate cards and there should be no Single point of faliure The equipment shall be configurable either as Terminal Multiplexer (TM) as well as MADM (Multi Add-drop multiplexer) with software settings only.
2 | Clause 22.2, Section-V, SCC, Vol-I of the bidding documents | Replace the first para of GCC Sub-Clause 22.2 with the following: “The Defect Liability Period shall be as under: (i) Sixty (60) months for (132kV/220kVclass) Transformer /Current Transformer/ Capacitive Voltage Transformer / Circuit Breaker from the date of Taking Over /Completion of Facilities (or any part thereof). For the purpose of this clause, the Measurable Defects as per the Technical Specifications shall also be considered for Transformer /Current Transformer/ Capacitive Voltage Transformer / Circuit Breaker. (ii) Twenty Four (24) months from the date of Taking Over/Completion of Facilities for all equipment/materials other than those specified in (i) above.` (iii) Twelve (12) months from the date of Taking Over/Completion of Facilities for all items other than those specified in (i) & (ii) above. | Replace the first para of GCC Sub-Clause 22.2 with the following: “The Defect Liability Period shall be as under: (i) Sixty (60) months for (132kV/220kVclass) Transformer /Current Transformer/ Capacitive Voltage Transformer / Circuit Breaker from the date of Taking Over /Completion of Facilities (or any part thereof). For the purpose of this clause, the Measurable Defects as per the Technical Specifications shall also be considered for Transformer /Current Transformer/ Capacitive Voltage Transformer / Circuit Breaker. (ii) Twenty Four (24) months from the date of Taking Over/Completion of Facilities for all other equipment/materials (i.e. equipments/materials as mentioned in Schedule-1 other than those specified in (i) above).` (iii) Twelve (12) months from the date of Taking Over/Completion of Facilities for all items other than those specified in (i) & (ii) above.