## Bidder Queries
Clarification No.–IV to the bidding documents for Package Substation Package SIK-SS01 for (i) 220/132kV Legship Pool (New) s/s, (ii) 132/66/11kV Dikchu pool (new) s/s, (iii) 66/11kV Makha (New) s/s, (iv) 66/11kV Temi (New) s/s, (v) 66/11kV Khamdong (New) s/s, (vi) 66/11kV Kumrek (New) s/s, (vii) 66/11kV Namthang (New) s/s, (viii) 66/11kV Rorathang (New) s/s & (ix) 66/11kV Mamring s/s Extn. associated with Comprehensive Scheme for Strengthening of Transmission and Distribution System in Sikkim. [Spec. No.: CC-CS/93-NER/SS-4007/3/G2]
Sl. no. | Volume / Section | Clause No. | Description | Bidder's Query | POWERGRID Reply
I
1 | - | - | Short Circuit Current Rating | In line with various clause of specification and Equipment rating , we understand that short circuit current rating shall be as :- 1) 220kV system - 40kA for 1 sec. 2) 132kV System - 31.5kA for 1 sec. 3) 66kV System - 31.5kA for 1 sec. 4) 33kV System - 25KA for 1 sec. 5) 11kV System - 25KA for 1 sec. Please confirm. | Please refer GTR, Rev. 14. Short circuit current rating shall be as follows: 1) 220kV system - 40kA for 1 sec. 2) 132kV System - 31.5kA for 1 sec. 3) 66kV System - 31.5kA for 3 sec. 4) 33kV System - 25KA for 3 sec. 5) 11kV System - 25KA for 3 sec.
2 | Bid Price Schedule, Sch-1 & Lighting Specification Rev.07 | BPS Item No.79, 80, 81, 82, 83 & 84 and Specification Rev.07 clause No. :- Annexure-II. | Lighting Fixture type-SF1, SF2, SF4, SF5, SC, & S-LED as per specification. | Please define and describe the SF1, SF2 , SF4, SF5, SC, & S-LED type fixtures as the details are missing in specification. | Please refer Sr No. 1,2,3,4,5,6,7,8 & 9 of Amendment No. III.
3 | Bid Price Schedule, Sch-1 & Lighting Specification Rev.07 | BPS Item No. 95 Clause no. 9 of Major Changes in Technical Specification Lighting System (Rev.07 w.r.t. Rev.06) | Occupancy sensors and other accessories as required for control of Lighting in the stairs area and corridors of control room cum administrative building as per specification. & 9. Use of Occupancy Sensor has been deleted. | Occupancy Sensor has been deleted as per latest specification while it is envisaged as per BPS. Please clarify. | Please refer Sr No. 1,2,3,4,5,6,7,8 & 9 of Amendment No. III.
4 | Metrological data |  | Minimum ambient temperature. | Please furnish the minimum ambient temperature of all the sites under this package. | Please refer Cl. No. 5.0 of section project in Technical Specification.
5 | Bid Price Schedule, Sch-1 & Lighting Specification Rev.07 | BPS Item No. 88 & Lighting Specification Rev.07 clause no. 7 (Major Changes in Technical Specification Lighting System (Rev.07 w.r.t. Rev.06) | Solar based street lighting pole including solar panel as per technical specifications. & Considering maintenance issue of Pole mounted battery, Solar Panel along with battery used for Street Lighting System has been deleted and Street Lighting using LED Luminaries is retained. | Please provide the specification for referred item as this has been deleted in the latest Lighting Specification Rev.07 clause no. 7. | Please refer Sr No. 1,2,3,4,5,6,7,8 & 9 of Amendment No. III.
6 |  | Dikhu S/S, Makha (New) substation, Temi S/S | 11kV Lighting arrester. | We understand that no GIS and AIS type lighting arrester considered for the LT transformer / incoming feeder bays. Please confirm. | 9kV Surge Arrester has been considered for 11kV Feeders. Bidder is to quote as per BPS.
7 | Bid Price Schedule, Sch-1 | Dikchu Pool Substation, Temi S/S, Makha S/S, Kmrek S/S, Rorarthang S/S, Namthang S/S, Khemdong S/S | 11KV XLPE CABLE TERMINATION EQUIPMENT ALONG WITH STRUCTURE ACCESSORIES FOR OUT DOOR TERMINATION (ONE SET CONSISTS OF COMPLETE & REQUIREMENT FOR ONE BAY) | We understand that there shall be single run of 3X300Sqmm or 3Cx185Sqmm Cable / feeder. Please confirm . | Bidder is to quote as per BPS.
8 | Conductor Details | GENERAL | - | Request you to provide the 66kV & 11kV Line side conductor details for Temi S/S, Makha S/S, Kumrek S/S, Rorarthang S/S, Namthang S/S, Khemdong S/S. | For 66kV: Single Dog Conductor For 11kV: Single Rabbit Conductor
9 | Section Project Cl.No. 3.1.2.(I).(h) Price Schedule SS01 | FOTE System | Digital protection coupler (DPC) along with Cabling between DPC & Communication equipment (for E1 interface) for both end of the following 132kV lines are considered at substation of other end, in separate package. However necessary coordination for wiring between DPC & Relay & protection panel shall be in the present scope. o Dikchu Pool –Singhik 132kV D/C line o Dikchu Pool -Rangpo (Samardong) (GIS) 132kV D/C line o Dikchu Pool –132kV Parbing D/C line | As per Section Project DPC is to be offered for following links: o Dikchu Pool –Singhik 132kV D/C line o Dikchu Pool -Rangpo (Samardong) (GIS) 132kV D/C line o Dikchu Pool –132kV Parbing D/C line However, asper Price Schedule no DPC Quantities are mentioned. Request you to amend the price schedule with DPC quantities required for links from Dikchu Pool S/S. | Bidder is to quote as per BPS. Please refer section project in Technical Specification.
10 | Price Schedule-SS01 , S.no. IX.1075 Section Project Cl. 3.2.1.9.(d) Section Project- Cl. 4 | FOTE System | RTU Augmentation at 66/11kV Mamring S/S (d) All required I/O points from the bays under present scope shall be wired to existing RTU (Make & Model shall be intimated during detail engineering) for sending data to SLDC/ERLDC. Specific Exclusions: (e) I/O module for existing RTU, modification of existing RTU data base, software configuration etc as required for integration of all bays (under present scope) with existing RTU for sending data to SRLDC/ERLDC (f) Modification of data base at SLDC/ERLDC | Please confirm make & model of existing RTU at 66kV Mamring S/S. As per Section Project Cl.4 ,we understand that Augmentation of existing RTU by addition of I/O Card, database modification at S/S end & Control Centre end is excluded from bidders scope. In view of the same, we request you to delete scope of RTU Aumentation at 66kV Mamring S/S from price schedule. | Bidder is advised to visit the site and acquaint themselves.
11 | Price schedule sch-1 and Sch-3 | Sch-1 Item no 118, 119 & 141 and Sch-3 Item no 51,52 & 74 | Non standard structure, 33 kv equipment | We understand that the referred items shall be used for non standard structure such as tertiary and neutral formation etc. Please confirm. | Non standard structures for 33 kv equipment shall be used as tertiary and neutral formation etc.
12 | Price schedule, sch-3, item no 114 and General arrangement & Electrical Layout Plan | Item no 114 and Drg no C/ENGG/ER/SIK/COMP-SCH/LEG/GE/01 | Switchyard Road | As per Price schedule and cross section drawing, road shall be concrete road. However, in proposed tender layout, its has been menteioned "Black Topping Road ". We understand that BPS shall be prevail and road shall be cement concrete. Please confirm . | Road shall be cement concrete and items are executed as per BPS
13 | Section Project | Cl.no 3.2.1.2, point iii j | Design, Engineering & Civil works (as per contractor supplied Drawings) for: (j)R.C.C. retaining wall | We understand that RCC retaining wall is in bidder scope and same shall be paid as per BPS in relevant head i.e. excavation,PCC,RCC ,Reinforcement steel, However Weep hole ( PVC pipe), & fillter media shall be amended and paid separatly. Please confirm . | Weep hole ( PVC pipe), & fillter media shall be amended and paid separatly under the following items:-
[5 empty] | Item Description:- |  | Unit | Unit Rate | Qty | Amount | Remark
[5 empty] | 1) Providing and fixing 100mm UPVC pipes conforming to IS : 15328, for weep holes (Activity number-170002803) | for Dikchu | M |  | 96
[6 empty] | for Legship Pool | M |  | 96
[6 empty] | for Kumrek | M |  | 48
[6 empty] | for Makha | M |  | 48
[6 empty] | for Temi | M |  | 48
[6 empty] | for Namthang | M |  | 48
[6 empty] | for Khamdong | M |  | 48
[6 empty] | for Rorathang | M |  | 48
[6 empty] | for Mamring extn | M |  | 20
[5 empty] | 2) Providing & Filling filter media with coarse aggregate confined in chicken mesh-(Activity number-170002158) | for Dikchu | EA |  | 60
[6 empty] | for Legship Pool | EA |  | 60
[6 empty] | for Kumrek | EA |  | 30
[6 empty] | for Makha | EA |  | 30
[6 empty] | for Temi | EA |  | 30
[6 empty] | for Namthang | EA |  | 30
[6 empty] | for Khamdong | EA |  | 30
[6 empty] | for Rorathang | EA |  | 30
[6 empty] | for Mamring extn | EA |  | 12
14 | Section Project and Civil Works Rev 11A | Civil works and Cl.no 3, point no iv,v,vi,vii & viii Page 13 of 80 | vi) All foundation drawings including foundations for buildings, towers, equipments etc shall be released to the Contractor after award in a phased manner, after receiving the geotechnical investigation report. v) Drawings for transformer, reactor foundations and fire walls are not enclosed and shall be made available to the successful bidders by the Employer during detailed engineering. vi) In case the site conditions warrant any special type of foundations to be used, the same shall be designed and issued by the Employer to the Contractor during detailed engineering unless otherwise mentioned in section project. vii) Drawings for any non-standard tower or equipment and their foundation, if required, shall be designed by the Employer and made available to the Contractor during detailed Engineering unless otherwise mentioned in section project. viii) Drawings that have been mentioned and to be issued by the Employer to the Contractor during detailed Engineering shall be made available to the Contractor as per the agreed work schedule finalized after award | We understand that all building including control room building, FFPH building, water tank, Switchyard panel room & security room shall be executed as per provided tender drawing and also foundation part shall be designed by employer and made available to the contractor. Please confirm . | Construction drawings for control room building, FFPH building, water tank, Switchyard panel room & security room shall be available to the contractor by employer.
15 | Section project | Cl. 13.34 | The length of 100mm dia MS pipe for rain water harvesting as per construction drawing shall be decided as per depth of underground water table and construction drawing of Rain water harvesting | Keeping in view the hilly terrain of all sites , we have considered the depth of MS Pipe,10m (max) from the proposed FGL for rain water harvesting , Please confirm. | The depth of MS Pipe shall be 18m (max) from the proposed FGL for rain water harvesting ,
16 |  | CRP SAS |  | Please provide the CRP SAS specification for 66KV System . | Bidder is to quote as per provisions of bidding documents.
17 |  | CRP SAS |  | Please confirm that combined Bay control cum Protection unit (BCPU) are acceptable for 33kV and 66kV level. | Bidder is to quote as per provisions of bidding documents.
18 |  | CRP SAS |  | For 66kV, there is no CBR panels, we understand all the 66kV (SAS based panels) shall be having BCU/BCPU and protection relays mounted in a single vertical. | Bidder is to quote as per provisions of bidding documents.
19 |  | CRP SAS |  | We understand that no Busbar and no standalone LBB is required for 66kV. Please confirm. | Confirm.
20 | 220/132kV Legship Pool Substation | BPS Item No.13 | As per BPS, total Qty. of 245kV, 1600A, 40 KA, 3-phase Double Break Tandem Isolator without E/S is 5 EA. | As per layout , total qty. of 220kV tandem isolators shall be 9 nos. Please revise the bid price schedule. | Bidder is to quote as per BPS.
21 | 220/132kV Legship Pool Substation | BPS Item No.23 | As per BPS, total Qty. of 145 kV, 1250 A, 31.5KA, 3-phase Double Break Isolator without E/S (Tandem) is 6 nos. | As per layout , total qty. of 132kV tandem isolators shall be 5 nos. Please revise the bid price schedule. | Bidder is to quote as per BPS.
22 | 220/132kV Legship Pool Substation | BPS Item No.230 | As per BPS, total Qty. of 220kV, 1600A, 0.5mH, 40 kA Line Trap total qty. is 2 nos. | As per layout, total qty. of 220kV wave trap shall be 4 nos. for two nos. of line bays. Please revise the bid price schedule. | Bidder is to quote as per BPS.
23 | 220/132kV Legship Pool Substation | BPS Item No.235 | As per BPS, total Qty. of 132kV,1250A,0.5mH , 31.5kA Line Trap total qty. is 2 nos. | As per layout, total qty. of 132kV wave trap shall be 6 nos. for three nos. of line bays. Request you to revise the bid price schedule. | Bidder is to quote as per BPS.
24 | General arrangement Layout and Electrical Layout Plan.(C/ENGG/ER/SIK/COMP-SCH/LEG/GA/01) & Electrical Section Layout (C/ENGG/ER/SIK/COMP-SCH/LEG/SECTION/01) | 220/132kV Legship Pool Substation | 220kV and 132kV Main and Transfer bus conductor details. | There is a discrepancy between section Layout and general arrangement layout for bus bar conductor . We understand that main and transfer bus bar rating shall be as following :- 1. 220kV Main Bus Bar - Twin Moose. 2. 220kV Transfer Bus Bar - Single Moose. 3. 132kV Main Bus Bar - Twin Moose. 4. 132kV Transfer Bus Bar - Single Moose. Equipments interconnection and jack bus bar shall be as per Layout and section drawing. Please confirm. | Confirm.
25 | General arrangement Layout and Electrical Layout Plan.(C/ENGG/ER/SIK/COMP-SCH/LEG/GA/01) & Single line diagram (C/ENGG/ER/SIK/COMP-SCH/LEG/SLD/01) | 220/132kV Legship Pool Substation | 220kV & 132kV bus bar for future bays. | There is a discrepancy between section Layout and single line diagram for bus bar for future bays. As per SLD, no buses are envisaged for future bays but as per layout, it is shown for 220kV bays ( ICT-3 and 2 nos. future line bays). Please confirm . | Bidder is to quote as per BPS.
26 | Electrical Section Layout (C/ENGG/ER/SIK/COMP-SCH/LEG/SECTION/01) | 220/132kV Legship Pool Substation | - | From the referred drawings, we understand that 220kV line side conductor shall be single zebra. Please confirm. Please also provide the conductor details of 132kV Line side . | 220kV Line side: Twin Moose 132kV Line Side: Single Panthar
27 | 220/132kV Legship Pool Substation | BPS Item No. 40 | 220kV Circuit Breaker Relay Panel with Auto Reclose (with Automation) | As per Price schedule, 4 no’s 220kV Circuit Breaker Relay Panel with Auto Reclose (with Automation) are required at legship pool substation. However, as per SLD , total 3 no’s of 220kV Circuit Breaker Relay Panel with Auto Reclose (with Automation) is required. Please revise the price schedule. | Bidder is to quote as per BPS.
28 | 220/132kV Legship Pool Substation | Clause No: 3.1.1_B | 220/132kV Legship Pool (New) Substation with the following bays: 01 no. 220kV Bus Coupler bay | One number of 220kV buscoupler Protection Panel (with Automation) at legship pool substation is not considered in BPS. Please revise the BPS. | Bidder is to quote as per BPS.
29 | 220/132kV Legship Pool Substation | Clause No: 3.1.1_B | 220/132kV Legship Pool (New) Substation with the following bays: 01 no. 220kV Transfer Bus Coupler bay | One number of 220kV Transfer buscoupler Protection Panel (with Automation) at legship pool substation is not considered in BPS. Please revise the BPS. | Bidder is to quote as per BPS.
30 | 220/132kV Legship Pool Substation | BPS Item No. 41 | 220kV Circuit Breaker Relay Panel without Auto Reclose (with Automation) | Price schedule asks for 2 no’s 220kV Circuit Breaker Relay Panel without Auto Reclose (with Automation) . But as per SLD & Project requirement ,total 3 no’s of 220kV Circuit Breaker Relay Panel without Auto Reclose (with Automation) is required. Please revise the price schedule. | Bidder is to quote as per BPS.
31 | 220/132kV Legship Pool Substation | Clause No: 3.1.1_B | 220/132kV Legship Pool (New) Substation with the following bays: 01 no. 132kV Transfer Bus Coupler bay | One number of 132kV Transfer buscoupler Protection Panel (with Automation) at legship pool substation is not considered in BPS. Please revise the BPS. | Bidder is to quote as per BPS.
32 | 220/132kV Legship Pool Substation | BPS Item No. 209 & 210 | SECONDARY RELAY INJECTION TESTING KIT & Relay Test kit | We understand that bidder shall consider Relay test kit as per CRP rev 09 specification Clause No 36. Hence separate secondary relay injection testing kit & relay test kit is not envisaged. Please confirm. | Bidder is to quote as per provisions of bidding documents.
33 | 220/132kV Legship Pool Substation | BPS Item No. 39 & 47 | 220kV & 132kV Bus Bar Protection Panel (Single)-(with Automation) | We understand that scope of Busbar protection required for 220kV & 132kV at Legship pool substation is limited to bays under present scope. Busbar protection for future bays is not in bidder scope of supply. Please confirm . | Bidder is to quote as per provisions of bidding documents.
34 | 220/132kV Legship Pool Substation | Clause No: 3.2.1.2_I of f,g & h | 220/132kV Legship Pool (New) Substation PLCC for 220kV & 132kV | We understand that Remote and local end PLCC equipments required for line bays under present scope at legship substation shall be in bidder scope of supply. Please confirm . | Confirm. Bidder is to quote as per provisions of bidding documents.
35 | 220/132kV Legship Pool Substation | S.No. N. 70 | HVW Spray System. Hydrant system and complete U/G, & O/G Piping and Accessories etc outside the Pump House for 33.3 MVA, 220/132/11 KV, 1 Phase Auto transformer. | We understand that quantity indicated as 6 sets should be replaced with 7 sets. Please confirm. | Bidder is to quote as per BPS.
36 | General arrangement Layout and Electrical Layout Plan.(C/ENGG/ER/SIK/COMP-SCH/DCK/GA/01) | 132/66/11kV Dikchu Pool Substation | Wave trap | As per layout all 132kV Line shown with wave trap but No PLCC and wave trap item considered in the BPS. Please clarify . | Bidder is to quote as per BPS.
37 | Single line diagram (C/ENGG/ER/SIK/COMP-SCH/DCK/SLD/01) & 33kV & 11kV Indoor switchgear (GIS type) for 132/66/11kV Dikchu Pool Substation | Clause No. 9.8 of section -33kV & 11kV Indoor switchgear (GIS type) | Bus bar rating of 11kV Indoor GIS. | 11kV Switchgear rating (GIS type) bus bar rating is following : - 1. as per SLD-25kA for 1 sec. 2. as per GTR clause no. 4.6 - 25kA for 3 sec. 3. As per 33kV & 11kV Indoor switchgear (GIS type) clause no. 9.8 - 25 kA (rms) for one (1) sec. Please confirm the actual requirement. | Short circuit current rating for 11kV Switchger is 25kA for 3 Sec.
38 | 132/66/11kV Typical Electrical Section Plan for New (C/ENGG/ER/SIK/COMP-SCH/SECTION/01 sheet 1 & 2) | 132/66/11kV Dikchu Pool Substation | - | Please furnish the 132kV, 66kV and 11kV Line side conductor details. | 132kV Line side: Single Panther 66kV Line side: Single Dog
39 | 132/66/11kV Dikchu Pool Substation | BPS Item No. 381, 382 & 383. | 66KV, 1-CORE, 95 SQ.MM XLPE AL CABLE ALONGWITH ACCESSORIES ETC. | Please clarify the requirement of 66kV XLPE cable and associated accessories etc. Please also provide the specification for 66kV 95Sqwmm XLPE cable and termination kit. | Bidder is to quote as per provisions of bidding documents.
40 | 132/66/11kV Dikchu Pool Substation | Clause No: 3.1.1_A | 132/66/11kV Dikchu Pool (New) Substation with the following bays: 01 no. 132kV Bus Coupler bay | One number of 132kV buscoupler Protection Panel (with Automation) at Dikchu pool substation is not considered in BPS. Please revise the BPS. | Bidder is to quote as per BPS.
41 | 132/66/11kV Dikchu Pool Substation | BPS Item No.287 | 132kV Bus Bar Protection Panel (Single)-(with Automation) | We understand that Scope of Busbar protection required for 132kV at Dikchu pool substation is limited to bays under present scope. Busbar protection for future bays is not in bidder scope of supply. Please confirm . | Bidder is to quote as per provisions of bidding documents.
42 | 132/66/11kV Dikchu Pool Substation | BPS Item No.413 | Complete Substation automation System for 66kV bay as per TechnicalSpecification | Price schedule asks for 6 no’s Complete Substation automation System for 66kV bays at Dikchu pool substation. But as per SLD & Project requirement ,total 5 no’s complete Substation automation System for 66kV bays is required. Please revise the price schedule. | Bidder is to quote as per BPS.
43 | 132/66/11kV Dikchu Pool Substation | Clause No: 3.1.1_A | 132/66/11kV Dikchu Pool (New) Substation with the following bays: 2 nos. 66kV Transformer bays for installation of 2 Nos. 5MVA, 66/11 kV, 3 Phase Power Transformers. | Since, two number of 66kV(5MVA) Transformer bays Protection Panel (with Automation) at Dikchu pool substation is not considered in BPS. We understand that same is excluded from bidder scope of supply. Please confirm . | Bidder is to quote as per BPS.
44 | 132/66/11kV Dikchu Pool Substation | Clause No: 3.2.1.1_h | 132/66/11kV Dikchu Pool (New) Substation (h) Digital protection coupler (DPC) along with Cabling between DPC & Communication equipment (for E1 interface) for both end of the following 132kV lines are considered at substation of other end, in separate package. However necessary coordination for wiring between DPC & Relay & protection panel shall be in the present scope. | We understand that PLCC equipment for both end of the 132kV lines at Dikchu pool substation is not in bidder's scope Please confirm . | Confirm. Bidder is to quote as per provisions of bidding documents.
45 | General | Extension of 66/11kV Mamring substation | General arrangement layout. | Request you to provide the general arrangement layout of 66/11kV Mamring substation. | Bidder is advised to visit the site and acquaint themselves.
46 | Extension of 66/11kV Mamring substation | Clause no. 3.2.1.9 (e) | (e) Bus extension for bays under present scope, for two bays (existing 66kV Bus is with single ACSR Panther conductor). | From the refer clause, we understand that bus bar extension for 2 nos. bays are under present scope of work but no line item of "erection h/w" is considered in the BPS. Request you to provide the line item for same. | Erection hardware for bus bar extension is covered under line item no. 1052 in BPS.
47 | Extension of 66/11kV Mamring substation | Clause no. 3.2.1.9 (h) | (h) Lighting and Illumination for the extended switchyard area. | We understand that sufficient and adequate feeders available in the existing MLDB and ELDB for present scope of work. Please confirm. | Bidder is to quote as per BPS.
48 | Extension of 66/11kV Mamring substation | Clause no. 1041&1042. | ACDB & DCDB Extension. | we understand that adequate feeders available in the existing ACDB and DCDB to connect the extension board. Please confirm. | Bidder is to quote as per BPS.
49 | Extension of 66/11kV Mamring substation | BPS Item No.1053 & 1054. |  | we understand that all cable required for power and control work shall be operated form the item no. 1055 to 1066. Please describe the item no. 1053 & 1054. | Please refer S.No. 10 of Amendment No. III. However, cable requirement shall be covered under item no. 1053 & 1054.
50 | Extension of 66/11kV Mamring substation |  | Earthing System &Cable Trench Layout. | Request you to provide the existing earthmat layout, details of earthing conductor etc. Please also provide the layout of existing cable trench. | Bidder is advised to visit the site and acquaint themselves.
51 | Extension of 66/11kV Mamring substation |  | Control relay panel. | We understand that sufficient space available in the control room building to place the control and relay panel of present scope. Please confirm. | Bidder is advised to visit the site and acquaint themselves.
52 | Extension of 66/11kV Mamring substation | - | Bus PT | We understand that Bus PT Input is available in the Relay and Control Panel of existing bays. Same shall be looped for present scope line Bay. Please confirm. | Bidder is advised to visit the site and acquaint themselves.
53 | Extension of 66/11kV Mamring substation | - | Protection against lightening. | Please provide the details of existing lightening system. Further there is no item envisaged in BPS. We understand that area under present scope is already protected from lightning by existing lightening system. Please confirm. | Bidder is advised to visit the site and acquaint themselves.
54 | Extension of 66/11kV Mamring substation | - | Structure & Tower. | We understand that exiting adjacent bay tower is suitable for extension. Please confirm. | Bidder is advised to visit the site and acquaint themselves.
55 | Extension of 66/11kV Mamring substation | Clause No: 3.2.1.9_I_(c) | 66kV Mamring Substation (Extension) Bidder shall be required to match Control & Relay panel with the existing panel. | Please provide make and model of existing control and relay panel details. | Bidder is advised to visit the site and acquaint themselves.
56 | Vol-II_Part 11/Section Project Final | Clause No: 3.3 | Design, engineering, manufacture, testing, supply to site, including transportation & insurance, unloading, storage, erection, testing and commissioning of the Fiber Optic based Communication equipment for all substations are covered under substation package –SIK-SS-01. The list of substations for which those equipment’s are envisages is enclosed at Annexure-IX(R-1). | we understand that Annexure-IX(R-1) mentioned in referred clause shall be replaced with ANNEXURE-VIII(R-1). Please confirm. | Confirm.
57 | Vol-II_Part 11/Section Project Final | Clause No: 4.0_(f) | SPECIFIC EXCLUSIONS Modification of data base at SLDC/ERLDC | We understand that Substation automation system at (1) 220/132kV Legship Pool (New) s/s, (2) 132/66/11kV Dikchu pool (new) s/s, (3) 66/11kV Makha (New) s/s, (4) 66/11kV Temi (New) s/s (5) 66/11kV Khamdong (New) s/s, (6) 66/11kV Kumrek (New) s/s, (7) 66/11kV Namthang (New)s/s, (8) 66/11kV Rorathang (New) s/s bays under present scope is limited to substation end gateway only. SAS integration at SLDC/ERLDC is excluded from the bidder scope of supply. Please confirm . | Bidder is to quote as per provisions of bidding documents.
58 | Extension of 66/11kV Mamring substation | Cl. No 3.2.1.9 I point no f | Galvanised Lattice and pipe structures for towers, beams, LMs and equipment support structures as per BPS. CB support structure shall be as per CB manufacturer’s design. The design/drawings/BOM of 66kV and 11 kV towers/beams and equipment supporting structures matching with the existing switchyard structures for extension substation shall be in the scope of the Contractor. For connection of proposed gantry with existing gantry structure, the bidder is required to visit the existing substation for ascertain suitability of existing tower for taking additional load for extension and tower-beam connection and verifythe same at their own as no drawing of existing gantry structures is available with POWERGRID. | If existing gantry is not capable to taking load for proposed extension, the existing structure to be dismantled by PGCIL, since dismatling item is not included in tender price schedule. If no, please add suitable line item in bid price schedule. | Bidder is advised to visit the site and acquaint themselves.
59 | Extension of 66/11kV Mamring substation |  | Dismatling of existing foundations | We understand that there is no dismtaling/moification/ refurbishment work is envisaged on existing foundation . Since the same is not found in tender BOQ. Please confirm . If yes, please include the line item in BOQ. | Bidder is advised to visit the site and acquaint themselves.
60 | Extension of 66/11kV Mamring substation | Cl.no 3.2.1.9 iii point c | (iii)Design, Engineering & Civil works (as per contractor supplied Drawings) for:(c)Drainage system as required in the substation including culverts. It shall match with the existing drainage system | We understand that drainage system is in bidder's scope. However relavant line item is not included in tender price schedule. Please amend same in price schedule. | Bidder is advised to visit the site and acquaint themselves.
61 |  |  |  | Please provide co-ordinates for all sites under this package. | Bidder is advised to visit the site and acquaint themselves.
62 |  |  |  | We have done the route survey for sites and noticed that roads are damaged at various places and not suitable for transportation. We understand that PGCIL shall take up with Govt autorities to repair the roads before notification of award. | Bidder is to quote as per provision of Bidding documents.
63 | Spares |  |  | 5MVA transformers is in scope of Temi S/S but spares have been asked for 10MVA transformers instead of 5 MVA transforners in section project . Please correct . | Bidder is to quote as per BPS.