## Sheet1 (hidden)
sr | discription | height | weidth | debth |  |  | height | weidth | debth
1 | foundation
| a (base ) | 100 | 600 | 600 | 36000000 | 0.036 | 0.32895 | 1.9737 | 1.9737 | 1.2814 | 1.2814
| b (rcc base) | 100 | 500 | 500 | 25000000 | 0.025 | 0.32895 | 1.6447 | 1.6447 | 0.88986 | 0.88986
| c (pillar ) | 600 | 300 | 300 | 54000000 | 0.054 | 1.9737 | 0.98684 | 0.98684 | 1.9221 | 1.9221
[6 empty] | 0.115 |  |  |  | 4.0933 | 4.0933

## measurement book (hidden)
sr no | description of item | no | length | breadth | height | quantity
1 | excuvation
2
3

## abstract sheet (hidden)
sr no | description of item | qty | unit | RATE | AMOUNT

## Sheet2 (hidden)
| Project Name |  | BBS: Fire Fighting Pipe laying and repairing
Client
|  |  |  | Spacing @c/c (mm) | [8 empty] | No's of Bend | Length Deduct ion (mm) | Cutting length (mm) |  | Nos of bars |  |  | No's of Fire Fighting columns
Sr. No | Particular | Bar Mark | Dia of bar(mm) |  | Shape and size | a | b | c | d | e | f | Length (mm) |  |  |  | No's |  | Total Length | Unit Weight |  | Total Weight | 8 mm
Fire Fighting Columns
1 | Raft | Main Bars | 8 | 150 | 50 50 | 50 | 400 | 50 |  |  |  | 500 | 2 | 32 | 468 | 1 | 4 | 1.87 | 0.395 | 178 | 131.6 | 131.64
[5 empty] | 400 | [11 empty] | 8 | 4 |  | 178 |  |  | 281.24
50
Column
2 | 300 mmx | vertical bars | 8 |  | 600 | 50 | 600 | 100 |  |  |  | 750 | 2 | 32 | 718 | 1 | 4 | 2.872 | 0.395 | 178 | 202 | 202 | 202
300 mm
100
80 250
| Col Main Ring | 300 mmx 300 mm |  |  | 80
3 |  |  | 8 | 150 | 250 250 | 250 | 250 | 250 | 250 | 80 | 80 | 1160 | 5 | 80 | 1080 | 1 | 5 | 5.4 | 0.395 | 178 | 379.7 | 379.7 | 379.7
250
4 | Road | Main Bars | 8 | 200 |  | 0 | 2000 | 0 |  |  |  | 2000 | 0 | 100 | 1900 | 1 | 41 | 77.9 | 0.395 | 1 | 30.8 | 30.78 | 30.78
2000
4 | Road | Main Bars | 8 | 200 |  | 0 | 8000 | 0 |  |  |  | 8000 | 0 | 100 | 7900 | 1 | 11 | 86.9 | 0.395 | 1 | 34.3 | 34.33 | 34.33
8000
[20 empty] | Total Weight |  | 778.44 | 928.05

## as per p.o (hidden)
Sample BOQ for Laying of 250NB pipe line and repairing of Fire Fighting System and at 765/400kV
Sr No | [5 empty] | Total
| Description | Unit | Quantity | Rate | Amount
1 | Earth work in excavation by mechanical means Hydraulic excavator)/ manual means over areas (exceeding 30 cm in depth, 1.5 m in width as well as 10 sqm on plan) including getting out and disposal of excavated earth lead upto 50 m and lift upto 1.5 m, as directed by Engineer-in-charge. | cum | 160 | 160 | 25600 | 25600
2.6.1 All kinds of soil
2 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering - All work up to plinth level : 1:3:6 (1 Cement : 3 coarse sand (zone-III) : 6 graded stone aggregate 20 mm | Cum | 6.41 | 5600 | 35896 | 35896
nominal size)
3 | Providing and laying in position specified grade of reinforced cement | Cum | 4 | 6800 | 27200 | 27200
concrete, excluding the cost of centering, shuttering, finishing and
reinforcement - All work up to plinth level :
1:1.5:3 (1 cement : 1.5 coarse sand (zone-III): 3 graded stone
aggregate 20 mm nominal size)
4 | Providing and laying in position specified grade of reinforced cement concrete, excluding the cost of centering, shuttering, finishing and reinforcement - All work up to plinth level : 1:2:4 (1 cement : 2 coarse sand (zone-III) : 4 graded stone | Cum | 14.06 | 6400 | 89984 | 89984
aggregate 20 mm nominal size)
5 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering - All work up to plinth level : 1:4:8 (1 Cement : 4 coarse sand (zone-III) : 8 graded stone | Cum | 5.8 | 5100 | 29580 | 29580
aggregate 40 mm nominal size)
6 | Demolishing R.C.C. work manually/ by mechanical means including stacking of steel bars and disposal of unserviceable material within 50 metres lead as per | Cum | 1.6 | 2200 | 3520 | 3520
direction of Engineer - in- charge. cum 2534.70
7 | Demolishing cement concrete manually/ by mechanical means including disposal of material within 50 metres lead as per direction of Engineer - in - charge. | Cum | 1.6 | 1600 | 2560 | 2560
15.2.1 Nominal concrete 1:3:6 or richer mix (i/c equivalent design mix)
8 | Centering and shuttering including strutting, propping etc. and removal of form work for Foundations, footings, | Sqm | 207.28 | 250 | 51820 | 51820
bases for columns
9 | Structural steel work riveted, bolted or welded in built up sections, trusses and framed work, including cutting, hoisting, fixing in position and applying a priming coat of | Kg | 668.95 | 83 | 55522.85 | 55522.85
approved steel primer all complete.
10 | Steel reinforcement for R.C.C. work including straightening, cutting, bending, placing in position and binding all complete upto plinth level Thermo- | Kg | 500.57 | 70 | 35039.9 | 35039.9
Mechanically Treated bars of grade Fe-500D or more
11 | Filling available excavated earth (excluding rock) in trenches, plinth, sides of foundations etc. in layers not exceeding 20cm in depth, consolidating each deposited layer by ramming and watering, lead up to 50 m and lift | Cum | 124.01 | 200 | 24802 | 24802
upto 1.5 m.
13 | Providing and laying non-pressure NP2 class (light duty) | Mtr. | 24 | 1250 | 30000 | 30000
R.C.C. pipes with collars jointed with stiff mixture of cement mortar in the proportion of 1:2 (1 cement : 2 fine sand) including testing of joints etc. complete :
450mm
14 | Supply of 250NB PN16 CI, ISI, Gate Valve | No. | 2 | 49000 | 98000 | 98000
15 | Supply of 250NB, IS:3589, Fe410 Grade pipe | Mtr. | 200 | 2200 | 440000 | 440000
17 | Supply of 150NB pipe IS:1239, Medium grade pipe | Mtr. | 30 | 1200 | 36000 | 36000
18 | Wrapping of 250NB pipe with corrosion resistiveresistance tapes | Mtr. | 30 | 400 | 12000 | 12000
20 | Replacement of old pipes of size 150NB with new pipe | Mtr. | 30 | 799 | 23970 | 23970
with flange both side complete with painting
21 | Fabrication, erection, testing, underground fabrication and painting work of 250 NB MS round hollow pipe, including making of Tee, Elbow band,reducer & flange at your site Jhatikara sub station, Najafgarh, Delhi as per | Mtr. | 200 | 729 | 145800 | 145800
engineer in charge
22 | Supply and fixing of 12mm dia MS round bar having thread and bolting system both end for fixing of 250NB | Nos. | 50 | 100 | 5000 | 5000
pipe on pipe support
23 | installlation of 250 nb gate valve | nos | 2 | 12500 | 25000 | 25000
| selonide valve | nos | 1 | 2000 |  | 2000
| pressure switch | nos | 2 | 9000 |  | 18000
| supply of CI gate valve 150 mm NB PN 16 Rising spindal | nos | 3 | 35000 |  | 105000
| supply of C I Deluge valve 150 mm NB | nos | 1 | 180000 |  | 180000
| supply of y stainer 150 mm NB | nos | 1 | 70000 |  | 70000
1 | supply 100NB G.I, Medium, IS:1239-M | Mtr | 18 | 1940 |  | 34920
2 | supply 65NB G.I, Medium, IS:1239-M | Mtr | 38 | 1376 |  | 52288
3 | supply 50NB G.I, Medium, IS:1239-M | Mtr | 38 | 959 |  | 36442
4 | supply 40NB G.I, Medium, IS:1239-M | Mtr | 54 | 702 |  | 37908
5 | supply 25NB G.I, Medium, IS:1239-M | Mtr | 102 | 621 |  | 63342
6 | supply 80NB M.S Pipe for Pylon | Mtr | 36 | 1222 |  | 43992
7 | supply 65NB M.S Pipe for Pylon | Mtr | 42 | 1307 |  | 54894
8 | supply Spray Nozzle , Brass, 20NB, K-23-120 | Nos. | 50 | 2340 |  | 117000
9 | supply Spray Nozzle , Brass, 20NB, K-18-80 | Nos. | 4 | 2200 |  | 8800
10 | supply Quartzoid buIld detector, 15NB, brass, Pendent 79⁰C | Nos. | 27 | 956 |  | 25812
1 | Installation and fixing of 100NB G.I, Medium, IS:1239-M | Mtr | 18 | 950 |  | 17100
2 | Installation and fixing of 65NB G.I, Medium, IS:1239-M | Mtr | 38 | 600 |  | 22800
3 | Installation and fixing of 50NB G.I, Medium, IS:1239-M | Mtr | 38 | 350 |  | 13300
4 | Installation and fixing of 40NB G.I, Medium, IS:1239-M | Mtr | 54 | 300 |  | 16200
5 | Installation and fixing of 25NB G.I, Medium, IS:1239-M | Mtr | 102 | 200 |  | 20400
6 | iInstallation and fixing of 80NB M.S Pipe Pylon support | Mtr | 36 | 900 |  | 32400
7 | Installation and fixing of 65NB M.S Pipe Pylon support | Mtr | 42 | 700 |  | 29400
8 | Installation and fixing of Spray Nozzle , Brass, 20NB, K-23-120 | Nos. | 50 | 1300 |  | 65000
9 | Installation and fixing of Spray Nozzle , Brass, 20NB, K-18-80 | Nos. | 4 | 1300 |  | 5200
10 | Installation and fixing of Quartzoid buld detector, 15NB, brass, Pendent 79⁰C | Nos. | 27 | 1300 |  | 35100
1132298

## Sheet4 (hidden)
0.6 | 0.6 | 0.1 | 0.036 | 52 | 1.872
0.6 | 0.6 | 0.1 | 0.036 | 178 | 6.408 | 1:3;6
0.5 | 0.5 | 0.1 | 0.025 | 178 | 4.45 | 1:02 | 14.062
0.6 | 0.3 | 0.3 | 0.054 | 178 | 9.612 | 1:02
|  |  |  | 178 | 0
4.6

## BOQ
BOQ for Extension of Fire Fighting work for 3×110 MVAR, 1-Phase 765 KV Bus Reactor at 765/220 kV Substation Orai (Jalaun) Uttar Pradesh
S. No. | BOQ Item No. | Item Description | Unit | Qty
1 | 2 | 3 | 4 | 5
1 |  | Design,Supply, Installation, testing and commissioning of HVWS Fire Proterction system for 3×110 MVAR, 1-Phase, 765 KV Bus Reactor
1.1 |  | Design of Fire Proterction system for 3×110 MVAR, 1-Phase, 765 KV Bus Reactor as per TS | LS | 1
1.2 |  | Supply and Installation of HVW SPPRAY SYSTEM FOR3×110 MVAR, 1-Phase, 765 KV Bus Reactor
1.2.1 |  | Cast Iron Deluge Valve (Hydraulically Actuated) complete with necessary Trims, Hydraulic Motor gong
(a) |  | Size 100 NB | Nos. | 3
1.2.2 |  | Cast Iron Gate Valve- Rising Spindle Type
(a) |  | Size 250 NB | Nos. | 1
(b) |  | Size 100 NB | Nos. | 9
1.2.3 |  | Y- Type Strainer
(a) |  | size 100 NB | Nos. | 3
1.2.4 |  | Pressure Switch | Nos. | 6
1.2.5 |  | Solenoid Valve | Nos. | 3
1.2.6 |  | Frangible Bulb Heat Detector- Rating 79 Deg.C | Nos. | 93
1.2.7 |  | HVW Spray Nozzles (K23, 120 deg.) | Nos. | 150
1.2.8 |  | HVW Spray Nozzles (K18, 80 deg.) | Nos. | 12
1.2.9 |  | Above ground Piping - ERW, MS (Galvanized) as per IS:1239 Class (B)
(a) |  | Size 100 NB | Meter | 54
(b) |  | Size 65 NB | Meter | 96
(c ) |  | Size 50 NB | Meter | 96
(d) |  | Size 40 NB | Meter | 144
(e ) |  | Size 25 NB | Meter | 252
1.2.10 |  | MS Class A as per IS:1239, (Pylon Support Pipe)
(a) |  | Size 80 NB | Meter | 54
(b) |  | Size 65 NB | Meter | 186
1.2.11 |  | Local Control Panel for Deluge Valves | Nos. | 3
1.3 |  | Supply and Installation of HYDRANT SYSTEM
1.3.1 |  | Single Headed, (External) Hydrant Valves (As per IS: 5290 Type - A ), 63NB, GunI MATERIAL | Nos. | 3
1.3.2 |  | Fire Hoses - with instantaneous End Couplings to IS:636 (Type-A) - For External Hydrants - Size - 63 mm, Dia x 15 M long | Nos. | 6
1.3.3 |  | Branch Pipe & Nozzles, (Solid Jet type) to IS:903 | Nos. | 3
1.3.4 |  | Hose Cabinets - 16 SWG thick. M.S. Fabricated type for External Hydrants Suitable For 2 x 15 M RRL Hose Length | Nos. | 3
1.4 | NS | Providing ,laying,testing & commissioning of MS PIPE 250 NB dia black conforming to IS 3589,5mm thick (for HVWS above ground) including welding, fittings like elbows, tees ,flanges ,tapers,nuts bolts, Ubolts,gaskets,embedded reinforcement etc. and fixing the pipe on provided concrete support with suitable clamp/support frame(channel) painting with two or more coats of synthetic enamel paint of required shade complete as per specifications (Civil works shall be dealt seperately) | Meter | 50
1.5 | NS | Providing ,laying,testing & commissioning of MS PIPE 100 NB dia black conforming to IS:1239, Part-I medium grade i (for HVWS above ground)including welding,fittings like elbows,tees,flanges,tapers,nuts bolts, U bolts,gaskets,embedded reinforcement etc. and fixing the pipe on provided concrete support with suitable clamp/support frame(channel) painting with two or more coats of synthetic enamel paint of required shade complete as per specifications (Civil works shall be dealt seperately) | Meter | 60
1.6 |  | Deluge Hut
(a) | 100007441 | Construction of Deluge Valve Room as per drawing (Excluding excavation, PCC, Reinforcement & RCC) | EA | 3
1.7 |  | CIVIL WORKS
1.7.1 | 2.8.1 | Earth work in excavation by mechanical means (Hydraulic excavator)/ manual means over areas (exceeding 30 cm in depth, 1.5 m in width as well as 10 sqm on plan) including getting out and disposal of excavated earth lead upto 50 m and lift upto 1.5 m, as directed by Engineer-incharge All kinds of soil | Cum | 2
1.7.2 | 4.1.6 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering - 1:3:6 (1 Cement : 3 coarse sand (zone-III) derived from natural sources : 6 graded stone aggregate 40 mm nominal size derived from natural sources) | Cum | 1
1.7.3 | 4.1.3 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering - All work up to plinth level :1:2:4 (1 cement : 2 coarse sand (zone-III) derived from natural sources : 4 graded stone aggregate 20 mm nominal size derived from natural sources) | Cum | 1
1.7.4 | 4.3.1 | Centering and shuttering including strutting, propping etc. and removal of form work for :Foundations, footings, bases for columns | SQM | 22
1.7.5 | 10.1 | Structure steel work in single section, fixed with or without connecting plate, including cutting, hosting, fixingin position and applying a priming coat of approved steel primer all complete | KG | 50
1.7.6 | 5.1.2 | Providing and laying in …. - All work up to plinth level : 1:1.5:3 (1 cement : 1.5 coarse sand (zone-III) derived from natural sources : 3 graded stone aggregate 20 mm nominal size de rived from natural sources) | Cum | 2
1.7.7 | 5.22.6 | Steel reinforcement for R.C.C. work including straightening, cutting, bending, placing in position and binding all complete upto plinth level Thermo-Mechanically Treated bars of grade Fe-500D or more | KG | 188
1.7.8 | 15.2.2 | Demolishing Cement Concrete (1:4:8) | Cum | 2
1.7.9 | 15.43.1 | Dismantling manually/ by mechanical means including stacking of serviceable material and disposal of unserviceable material within 50 metres lead as per direction of Engineer-in-charge Water bound macadam road | Sq.m. | 19
1.7.10 | 15.58 | Demolishing R.C.C. work by mechanical means and stockpiling at designated locations and disposal of dismantled materials up to a lead of 1 kilometre, stacking serviceable and unserviceable material separately including cutting reinforcement bars | Cum | 2
1.7.11 | 19.35.1 | Providing and laying Non Pressure NP-3 class (Medium duty) R.C.C. pipes including collars/spigot jointed with stiff mixture of cement mortar in the proportion of 1:2 (1 cement : 2 fine sand) including testing of 450 mm dia RCC pipes | RM | 5