| S.No | Clause No. | Text as per bid document | Bidder Query | Clarification |
| --- | --- | --- | --- | --- |
| 1 | Clause 2.2.1.1.A).c0) of Section Project | Complete Control, Relay and Protection system as per Section–Control and Relay Panels for 400 kV & 220 kV bays under present scope. Existing 400 kV & 220 kV Bus bar protection scheme is type REB 500 (distributed type) of M/s ABB make. As per Section-Control and Relay Panels, Augmentation of existing 400kV and 220kV Bus bar protection scheme including required Bus bar protection bay modules, trip/auxiliary relays, wirings etc. for 2 numbers of 400kV bays, 4 Number of 220kV bays are under present scope. Supply of Bus Bar Protection Bay Modules for above mentioned 400kV & 220kV bays are included in the present scope. Bus Bar protection of 220kV Bays mentioned above can be included in the existing 220kV Bus Bar Protection Scheme by incorporating suitable scheme logics. | As per the Site input we understand that existing 220kV Busbar Protection is of Siemens make (distributed type). Request you to kindly check and clarify on the same. | Existing Bus Bar Protection relays at Indore S/s are as follow a)400kV Switchyard: ABB Make REB 500 b) 220kV Switchyard: Siemens Make 7SS522 |