| Sr. No | Clause No. | Clause Description | Bidder Queries | POWERGRID REPLY |
| --- | --- | --- | --- | --- |
| Volume-II of the Bidding Documents |  |  |  |  |
|  | Fire Hydrant | Section Project II A (d) | Please arrange to provide the existing hydrant layout. Other wise specify the length of tap off point of water line from present scope transformer area for estimation as it is lot items. | Clarification-1 may be referred to where the reply was already been given. |
|  | BB Protection System | Section Project 2 I (A) (b) | At Banaskhanta SS, For 765KV, 400KV Busbar protection main unit and peripheral unit are not in present scope for the bays under present scope. We will provide only cut out for peripheral unit it present scope CRP. Interconnection of peripheral unit & peripheral unit to main Busbar protection relay are not in present scope. Please confirm. | Please refer clause 2.0, I, A), (b) and 2.0, II, A), (b) of Section Project, where in it is mentioned that Necessary modifications, wiring, etc. for completion of the bus bar protection scheme for bays under present scope has to be carried out by contractor. Any modification required in the existing protection scheme is included in the present scope. |
|  | BB Protection System | Section Project 2 II (A) (b) | For Sankhari Substation, plesae arrange to provide the Busbar protection system details for augmentation for present scope bays. | Clarification-1 may be referred to where the reply was already been given. |
|  | SAS integration | Section Project 2 I (A) (c) & 2 II (A) (c) | Present scope include upgradation of hardware & software includue license fees(if any). Hence, arrange to provide the GTP of existing SAS system & existing SAS architecture to access the cost of the same. | Existing SAS architecture shall be provided to successful bidder during detailed engineering |
|  | Erection Hardware | Bid Price Schedule | For 400KV Tie bays are not included in BPS. Please review & clarify where the cost of the same will be included. | Bidder may quote as per BPS |
|  | Earthing for Sankhari | Existing drawing | Plesae arrange to provide the existing earthing layout for Sankhari SS to quantify earthing riser quantity. Otherwise plesae indicate the earth grid spacing for quantify earthing lot items. | Clarification-1 may be referred to where the reply was already been given. |
|  | General |  | As per BPS there are no items for ACDB, DCDB or its extension. So we assume that sufficient feeder required for present scope will be available in existing system. Please confirm. | Clarification-1 may be referred to where the reply was already been given. |
|  | General |  | For 765KV & 400KV bays Cable trench layout to be constructed for present scope only extended from nearby existing trench. We presume that existing trench have sufficient space for present scope cable. Plesae confirm. | Clarification-1 may be referred to where the reply was already been given. |
| Civil Queries- Banaskantha |  |  |  |  |
|  | Transformer drawing | 0.0 Section Project-Rev-0, Clause 2.0, Page no.1 | Kindly provide the vendor drawing of Power tranformer along with the details such as weight of transformer, volume of oil etc. for working out the quantities for Civil works associated. | Drawing of Power Transformer shall be shared during detailed engineering. Bidder may quote as per BPS. |
|  | Switchyard panel room | 0.0 Section Project-Rev-0, Clause 2.0 (C), Page no.4 | Kindly provide the standard drawing of Switchyard panel room as the same is not available in tender document. | Architectural drawing of Switchyard panel room is already attached in tender document. Structural drawing shall be shared during detailed engineering. |
|  | Rail cum road | 0.0 Section Project-Rev-0, Clause 2.0 (C), Page no.4 | Kindly provide the standard drawing for Rail cum road arrangement. | Please Refer Amendment -III |
|  | Drain layout | 0.0 Section Project-Rev-0, Clause 2.0 (C), Page no.4 | Kindly provide drain layout of the existing substation. | Drain layout of existing substation shall be shared during detailed engineering. Bidder is advised to visit the substation as per clause no. 1.4 of Section Project. |
|  | Contour map | 0.0 Section Project-Rev-0, Clause 2.0, Page no.1 | In order to evaluate the quantities for earthwork & slope protection works, we request you to provide the Topography survey report of the extension portion. | Site Levelling & Slope Protection Works are not envisaged in the BPS. |
|  | Geotechnical Investigation Report | 0.0 Section Project-Rev-0, Clause 2.0, Page no.1 | Kindly provide the Geotechnical investigation report for tender purpose | Soil Investigation report shall be shared during detailed engineering. |
| Civil Queries -Sankheri |  |  |  |  |
|  | Transformer drawing | 0.0 Section Project-Rev-0, Clause 2.0, Page no.1 | Kindly provide the vendor drawing of Power tranformer along with the details such as weight of transformer, volume of oil etc. for working out the quantities for Civil works associated. | Power transformer is not envisaged under the present scope. |
|  | Switchyard panel room | 0.0 Section Project-Rev-0, Clause 2.0 (C), Page no.6 | Kindly provide the standard drawing of Switchyard panel room as the same is not available in tender document. | Architectural drawing of Switchyard panel room is already attached in tender document. Structural drawing shall be shared during detailed engineering. |
|  | Rail cum road | 0.0 Section Project-Rev-0, Clause 2.0 (C), Page no.4 | Kindly provide the standard drawing for Rail cum road arrangement. | Rail cum road arrangement is not envisaged under the present scope. |
|  | Foundation layout | 0.0 Section Project-Rev-0, Clause 2.0 (C), Page no.6 | Kindly provide foundation layout of the existing substation. | Clarification-1 may be referred to where the reply was already been given. |
|  | Cable trench layout | 0.0 Section Project-Rev-0, Clause 2.0 (C), Page no.6 | Kindly provide cable trench layout of the existing substation. | Clarification-1 may be referred to where the reply was already been given. |
|  | Drain layout | 0.0 Section Project-Rev-0, Clause 2.0 (C), Page no.6 | Kindly provide drain layout of the existing substation. | Drain layout of existing substation shall be shared during detailed engineering. Bidder is advised to visit the substation as per clause no. 1.4 of Section Project. |
|  | Contour map | 1.0-Appendix-II (R1) Section-Project Part-A3; Civil works; Page no.7 | In order to evaluate the quantities for earthwork & slope protection works, we request you to provide the Topography survey report of the extension portion. | Contouring work and Site levelling is in bidder's scope. Bidder is advised to visit the substation as per clause no. 1.4 of Section Project. |
|  | Geotechnical Investigation Report | 1.0-Appendix-II (R1) Section-Project Part-A3; Civil works; Page no.12 | Kindly provide the Geotechnical investigation report for tender purpose | Soil investigation is in bidder's scope. |