| Sl. No. | Ref. document | Provision in bidding document | Bidders Queries/Observation | POWERGRID Reply/Clarification |
| --- | --- | --- | --- | --- |
| 1. |  | General Query. | 48F and 96F OPGW is required under this package. Quantity bifurcation is not provided in the Price Schedule. Please confirm the quantity of OPGW required along with transmission line details and its wind zone details. | The quantities for 24/48/96F are clearly specified in the Price Schedule. Reference may be made to Appendix-A of the Volume-II Technical Specification (TS), where the voltage levels and line details are clearly specified. Further, the line details have already been provided in the Technical Specification (TS) under Appendix-A. The same may be considered as tentative parameters for Wind Zone. Line-wise Wind Zone details shall be furnished during the detailed engineering stage. |
| 2. | Page No. 9 &10 of Vol-II, Part-3, Section-2 Clause 2.1.3.2 | OPGW Parameters to be considered for different line voltage and wind zones | 96F OPGW is also required. However, the design parameters of proposed 96F OPGW design may differ from the technical parameters given in table in clause 2.1.3.2 of Section-02 of Technical Specifications_part_1. Please confirm if this is acceptable subject to meeting the sag and tension criteria. Please also confirm the quantity of 96F OPGW required along with transmission line details along with its wind zone details. | Standard OPGW designs shall be adopted as per Clause 2.1.3.2 of Section-02 of the Technical Specifications. However, in case of any constraints in adopting the standard design, the Contractor may propose customized design(s) during the detailed engineering stage to meet the sag and tension requirements. As per the requirement, the quantity of 96F OPGW is specified in the Price Schedule. The wind Zone details shall be shared during detailed engineering |
| 3. | Page no 45 of Volume-II Part 1 of 2 | TS OPGW-08 WR-II-Part 1 of 4, (Appendix- I, Apr 26, Revision-02) Fibre Optic Approach Cable Installation Manual APPROACH CABLE INSTALLATION AND HANDLING DOCUMENT | There are some contradiction - As per Clause-"Approach Cable Structure", 4 loose tube & 2 fillers are shown in the diagram, i.e. 12 fibers in a loose tube, while in "Technical Characteristics" matrix for 48F is mentioned with 8 fibers in a loose tube. As, OPGW shall be with 12 fiber in a loose tube, hence for the fiber grouping & splicing point of view, we recommends for 12 fiber in a loose tube. We request you to please confirm fiber per loose tube. | Please refer Amendment-II for Appendix-I of Technical Specification. |
| 4. | Volume-II, TS Part 1 of 2 | General Query | 96F Approach Cable specification is missing in the Tender document. We request you to provide the same. OR Please confirm to proceed with 12 fibers in a tube, 8 tubes & mechanical parameter as mentioned in this clause i.e "Dimension & Properties" (Cable diameter & weight shall be offered accordingly). | Please refer Amendment-II for Appendix-I of Technical Specification. |
| 5. | Volume-II-TS |  | 1.Kindly specify the voltage level for the given tender BoQ. 2. Kindly specify the Wind Zone for the given tender BoQ. | 1) Please refer to Appendix-A of the Volume-II Technical Specification (TS), where the voltage levels and line details are clearly specified. 2) The line details have already been provided in the Technical Specification (TS) under Appendix-A. The same may be considered as tentative parameters for Wind Zone. Line-wise Wind Zone details shall be furnished during the detailed engineering stage. |
| 6. | Volume-II-TS |  | Kindly provide Sag-Tension criteria for OPGW cable for 132 kV, 220 kV, 400 kV and 765 kV lines, including span, wind pressure, sag, and tension parameters. | Please refer to Appendix-A of the Volume-II Technical Specification (TS), where the voltage levels and line details are clearly specified. Further, the span, wind pressure, sag, and tension parameters shall be shared/finalized during the detailed engineering stage. |