| Clause No./ sections | Existing Clause/item |  |  |  |  |  |  |  | Amended provision |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | SR. NO. | ACTIVITY DESCRIPTION | MATERIAL CODE | DESCRIPTION | UNIT | QTY |  |  | SR. NO. | ACTIVITY DESCRIPTION | MATERIAL CODE | DESCRIPTION | UNIT | QTY |  |
| BPS PRICE SCH-1 & 2 |  | 37 | Insulator | 1000076490 | 25 nos of 120KN AC Porcelain Disc Insulator/3 nos of 120KN AC Porcelain Long Rod Insulators (220KV). | SET | 129 |  |  | 37 | Insulator | 1000076490 | 25 nos of 120KN AC Disc Insulator/3 nos of 120KN AC Porcelain Long Rod Insulators (220KV). | SET | 129 |  |
|  |  | 38 | Insulator | 1000076491 | 22 nos of 160KN AC Porcelain Disc Insulator/3 nos of 160KN AC Porcelain Long Rod Insulators (220KV). | SET | 1392 |  |  | 38 | Insulator | 1000076491 | 22 nos of 160KN AC Disc Insulator/3 nos of 160KN AC Porcelain Long Rod Insulators (220KV). | SET | 1392 |  |
| BPS PRICE SCH-3 |  |  |  |  | N/A |  |  |  |  |  | Survey | 100056953 | Land Scheduling-Compensation | KM | 47 |  |
| BPS PRICE SCH-3 |  | 36 | Stringining | 100044617 | Installing and stringing of OPGW including fixing of OPGW accessories for 220 kV Double circuit towers | KM | 47 |  |  | 36 | Stringining | 100044617 | Installing and stringing of OPGW including fixing of OPGW accessories for 220 kV Double circuit towers | KM | 42 |  |
|  |  | 37 | Stringining | 100054794 | Installation of Insulator strings complete with arcing horns and necessary hardware, Installing and stringing of conductor includingfixing of conductor accessories for 220 kV Double circuit towers with Single conductor on single side strung. | KM | 47 |  |  | 37 | Stringining | 100054794 | Installation of Insulator strings complete with arcing horns and necessary hardware, Installing and stringing of conductor includingfixing of conductor accessories for 220 kV Double circuit towers with Single conductor on single side strung. | KM | 42 |  |
|  |  |  |  |  | N/A |  |  |  |  |  | Stringining | 100056980 | STRINGING 220KV D/C 1C 1S WITH DRONE | KM | 5 |  |
| BPS PRICE SCH-3 |  |  |  |  | N/A |  |  |  |  |  | Cable bypass arrangement | 100056872 | CABLE BYPASS ARRANGEMENT-11KV | EA | 23 |  |
|  |  |  |  |  | N/A |  |  |  |  |  | Cable bypass arrangement | 100056873 | CABLE BYPASS ARRANGEMENT-33KV | EA | 5 |  |
|  |  |  |  |  | N/A |  |  |  |  |  | Cable bypass arrangement | 100056874 | CABLE BYPASS ARRANGEMENT-LT | EA | 19 |  |
| 1.2 (xxi) of Section- IA (VOLUME-II) of TS |  | NIL |  |  |  |  |  |  |  | Add new clause 1.2 (xxi) in Section-IA (VOLUME-II) of TS: 1.2 (xxi) Cable bypass arrangement of 11KV/33KV/LT Powerline crossing. (wherever applicable & covered under BPS). |  |  |  |  |  |  |
| 1.2 (xxii) of Section- IA (VOLUME-II) of TS |  | NIL |  |  |  |  |  |  |  | Add new clause 1.2 (xxii) in Section-IA (VOLUME-II) of TS: 1.2 (xxii) Stringing of transmission line through Drones (wherever applicable &covered under BPS |  |  |  |  |  |  |
| 1.2 (xxiii) of Section- IA (VOLUME-II) of TS |  | NIL |  |  |  |  |  |  |  | Add new clause 1.2 (xxiii) in Section-IA (VOLUME-II) of TS: 1.2 (xxiii) Land scheduling for compensation |  |  |  |  |  |  |
| Clause no. 3.1.8 of SECTION-IV C (VOLUME-II) of TS |  | NIL |  |  |  |  |  |  |  | Add new clause 3.1.8 in Section IVC Fabrication, Erection & Stringing,Rev-7(Dec'2023) (VOLUME-II) of TS: 3.1.8: For crossing of 33kV/11kV/LT lines during stringing, shut down shall be obtained by Employer. However, contractor shall be required to arrange bypass arrangement for such lines with suitable LT/HT power cables whenever shutdown cannot be arranged during stringing. The bypassing work shall be executed with suitable 33kV/11kV/LT cables, following all electrical guidelines and proper safety measures in co-ordination with concern DISCOM/agency/authority. However, the healthiness of cables shall be ensured by the contractor before installation at each crossing. The 33kV/11kV/LT line shall be restored after the completion of stringing work, with confirmation from Employer. The work shall be carried out as per the direction of the Engineer-in-Charge. The payment of bypass arrangement shall be inclusive of suitable cables and all necessary items/arrangements/works required for successful bypassing of existing 33kV/11kV/LT lines that includes de-stringing of existing 33kV/11kV/LT conductors and their restoration after completion of stringing. The provisional quantities for bypass arrangements are indicated in the BPS. The bidders are required to quote unit rates for the same in appropriate schedule of BPS. The Contractor shall be entirely responsible for repair/rectification/replacement of any damage to the existing 33kV/11kV/LT line of DISCOM/agency/authority during the execution of the work. |  |  |  |  |  |  |
| 1.10 d) of Section 1B ((VOLUME-II) of TS |  | d) For transmission line with Bundle Conductor per phase: The entire stringing work of conductor shall be carried out by tension stringing technique. The bidder shall deploy requisite number of TSEs as per following so as to meet the completion schedule -Minimum 8Tonne capacity for 220kV Twin Bundle, -Minimum 8Tonne capacity for 400kV Twin Bundle, -Minimum 8Tonne capacity for 400kV Triple Bundle, -Minimum 15Tonne capacity for Quad Bundle, -Minimum 18Tonne capacity for Hexa Zebra Bundle and, -Minimum 24Tonne capacity or double no. of TSEs of 15Tonne capacity for Hexa Lapwing Bundle Conductor. The details regarding numbers and capacity of TSEs to be deployed shall be as mutually agreed between the Employer and Contractor. The period of deployment of tension stringing equipment shall be as per actual site requirement. No tractor shall be allowed for final sagging. To promote mechanization, for better safe working condition at site the Contractor shall mandatorily provide at site for each package (i) requisite numbers (minimum 2 nos. per TSE) of sagging bridges/ working platform with pull lifts for facilitating sagging & dead end jointing (ii) requisite numbers (minimum six nos. for each package) of power operated hydraulic/motorized winch machines for tower erection & carrying out final sagging (iii) requisite numbers (minimum four) ladders with suitable hooks and attachment arrangement to facilitate worker movement on insulators strings and (iv) adequate number of walkie- talkies. In case more number of sagging bridges/ working platform, power operated winch machines etc. are required for stringing of transmission line in accordance with time schedule, the same shall be provided by the Contractor. Further, use of tractor for final sagging shall not be permitted. The Contractor shall use power operated hydraulic/ motorized winch machines only. Power line crossing, river crossings, railway crossings, other single span sections where deployment of tension stringing machine is not warranted and in hilly terrain, thick forest or areas with site constraints, where deployment of tension stringing machine is not feasible, manual stringing may be adopted after getting approval of Employer’s site Engineer. The contractor shall deploy appropriate tools/ equipments/ machinery to ensure that the stringing operation is carried out without causing damage to conductor/ earth wire/ OPGW which are installed at the prescribed sagtension as per the approved stringing charts. However, the Bidder having requisite experience may use helicopter for stringing. The Bidder intending to use helicopter shall furnish detailed description of the procedure, type & number of helicopter & accessories etc., to be deployed for stringing operation. The Contractor may also deploy drones for stringing of pilot wires/ ropes for pilot wire, keeping in view site condition & feasibility. Helicopters/Drones may be used in stringing process, particularly in difficult and inaccessible terrain, subject to the required clearance from Director General of Civil Aviation (DGCA) / any other competent authority. The payment for stringing shall be done as per the unit rates of stringing under the contract irrespective of the methodology adopted for stringing. |  |  |  |  |  |  |  | d) For transmission line with Bundle Conductor per phase: The entire stringing work of conductor shall be carried out by tension stringing technique. The bidder shall deploy requisite number of TSEs as per following so as to meet the completion schedule -Minimum 8Tonne capacity for 220kV Twin Bundle, -Minimum 8Tonne capacity for 400kV Twin Bundle, -Minimum 8Tonne capacity for 400kV Triple Bundle, -Minimum 15Tonne capacity for Quad Bundle, -Minimum 18Tonne capacity for Hexa Zebra Bundle and, -Minimum 24Tonne capacity or double no. of TSEs of 15Tonne capacity for Hexa Lapwing Bundle Conductor. The details regarding numbers and capacity of TSEs to be deployed shall be as mutually agreed between the Employer and Contractor. The period of deployment of tension stringing equipment shall be as per actual site requirement. No tractor shall be allowed for final sagging. To promote mechanization, for better safe working condition at site the Contractor shall mandatorily provide at site for each package (i) requisite numbers (minimum 2 nos. per TSE) of sagging bridges/ working platform with pull lifts for facilitating sagging & dead end jointing (ii) requisite numbers (minimum six nos. for each package) of power operated hydraulic/motorized winch machines for tower erection & carrying out final sagging (iii) requisite numbers (minimum four) ladders with suitable hooks and attachment arrangement to facilitate worker movement on insulators strings and (iv) adequate number of walkie- talkies. In case more number of sagging bridges/ working platform, power operated winch machines etc. are required for stringing of transmission line in accordance with time schedule, the same shall be provided by the Contractor. Further, use of tractor for final sagging shall not be permitted. The Contractor shall use power operated hydraulic/ motorized winch machines only. Power line crossing, river crossings, railway crossings, other single span sections where deployment of tension stringing machine is not warranted and in hilly terrain, thick forest or areas with site constraints, where deployment of tension stringing machine is not feasible, manual stringing may be adopted after getting approval of Employer’s site Engineer. The contractor shall deploy appropriate tools/ equipments/ machinery to ensure that the stringing operation is carried out without causing damage to conductor/ earth wire/ OPGW which are installed at the prescribed sagtension as per the approved stringing charts. However, the Bidder having requisite experience may use helicopter for stringing. The Bidder intending to use helicopter shall furnish detailed description of the procedure, type & number of helicopter & accessories etc., to be deployed for stringing operation. Helicopters may be used in stringing processes, particularly in difficult and inaccessible terrain, subject to the required clearance from Director General of Civil Aviation (DGCA) / any other competent authority. The payment for stringing shall be done as per the unit rates of stringing under the contract irrespective of use of Helicopters for stringing. However, in the Forest areas the stringing of pilot wires/ropes shall be carried out through drones only. The Contractor may also deploy drones for stringing of pilot wires/ ropes for stringing, keeping in view site constraints as per the direction of Engineer-In-charge. The quoted rate of stringing through drones shall be inclusive of all necessary T&P's required for successful completion of stringing work including deployment of drone of suitable capacity etc. For use of Drones in stringing, clearance from Director General of Civil Aviation (DGCA) / any other competent authority may be obtained if required. |  |  |  |  |  |  |
| Second Envelope |  | In view of the above Amendments, the ‘Price_schedule_Rev02’ excel stand revised as ‘Price_schedule_Rev03’. Note- Bidders are requested to consider the revised excel sheet(s) titled “Price Schedule_Rev03” for bid preparation/submission for the subject package. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |