## PBQ FORMAT
Clarification No- VI dated 10/01/2025 to the Bidding Documents for Transmission Line Tower Package- TL01 for 220 kV S/C (on D/C Tower) Pang- Upshi line (Part-1) and establishment of new 2 x 10 MVA 66/11kV GIS Sub Station at Pang for 220kV AC Transmission line between Pang and Phyang associated with Transmission system for evacuation of RE power from renewable energy parks in Leh (5 GW Leh-Kaithal transmission corridor).; Spec. No: CC/NT/W-TW/DOM/A06/24/11961
Sr. No. | NAME OF THE DOCUMENTS | CLAUSE | BIDDER's QUERIES | POWERGRID Reply
1
1 | General | Soil profile data | We were unable to conduct the contour survey and soil investigation due to accessibility issues and limited accommodation during the winter season. Therefore, it is requested to furnish the soil investigation and contour survey reports. | 1. Soil investigation is in the scope of bidder. 2. Site levelling and contouring is in the scope of bidder.
2 | General | Earthing | In the absence of a soil report (including water level data), we are unable to estimate the type and quantity of earthing material required. It is requested to furnish the complete earthing BOQ (Earth mat risers, GI and MS flats, Pipe and Rod electrodes etc.) | As per Cl. 3.1. (I) (B) p) of Section: Project, Design of Earthmat is in scope of the bidder. Accordingly, necessary estimation of earthing materials is also in the scope of the bidder. Bidder shall quote accoridngly.
3 | General | PGCIL approved vendor (with similar meteorological data) | Kindly furnish the list of approved PGCIL vendors who have valid type test reports and have supplied to PGCIL for projects similar (with similar meteorological data) to the current package under bidding. | Bidder may refer to Compendium of Vendors in POWERGRID website for list of approved makes
4 | General | Completion Period | Given the challenging terrain and extreme weather conditions, we believe that the current 24-month completion period is insufficient. We kindly request an extension to 36 months to ensure the project is executed safely. | Provisions of the Bidding Documents shall remain unchanged.
5 | General | Heating & ventilation sytem | According to the Technical Specification, we understand that the temperature in the 66kV and 11kV GIS Hall should not fall below -10°C. Could you please confirm the required temperature limits for the Control Room cum Indoor Switchgear Room? Additionally, as per the price schedule, we assume that no controled heating system is required for the Security Room and DG Set Building. Kindly confirm. | As per Bidding documents, Controlled Heating System are envisaged for GIS Building, 11kV Indoor Switchgear Room & DG set Room. Design of these heating systems are in scope of the bidder to meet the requirements of bidding documents. Heating System is not envisaged for Security Room. | No separate Controlled Heating system is envisaged for Control Room cum indoor Switchgear Room & DG Set Building. However, due to limitation in equipment capability to operate at min ambient temeprature of site, additional Controlled Heating system or any other solution to meet the technical & functional requirements of the bidding documents; may be provided by the bidder, without any additional price implications. Controlled Heating System is not envisaged for Security room. Bidder shall quote accordingly.
6 | TS- Section Project(Rev00) : New Clause no: 10.16 | Type test report | The validity of the type test for the power transformer is 5 years. We presume that the referred clause does not apply to the Dynamic Short Circuit test report, as this is a special test. Once conducted, the Dynamic Short Circuit test report remains valid. Kindly confirm | Confirmed
7 | Section Project | Battery Battery charger | As per section project ,Minimum temperature of -35 degree is mentioned . We understand that Battery room shall be temperature controlled. Hence , please confirm the design temperature to be consideration for battery capacity calculation | Hot & cold type Split ACs are envisaged for battery room. Battery sizing shall be based on min temperature that can be maintained by the offered Split AC. Bidder shall quote accordingly. Bidder shall quote accordingly.
8 | General | Illumination | The standard PGCIL luminaires for specific areas have an operating temperature range of -5°C to 45°C. However, as per the meteorological data in the technical specification for the Pang substation, the temperature ranges from -35°C to 30°C. We understand that outdoor fixtures and luminaires must be capable of operating within this range (-28°C to 30°C).Please confirm and revise Illumination TS accordingly | All fixtures offered under subject package shall be suitable for operating at min & max ambient temperature (-35°C to +30C°). Further, it shall also meet other requirements specified in Sr. No. 6 of Amendment-1. Bidder shall quote accordingly.
9 | Technical specifications for 33kV & 11kV GIS | 11kV Indoor switchgear | 11kV Indoor switchgear OEM's are offering temperature range as per below: 1- Siemens make : switchgear offered for temperatures from (25-)deg to (40) deg C ambient temperature, 2- ABB make : switchgear offered for temperatures from (25-)deg to (40) deg C ambient temperature. We presume that the above product is acceptable to PGCIL under controlled environment (Heating and ventilation system) and we do not need to conduct fresh type test/special test for -35 deg ambient temtreture . Kindly confirm. | As per Bidding documents, Controlled Heating System is envisaged for 11kV Indoor Switchgear Room. The Indoor Switchgear shall be suitable for operation under this controlled environment. The Validity of TypeTest reports of offered equipment shallbe verified at the time of detailed engineering, based on the requirements of Bidding document.
Siemens -66 kV GIS
10 | Technical specification for 400kV GIS (GIS-REV 5A) | Clause No. 5.2 C c. These compartments shall be such that maintenance on one feeder may be performed without de-energising the adjacent feeders. | As offered GIS is single busbar scheme, this clause of service continuity is not applicable. | Requirement of Technical Specification shall prevail. Bidder shall quote accordingly.
11 | Technical specification for 400kV GIS (GIS-REV 5A) | Clause No. 5.21. The GIS shall be designed, so as to take care of the VFT over voltages generated as a result of pre-strikes and re-strikes during isolator operation. Maximum VFT over voltages peak shall not be higher than rated lightning impulse withstand voltage (LIWV) of the equipment. Necessary measures shall be under taken by GIS manufacture to restrict maximum VFT over voltages lower than the LIWV. Manufacturer shall submit the study report of VFTO generated for GIS installation. | As requirement is of 72.5 kV GIS, the effect of VFTO is negligible. Considering the said, we request PGCIL to exclude VFTO study from scope of deliverables. | Confirmed.
12 | Technical specification for 400kV GIS (GIS-REV 5A) | Clause No. 6.6.7 Provisions shall be made for attaching an operational analyzer to record travel, speed and making measurement of operating timings etc. after installation at site. The contractor shall supply three set of transducer for each substation covered under the scope. | We presume that supply of transcducers are excluded from biider Scope of supply. Please Confirm | Requirement of Technical Specification shall prevail. Bidder shall quote accordingly.
13 | Technical specification for 400kV GIS (GIS-REV 5A) | Annexure I Reclosing : Single phase &Three phase auto reclosing. | We understand that as the requirement is for three phase encapsulated GIS CB, which shall be electrically/mechanically ganged with common CB drive mechanism, the requirement of single phase auto reclosing is not applicable. Kindly confirm the same. | Confirmed.
14 | General | CT parameters | Please find enclosed CT and VT parameters. Request customer confirmation on same. Any changes in the same shall be discussed for technical feasibilty and may have price and time implications. | The Current rating of individual bays are defined in BPS & TS. The parameters of Current & Voltage Transformers shall be decided at the time of detailed engineering meeting the requirements of Bidding documents without any additional cost or time implications. | The Current rating of individual bays are defined in BPS & TS. Further, in addition to the proposed parameters of CT, tapping at the rated current of the module shall also be provided without any additional cost & time implications.
15 | General | Wall bushing | The offered SF6-Air bushing shall be mounted horizontally and shall be suitable for customer applications. Request to kindly review and confirm. GTP for same is enclosed as part of technical offer. | Horizontally mounted SF6-Air bushings are also acceptable. However, the technical parameters of these bushings shall be finalised during detailed engineering based on solution offered.
16 | BOQ | 3-phase of 1250A disconnector switch including main circuit, enclosure, driving mechanism and support insulator etc., complete in all respect as per TS. | For the said clause we infer that PGCIL requires 02 nos of DS of each type for one-one replacement. Please confirm. | Requirement of Technical Specification shall prevail. Bidder shall quote accordingly.
ABB-11 kV GIS
17 | Technical specifications for 33kV & 11kV GIS | Clause No. 3.01 f), page 2 of 22 The design should be such that all parts subjected to wear and tear are easily accessible for maintenance purposes. The Service Class Continuity of Switchgears shall be LSC 2B-PM (as per IEC 622771-200) | As per the old IEC our product complied to LSC2B However as per the Latest IEC now it comes under the classification LSC 2 . For MV GIS , Loss of service continuity shall be LSC 2 ,on access to the cable terminations of panel, the busbar and all other panels can remain energized . | As per requirement for subject package, atleast LSC2A-PM or better (as per IEC 62271-200:2024) shall be provided for offered 11kV Switchgear.
18 | Technical specifications for 33kV & 11kV GIS | Clause No. 3.01-m), page no. 3/22 Suitable base frames made out of steel channels shall be supplied along with necessary anchor bolts and other hardware, for mounting of the switchgear panels. | Base frame shall be made up of extruded aluminium as it provides superior Surface tolerance . | Acceptable provided other functional reqirements of technical specifications are fulfilled.
19 | Technical specifications for 33kV & 11kV GIS | Clause No. 3.01-g), page no. 2/22 All necessary equipment required for Gas handling at site (if any), shall be arranged by the supplier at their own cost. | The panels are factory filled and there is no need of gas work required at site . So the supply of gas and the gas handling kit is not required and same shall not be in the ABB scope of supply. | Noted. However, in case any top-up of gas is required at site, necessary equipment required shall be arranged by the supplied without any additional cost implications.
20 | Technical specifications for 33kV & 11kV GIS | Clause No. 3.01-k), page no. 3/22 Total height of the switchgear panels shall be finalized during detail engineering in line with building design. The height of switches, pushbuttons and other hand operated devices shall not exceed 1800 mm and shall not be generally less than 700 mm. | The height of the panels shall be 2350mtrs. And operating height shall be 1900mm. Kindly accept the same. | Opearting height of max. 2000mm is acceptable. | Due to SIEMENS
21 | Technical specifications for 33kV & 11kV GIS | Clause No. 3.02-j), page no. 4/22 Motor windings shall be provided with class E insulation or better. The insulation shall be given tropical and fungicidal treatment for successful operation of the motor in a hot, humid and tropical climate. | It shall be as per our standard type tested design and we understand the panels shall be erected in a positive pressure, ventilated air conditioned room. | Rquirement of technical specifications shall prevail. It may be informed that only heating system is envisaged for 11kV Switchgear room.
22 | Technical specifications for 33kV & 11kV GIS | Clause No. 3.05-c),page no. 5/22 c) Bus bar cross-section shall be uniform throughout the length of switchgear board. Bus bars shall be in SF6 gas insulated compartment. | According to the amendment in "Technical Specification, Section – Project (Rev.00) C/ENGG/SPEC/PANG/PROJECT/GIS, Rev 0": (A) For all indoor switchgear (GIS Type), manufacturer’s standard design of busbar (SF6/solid core/epoxy insulated), various gas chambers, placement of various equipments in the panel etc. shall also be acceptable. We have complied with this amendment. | Noted.
23 | Technical specifications for 33kV & 11kV GIS | Clause No. 3.05-d),page no. 5/22 In case of organic insulator partial discharge shall be limited to 100pico coulomb at rated Voltage X 1.1/ 3 . | It shall be as per our standard type tested design and Partial discharge limit shall be as per IEC. | Requirement of Technical Specification shall prevail.
24 | Technical specifications for 33kV & 11kV GIS | Clause No. 3.05-e),page no. 5/22 Bus switching scheme shall be as per Single Line diagram attached with bidding documents. | Please clarify what is the scheme required. | As per Tender drawing No. C/ENGG/GIS/PHANG/SLD/01 included with the bidding documents, Switching scheme for 11kV system shall be Single Bus with bus sectionaliser.
25 | Technical specifications for 33kV & 11kV GIS | Earthing and Earthing Devices | Please note we shall provide necessary connections to the earthing bar however, connection from there to earthing mat shall not be in our scope. | The connection of 11kV Switchgear with the earthing mat is in the scope of the bidder.
26 | Technical specifications for 33kV & 11kV GIS | Clause No. 3.08.01 page no. 7/22 ...Modbus to IEC 61850 converter shall be provided for integration with SAS. | Converter shall not be in our scope of supply. And we shall provide relays with IEC61850 protocol. Relays are compatible for SAS communication. Integration of SCADA is not in ABB scope. | In case offered relays are IEC 61850 based and direct communication with IEC 61850 based SAS is possible, converter is not envisaged. In any other case, suitable converter and other accessories for connection with IEC 61850 based SAS is also included in the scope of the bidder.
27 | Technical specifications for 33kV & 11kV GIS | Clause No. 3.09.01 page no. 8/22 Numerical Transformer Protection Relay | We understand that, this shall be part of the upstream breaker. Hence, not considered in 11kV GIS scope. | This relay shall be provided for all transformer feeders to be supplied under present scope.
28 | Technical specifications for 33kV & 11kV GIS | Clause No. 3.10, page 10 of 21 3.10 Painting Painting of panels shall be as specified in Section-GTR | Painting : We have offered panels made up of special material called "Alu Zinc". Alu Zinc is light in weight, has more strength, and extremely corrosion resistant compared to normal CRCA sheets and this does not require any surface treatment like powder coating. Panels shall be made up of Alu Zinc material except front doors & end covers which shall be painted sheet steel. We shall provide powder coated paint only for front doors and end covers, which shall be made of CRCA sheet. However, painting procedure and thickness shall be as per our standard procedure. | Alu Zinc material shall be acceptable for 11kV Switchgear panels except for doors, end covers & bottom gland plates for which requirements of Technical Specifiations shall prevail. However, Painting procedures & thickness of all materials other than Alu Zinc shall be as per requirement of Technical Specifications.
29 | Technical specifications for 33kV & 11kV GIS | Clause No. 7-5.page no. 12/22 ON/OFF indicators for AIS Line Isolator & Line Earth Switch | Please note we have offered GIS panels without any line side disconnector and earth switch as the same is not required technically as the feeder earthing in GIS is via bus side three position switch through circuit breaker. | Bidders understanding is generally in order.
30 | Technical specifications for 33kV & 11kV GIS | Clause No. 7 -10. page no. 12/22 Control Switches for Three position GIS Isolator & Earth switch (Electrical) | Kindly note the controlling of three position switch shall be provided via relay. Separate control switches not envisaged. | Acceptable provided other functional reqirements of technical specifications are fulfilled.
31 | Technical specifications for 33kV & 11kV GIS | Clause 7.0 Note -5 Location of VT (I/C or B/S Panel) shall be decided during detail engineering. | Bus VT is not shown as per SLD hence not considered. And as per SLD (Section project package-1; Annexure-A & B : SLD) Line VT is considered in all panels | Requirement of Technical Specification shall prevail.
32 | Technical specifications for 33kV & 11kV GIS | Clause 8 Type Tests Page 13/21 Clause 8.01-A.h Test to verify pressure relief operation of the panel (During internal arc test) | Kindly note as per IEC, this test is not applicable and mentioned in the internal arc section . Pressure withstand test is a separate test in IEC wherein 1.3 times rated pressure is applied to test the integrity of the gas filled compartment . Hence, request to kindly remove this test as the same is not applicable. Alternatively, kindly consider "Pressure Withstand test for Gas Filled Compartments with pressure relief device" instead of the mentioned test. | Internal Arc Test & Pressure withsatnd tests (as per IEC 62271-200:2024) shall be acceptable.
33 | Technical specifications for 33kV & 11kV GIS | Clause 8.01 A, page no. 13/22 Switchgear panel j) Short circuit withstand test of earthing device | Please note as the offered 3position switch cum disconnector cum earth switch is an off load switch. Hence, the type test report is not applicable. | Requirement of Technical Specification shall prevail.
34 | Technical specifications for 33kV & 11kV GIS | Clause 8.02 page no. 13/22 Routine Test | All routine tests shall be as per ABB standards | Requirement of Technical Specification shall prevail.
35 | Technical specifications for 33kV & 11kV GIS | Clause 8.02 page no. 13/22 The manufacturer shall furnish a detailed Quality Plan indicating the practice and procedure along with relevant supporting documents. | QAP shall be provided for your reference DDE | Requirement of Technical Specification shall prevail.
36 | Technical specifications for 33kV & 11kV GIS | Clause No. 9, page no. 17/22 d) LT Transformer Feeder 2. CT Ratio LT Trafo feeder- 40-20A Burden 7.5VA | Such lower CT ratio is not possible to accommodate in GIS CT due to size constraint, minimum possible CT ratio shall be 200A with burden 2.5VA. | CT of higher current rating is acceptable, provided other functional requirements of Technical Specifiations are fulfilled, without any additional price implications. However, tapping at ratios as defined in Technical Specification shall also be provided.
37 | Technical specifications for 33kV & 11kV GIS | 11KV CT CT Class: 0.2S | According to the amendment in "Technical Specification, Section – Project (Rev.00) C/ENGG/SPEC/PANG/PROJECT/GIS, Rev 0": (D) 11 kV Current Transformers metering core accuracy class shall be 0.5S instead of 0.2S class as given at clause no 9.0 on page 19 of 21. We have complied with this amendment. | Noted.
38 | Technical specifications for 33kV & 11kV GIS | Clause No. 10.00, page no. 21/22 Bus VT FUSE Fail | PT are of plug in desing hence HV fuses are not possible at primary circuit of PT in GIS. MCB's shall be provided in the secondary side of the PT. | In such case MCB monitoring shall be provided in place of fuse fail to SAS.
39 | Technical specifications for 33kV & 11kV GIS | Clause No. 12.00, page no. 21/22 2. ON/OFF Indicator for CB(Mechanical) 3. ON/OFF Indicator for GIS Isolator/Earth Switch(Mechanical) | mechanical ON/Off indication is part of operating mechanism. Hence this parts are not available as standard spares. | Based on OEM deisgn, in case mechanical indicator for CB, Isolator/Earthswitch is part of the operating mechanism itself, then complete mechanism shall be provided as spare against the referred item without any additional price implications. Bidder shall quote accordingly.
40 |  | Clause No. 12.00, page no. 21/22 8. Control switch for GIS Isolator 9. Control switch for GIS Earth Switch | VCB & 3 position switch shall be operated via relays hence switches are not envisaged. Hence as spares these items are not applicable | Based on OEM deisgn, in case control switch for VCB, Isolator/Earthswitch is part of the relay, then this relay shall be provided as spare against the referred item without any additional price implications. Bidder shall quote accordingly.
41 |  | Clause No. 12.00, page no. 21/22 14. Indicator for line isolator & earth switch | Please note we have offered GIS panels without any line side disconnector and earth switch as the same is not required technically as the feeder earthing in GIS is via bus side three position switch through circuit breaker. | Noted.
42 |  | 5.2 Meteorological data Page 9 of 14 Min. Temperature -28°C | The offered panel shall be suitable for the temperature range -5°C to +50. Kindly request you to confirm the minimum ambient temperature inside the switchgear room and also recommend to provide heaters inside the switchgear room to maintain the minimum temperature not less than -5°C | Heating System for 11kV Switchgear Room is included in present scope. Design of this heating syestem may be done accordingly by the bidder.
43 |  | 5.2 Meteorological data Page 9 of 14 Line-VT,BUS-VT | kindly confirm requirement of Line VT & Bus VT | Requirement of Bus VT is already included in the Technical Specifications. However, Line VTs are not envisaged in present scope.
44 |  | Relays | Please provide below details require for the relay selection. 1).Protection list Feeder wise 2).Communication protocol 3).Communication Port details 4).No. of communication port on rear side 5).DI/DO requirement As of now we have considered normal overcurrent, earth fault relay for each panel. We shall offer relay with one Rear RJ45 port for remote communication & front RJ45 port for local communication. Kindly confirm | 1) & 2) Refer Cl. 3.08 & 4.0 of Section: 33kV & 11kV Indoor Switchgear (GIS Type), Rev.00 for requirements of relays & Ethernet Switches of 11kV Switchgear. Complete design of protection system is in scope of the bidder. 3), 4) & 5) Since design of protetcion system is in scope of the bidder, these requirements shall be decided during detailed engineering based on solution offered by the bidder.
45 |  | CT-VT details | CT VT details like VA burden ,vk values to be decided during detail engg. as per CT-VT sizing calculations. Kindly provide SLD for better clarity regarding the CT-VT ratios. | Requirements of CT & VT for 11kV system is already included in the bidding documents additional parameters of instrment transformers, if required, shall be finalised during detailed engineering. Substation SLD already provided along with the Tender Drawings in the Bidding Documents.
Siemens-11 kV GIS
46 | 33kV & 11kV Indoor switchgear (GIS type).pdf | 33kV Indoor Switchgear : Cable sizes for all 3 types of feeders | We understand from the document Incomer cable runs are 2Rx3Cx95 sq.mm per phase & Outgoing LT Trafo - 1Rx3Cx300sq.mm per phase. However cable termination for Line bays is missing | Refer S. No. 3 of Amendment-1 for cable sizes of LT Transformer & incoming feeders. Further as per Cl. 3.1. o) iv) of Section: Project, the size & run of outgoing (line) feeders shall be provided at the time of detailed engineering. Bidder shall quote accordingly.
47 | 33kV & 11kV Indoor switchgear (GIS type).pdf | 33kV Indoor Switchgear : Cable sizes for all 3 types of feeders | Cable termination kit shall be quoted only for GIS end and not at other end .Also outdoor accessories not in GIS scope/also cable jointing at site not considered in GIS scope as of now. | All cable termination kits, joints & other accessories for 11kV Cables is in scope of the bidder.
48 | 33kV & 11kV Indoor switchgear (GIS type).pdf | Termination kit & all other accessories required for direct termination to the 2 nos. of Spare Outgoing feeders in 11 kV Indoor Switchgear module is included in the present scope. The size and run of 11 kV HT cables required for Outgoing (line) feeders shall be provided to the contractor at the time of detailed engineering. | Please provide cable sizes & runs at this stage only for outgoing feeders since we have to provide provision of cable sockets accordingly. Currently we are considering single run of 3C-300 sq.mm cable per phase same as per LT trafo feeder. Pls confirm. | Requirement of Technical Specification shall prevail.
49 | 33kV & 11kV Indoor switchgear (GIS type).pdf | Min temp -28°C | Min temp we can confirm is (-)25Deg deg C. Hence we request client to have space heater inside switchgear room for maintaining temperature above (-)25 deg C. | Heating System for 11kV Switchgear Room is included in present scope. Design of this heating syestem may be done accordingly by the bidder.
50 | 33kV & 11kV Indoor switchgear (GIS type).pdf | The substation shall be designed considering current ratings as indicated below: | We understand that Ratings as mentioned in section project to be followed. Since specification has different ratings. | Confirmed
51 | 33kV & 11kV Indoor switchgear (GIS type).pdf | Overall scope | Our scope is only limited to Supply of 33kV GIS panels along with 33kV GIS side Cable termination kits. Site services scope is not considered | 11kV Indoor Switchgears are envisaged under present scope. Accordingly, bidder shall quote as per provisions of Bidding documents.
52 | 33kV & 11kV Indoor switchgear (GIS type).pdf | Each circuit shall have a separate vertical panel with required compartments for circuit breaker, cable termination, main bus-bars and auxiliary control devices. | Noted, however Main busbar compartment is common per bus section and is not bay segregated | Acceptable provided other functional reqirements of technical specifications are fulfilled.
53 | 33kV & 11kV Indoor switchgear (GIS type).pdf | The Service Class Continuity of Switchgears shall be LSC 2B- PM (as per IEC 622771-200) | We confirm to LSC 2 | As per requirement for subject package, atleast LSC2A-PM or better (as per IEC 62271-200:2024) shall be provided for offered 11kV Switchgear.
54 | 33kV & 11kV Indoor switchgear (GIS type).pdf | All necessary equipment required for Gas handling at site (if any), shall be arranged by the supplier at their own cost | for 33 kV :We have considered SF6 gas required for busbar filling at site and SF6 gas handling kit shall be in the scope of site services. Currently not considered in Siemens scope. | Requirement of Technical Specification shall prevail.
55 | 33kV & 11kV Indoor switchgear (GIS type).pdf | The height of switches, pushbuttons and other hand operated devices shall not exceed 1800 mm and shall not be generally less than 700 mm. | The height of switches, pushbuttons and other hand operated devices shall not exceed 2000 mm and shall not be generally less than 700 mm. | Opearting height of max. 2000mm is acceptable.
56 | 33kV & 11kV Indoor switchgear (GIS type).pdf | Suitable base frames made out of steel channels shall be supplied along with necessary anchor bolts and other hardware, for mounting of the switchgear panels | GIS suitable for floor standing. External base frame if required is not in our scope of supply and same shall be in EPC scope of supply. We shall provide Base frame drawing during detail engg. | Requirement of Technical Specification shall prevail.
57 | 33kV & 11kV Indoor switchgear (GIS type).pdf | Thermostatically controlled space heater with common MCB shall be provided for various compartments | Applicable for LV compartment only. | Requirement of space heaters for any other compartments than LV compartment shall be based on the design of Heating System envisaged for 11kV Switchgear Room. Bidder shall quote accordingly.
58 | 33kV & 11kV Indoor switchgear (GIS type).pdf | The panel shall have Voltage Presence Indicator (VPI) to warn the operator against earthing of live connections | The warning is via lamps which are part of VPI and shall glow when the respective phase is live(1 lamp per phase) | Acceptable provided other functional reqirements of technical specifications are fulfilled.
59 | 33kV & 11kV Indoor switchgear (GIS type).pdf | All current transformers shall preferably be ring type where as voltage transformers (PT) shall be cast resin insulated type. | PT is of epoxy resin | Acceptable provided other functional reqirements of technical specifications are fulfilled.
60 | 33kV & 11kV Indoor switchgear (GIS type).pdf | All instrument transformers shall withstand the power frequency and impulse test voltage specified for the switchgear assembly | Impulse test of 170 kVP not applicable for CTs as CTs are ring type and placed around GIS enclosure. | Lightning Impulse Voltage tests on 11kV Switchgear shall be as per Cl. 7.2.7 of IEC 62271-200:2024. Bidder shall quote accordingly.
61 | 33kV & 11kV Indoor switchgear (GIS type).pdf | All Numerical relays shall have features for electrical measurements including voltage, current, power (active & reactive), frequency, power factor etc. | Voltage coil for relays shall be applicable as per technical specs for individual feeder reqt | Requirement of Technical Specification shall prevail.
62 | 33kV & 11kV Indoor switchgear (GIS type).pdf | Battery backup for real time clock in the event of power supply failure shall be provided | Same shall be confirmed during detailed engineering | Requirement of Technical Specification shall prevail.
63 | 33kV & 11kV Indoor switchgear (GIS type).pdf | Painting | Painting procedure shall be standard by means of powder coating ,paint shade shall be RAL 7035 | This shall be decided during detailed engineering complying the requirements of Technical Specification.
64 | 33kV & 11kV Indoor switchgear (GIS type).pdf | Cable entry shall generally be from the bottom; however, this shall be finalized during detail engineering. | Pls provide confirmation of cable entry at this stage only.Currently bottom cable entry is considered. | Requirement of Technical Specification shall prevail.
65 | 33kV & 11kV Indoor switchgear (GIS type).pdf | GENERAL REQUIREMENTS FOR ERECTION | We have not considered Erection activity in our scope. | Erection of 11kV Switchgear is also in scope of the bidder.
66 | 33kV & 11kV Indoor switchgear (GIS type).pdf | ON/OFF indicators for AIS Line Isolator & Line Earth Switch | Understand that AIS Line Isolator & Line Earth Switch is not in our scope of supply.We can provide ON,OFF indications in our panel which shall be connected to Aux contacts of AIS Line Isolator & Line Earth Switch.The aux contacts and wiring upto GIS panel for above shall be in client's/contractor's scope of supply | Confirmed.
67 | 33kV & 11kV Indoor switchgear (GIS type).pdf | VT(1-phase) | We understand same shall be Bus VT .We have not considered Line VT in the current requirement. | Confirmed.
68 | 33kV & 11kV Indoor switchgear (GIS type).pdf | 18. LAN/FO Cables Set AS per requirement | Note that as per specs on pg 10 for ethernet switch,Fibre optic port=2 nos i.e only reqd for connection from Switch to SCADA(ring formation).Hence,FO cables are not required within GIS switchboard and same is not in our scope of supply | LAN/FO cables required for subject package is in scope of the bidder.
69 | 33kV & 11kV Indoor switchgear (GIS type).pdf | Current Transformer - c. Lighting Impulse voltage withstand test | Impulse test of 170 kVP not applicable for CTs as CTs are ring type and placed around GIS enclosure. | Lightning Impulse Voltage tests on 11kV Switchgear shall be as per Cl. 7.2.7 of IEC 62271-200:2024. Bidder shall quote accordingly.
70 | 33kV & 11kV Indoor switchgear (GIS type).pdf | E. Switchgear Panel a. IP 4X test | IP4X applicable only for LV compartment.We confirm to maximum degree of protection of IP3XD for Swgr. | Requirement of Technical Specification shall prevail. | IP2X is acceptable as per IEC & IP3X is as per GTR
71 | 33kV & 11kV Indoor switchgear (GIS type).pdf | Control Supply Voltage | Pls provide clarity regarding control voltage for both trip-closing coil & spring charging motor. Currently we are considering 110V DC as aux voltage. | Bidder's understanding is generally in order.
72 | 33kV & 11kV Indoor switchgear (GIS type).pdf | 1. Rated primary voltage 11kV | Rated voltage of 11 kV not applicable for CTs as CTs are ring type with LV voltage levels and placed around GIS enclosure and hence free from HV stress levels(enclosure is touch proof in our design) | Noted. However, the HV side of CT shall be rated for 11kV system volatge.
73 | 33kV & 11kV Indoor switchgear (GIS type).pdf | Rated burden 7.5VA | Confirmed and same is considered on highest CT primary tapping | Noted.
74 | 33kV & 11kV Indoor switchgear (GIS type).pdf | Knee point voltage (at minimum ratio) - - 400V | Reqt of 400 V for lower tapping is stringent and is subject to CT design feasibility. Same shall be confirmed during detail engg. | Requirement of Technical Specification shall prevail.
75 | 33kV & 11kV Indoor switchgear (GIS type).pdf | Current ratio 40-20/1 A | Reqt of 40-20 A for ratio is not possible.Minimum ratio of CT shal be 100-50.CT parameters shall be confirmed during detailed engineering | CT of higher current rating is acceptable, provided other functional requirements of Technical Specifiations are fulfilled, without any additional price implications. However, tapping at ratios as defined in Technical Specification shall also be provided.
76 | 33kV & 11kV Indoor switchgear (GIS type).pdf | v) Bus VT FUSE Fail | Fuses are not applicable for VT primary side.Detailed explanation shall be provided during detailed engineering | Requirement of Technical Specification shall prevail.
77 | 33kV & 11kV Indoor switchgear (GIS type).pdf | Scope of supply | Considered as that shown within solid lines | Bidder to quote as per provisions of bidding documents.
78 | 33kV & 11kV Indoor switchgear (GIS type).pdf | External line side isolator and surge arrester | Not in scope of supply | Confirmed
79 | 33kV & 11kV Indoor switchgear (GIS type).pdf | 3.0 GIS Rev 5A,Annexure 1 Mandatory spares ,Annexure VI | We understand the mentioned documents are not directly applicable to 11kV GIS hence not reviewed. Our scope shall be limited to supply of 11kV GIS panels only. | Requirements for 11kV Current Transformer (for Bus Section bay) provided in Annexure-VI to section: Project shall be applicable for 11kV Switchgear.
80 | 33kV & 11kV Indoor switchgear (GIS type).pdf | Numerical Relay | We shall provide single Numerical relay per panel. We do not envisage separate BCU for each panel. | Refer Cl. 3.1. (I) (B) f) for scope of BCU for 11kV System. Bidder shall quote accordingly.
81 | 33kV & 11kV Indoor switchgear (GIS type).pdf | CT VT | CT VT details such as burden ,vK values shall be decided during detail engineering as per CT VT sizing calculation. | Requirements of CT & VT for 11kV system is already included in the bidding documents additional parameters of instrment transformers, if required, shall be finalised during detailed engineering. Substation SLD already provided along with the Tender Drawings in the Bidding Documents.
82 | 33kV & 11kV Indoor switchgear (GIS type).pdf | Spares | We shall only consider Mandatory spares list as mentioned in specifications. | Refer Annexure-1 to Section: Project for List of Mandatory Spares under subject package.
83 | 33kV & 11kV Indoor switchgear (GIS type).pdf | Ethernet switch | Relay shall be provided with one no. RJ45 port for remote communication same shall be connected via LAN cable up to ethernet switch in GIS panel. Rest upward communication not considered in GIS scope of supply. | Complete communication of relays & multifunction meters to SAS is in scope of the bidder.
84 | 33kV & 11kV Indoor switchgear (GIS type).pdf | SLD | Pls provide SLD as per SLD no. mentioned in the tender drawings. | Substation SLD already provided along with the Tender Drawings in the Bidding Documents.
85 | 33kV & 11kV Indoor switchgear (GIS type).pdf | Ambient temp | Pls note our switchgear is suitable for tempratures from (25-)deg to (40) deg C ambient temprature. | Heating System is envisaged for 11kV Indoor Switchgear Room. The Indoor Switchgear shall be suitable for operation under this controlled environment.
Schnedider-11 kV GIS
86 | TS_33_11 kv switchgear_GIS SECTION PROJECT | The Service Class Continuity of Switchgears shall be LSC 2B-PM (as per IEC 622771-200). | Loss of service continuity category with circuit breaker is LSC2 | As per requirement for subject package, atleast LSC2A-PM or better (as per IEC 62271-200:2024) shall be provided for offered 11kV Switchgear.
87 | TS_33_11 kv switchgear_GIS SECTION PROJECT | SF6 gas leakage rate should not exceed 0.5% per annum. | As per sealed pressure system defined in IEC 62271-1, leakage rate should not exceed 0.1% per annun. Kindly review and confirm the requirement | Requirement of Technical Specifications shall prevail.
88 | TS_33_11 kv switchgear_GIS SECTION PROJECT | ON/OFF indicators for AIS Line Isolator & Line Earth Switch | We don’t have the Isolator or earth switch on line side in our design. | Line side Isolator & Line Earthswitch not applicable for subject package.
89 | TS_33_11 kv switchgear_GIS SECTION PROJECT | Isolator with one E/S at cable side | We don’t have the Isolator or earth switch on line side in our design. | Line side Isolator & Line Earthswitch not applicable for subject package.
90 | SECTION PROJECT | For 11 kV GIS type, indoor switchgear, manufacturer’s standard design i.e busbar (SF6/Solid core/epoxy insulated), various gas chambers, placing of various equipment in the panel etc shall also be acceptable | As per the clause referred, Busbar in SF6 or busbar solid insulated both are acceptable. However, these two are distinct technologies & also the price range for GIS & Hybrid GIS are highly different. Therefore, to promote fair tender evaluation and wider participation we recommend adoption of busbar in SF6 only. You may also refer CEA Notification ( File no CEA-GO-16/3/2020-DPT Division) which says Discom should choose single technology | Bidder to quote as per provisions of bidding documents. | 66/11kV Pang Substation does not fall under DISCOM category, hence requirements of Bidding documents shall prevail.
91 | TS_33_11 kv switchgear_GIS SECTION PROJECT | Closed door operation- widely accepted industry safety feature | We recommend Manual operations of the different switches like breaker, disconnector, earthing switch of the switchgear should be possible without opening the front door. This important safety aspect is missing from the specification hence we request your consideration of the same and make part of the specification . | Closed door operation shall also be acceptable provided other functional reqirements of technical specifications are fulfilled. Bidder shall also refer to Cl. 3.01.e) of Section: 33kV & 11kV Indoor Switchgear (GIS type), Rev.00 & same shall be complied.
92 | TS_33_11 kv switchgear_GIS SECTION PROJECT | LinePT Isolation switch | Please confirm if LinePT isolation switch is required for the purpose of cable testing without the need to handle the PTs and thereby minimize the risk to operator safety | Line-side PT is not envisaged under present scope.
93 | Fire Fighting Systme | Fire Detection and Alarm system | We understand that Conventional type Fire Detection and Alarm system are to be considered for control Room Building cum 11 kV Switchgear Room, 66 kV GIS Hall (including Relay room & AHU room) Please confirm | Refer S.No. G of Annexure-IV to Section: Project & Cl. 2.03 of Section: Fire protetcion System, Rev. 6 for details of Fire detection & Alarm System to be supplied under present scope.
94 | Appendix-2, Price Adjustment, Section - VI Forms and Procedure Vol.-I of the Bidding Documents | 2.0 -works Price Component The formulae for calculating the price adjustment to be applied to the Ex-works price component of the equipment/material will be as follows: ……… …….... | supply of Disc / Porcelain Long Rod Insulator is in scope of the bidder, however, PV formula is missing in Appendix-2. Therefore, we request you to kindly incorporate PV formula for Disc / Porcelain Long Rod Insulator under the scope of these packages as per IEEMA. Please confirm and issue necessary amendment to Appendix-2. | refer Amendment No. IX to the Bidding Documents attached herewith.