| Clause No./ sections | Existing Clause/item | Amended provision |
| --- | --- | --- |

| Clause no. 2.14 of Sec- IA of TL01 | 2.14 Details of Insulator Strings with disc insulators Following disc insulator strings shall be used in the transmission line covered under the above package. All other requirement of insulators and insulator strings shall be as per Section-VIII of this specification: - Sl. No; Type of String; Size of Disc Insulator mm; Minimum Creepage distance of each disc (mm); No. of Units per String (Nos.); Electro- Mechanical Strength of Insulator Disc (kN); Mechanical Strength of Insulator String along with Hardware Fittings (kN). 1; Single “I” suspension pilot; 255-280 x 145; 370; 1 x 25; 120; 120. 2; Double Tension; 255-280x 170; 370; 2 x 22; 160; 2 x 160. 3; Double I Suspension; 255-280 x 145; 370; 2x25; 120; 2x120. | 2.14 Details of Insulator Strings with disc/Porcelain long rod insulators Following insulator strings shall be used in the transmission line covered under the above package. All other requirement of insulators and insulator strings shall be as per Section-VIII of this specification: - - Details of Insulator Strings with disc insulators Sl. No; Type of String; Size of Disc Insulator mm; Minimum Creepage distance of each disc (mm); No. of Units per String (Nos.); Electro- Mechanical Strength of Insulator Disc (kN); Mechanical Strength of Insulator String along with Hardware Fittings (kN). 1; Single “I” suspension pilot; 255-280 x 145; 370; 1 x 25; 120; 120. 2; Double Tension; 255-280x 170; 370; 2 x 22; 160; 2 x 160. (b) Description of long rod insulator string (equivalent to standard disc insulator) Sl. No.; Type of string; Size of long rod insulators (mm); Minimum creepage distance of each unit (mm); No. of individual units per string; Electro-mechanical strength of insulator disc(KN); Mechanical strength of insulator string along with hardware fittings (KN). 1.; Single ‘I’ suspension pilot; 60-75; 4625; 1 x 3; 120; 120. 2.; Double Tension; 75-85; 4070; 2 x 3; 160; 2 x 160. |
| --- | --- | --- |
| Clause no. 3.0 of Sec- IA of TL01 | - 3.0 Different Sections to Technical Specification - For the purpose of present scope of work, technical specification shall consist of following parts and they should be read in conjunction with each other: - Sl. No.; Section Number; Name of Section; Rev No.. 1; Section-IA; Scope; Rev-3 (Jan’2022). 2; Section-IB; General Information; Rev-4 (April’2022). 3; Section-II; General Technical Conditions; Rev-2 (Feb’2022). 4; Section-III; Survey and Soil Investigation; Rev-2 (Jan’2022). 5; Section-IVA; Tower Design; Rev-4 (April’2022). 6; Section-IVB; Tower Testing; Rev-1 (Sept’2021). 7; Section-IVC; Fabrication, Erection and Stringing; Rev-3 (Feb’2022). 8; Section-IVD; Foundation (Contractor’s Design); Rev-3 (April’2022). 9; Section-IVE; Foundation (Employer’s Design); Rev-2 (Jan’2022). 10; Section-VIA; HARDWARE FITTINGS & ACCESSORIES FOR CONDUCTOR & EARTHWIRE; Rev-2 (Jan’2022). 11; Section-VIIIB; DISC INSULATORS; Rev-0 (April’2022). 12; Section-X; OPGW; Rev-0 (June’2021). 13; Section-XI; Drawings; Rev-0 (June’2021). 14; Section-XII; FAQ; Rev 0 (June’2021). | - 3.0 Different Sections to Technical Specification - For the purpose of present scope of work, technical specification shall consist of following parts and they should be read in conjunction with each other: - Sl. No.; Section Number; Name of Section; Rev No.. 1; Section-IA; Scope; Rev-9 (Mar’2024). 2; Section-IB; General Information; Rev-9 (Feb’2024). 3; Section-II; General Technical Conditions; Rev-2 (Feb’2022). 4; Section-III; Survey and Soil Investigation; Rev-5 (Dec’2023). 5; Section-IVA; Tower Design; Rev-6 (Dec’2023). 6; Section-IVB; Tower Testing; Rev-3 ( Dec’2023). 7; Section-IVC; Fabrication, Erection and Stringing; Rev-7 (Dec’2023). 8; Section-IVD; Foundation (Contractor’s Design); Rev-6 (Dec’2023). 9; Section-IVE; Foundation (Employer’s Design); Rev-5 (Dec’2023). 10; Section-VIA; HARDWARE FITTINGS & ACCESSORIES FOR CONDUCTOR & EARTHWIRE; Rev-3 (Dec’2023). 11; Section-VIIIB; DISC/PORCELAIN LONG ROD INSULATORS; Rev-0 (April’2022). 12; Section-X; OPGW; Rev-1 (June’2024). 13; Section-XI; Drawings; Rev-1 (Dec’2023). 14; Section-XII; FAQ; Rev 0 (June’2021). |
| BPS PRICE SCH-1 & 2 | SR. NO.; ACTIVITY DESCRIPTION; MATERIAL CODE; DESCRIPTION; UNIT; QTY. 37; Insulator; 1000000624; 120KN AC Disc Insulator; EA; 3225. 38; Insulator; 1000001057; 160KN AC Disc Insulator; EA; 30624. | SR. NO.; ACTIVITY DESCRIPTION; MATERIAL CODE; DESCRIPTION; UNIT; QTY. 37; Insulator; 1000076490; 25 nos of 120KN AC Porcelain Disc Insulator/3 nos of 120KN AC Porcelain Long Rod Insulators (220KV).; SET; 129. 38; Insulator; 1000076491; 22 nos of 160KN AC Porcelain Disc Insulator/3 nos of 160KN AC Porcelain Long Rod Insulators (220KV).; SET; 1392. |
| TS(Vol-II)- Sec-VIIIB, | In view of the above Amendments, the file namely ‘08_2 Section VIIIB Disc Insulators’ stand replaced with file namely ‘TS(Vol-II)-Sec-VIIIB R2’. (attached herewith) |  |
| Second Envelope and Bid Forms | In view of the above Amendments, the ‘Price_schedule’ excel sheet stand revised as ‘Price_schedule_Rev02’. Note- Bidders are requested to consider the revised excel sheet(s) titled “Price Schedule_Rev02” for bid preparation/submission for the subject package. |  |