## TL01
Clarification No.- I dated 09/10/2024 to the Bidding Documents for Transmission Line Tower Package- TL01 for 220 kV S/C (on D/C Tower) Pang- Upshi line (Part-1) and establishment of new 2 x 10 MVA 66/11kV GIS Sub Station at Pang for 220kV AC Transmission line between Pang and Phyang associated with Transmission system for evacuation of RE power from renewable energy parks in Leh (5 GW Leh-Kaithal transmission corridor).; Spec. No: CC/NT/W-TW/DOM/A06/24/11961
Sl no. | Re. Clause no. | Existing provision | Bidder's Query/Comment | POWERGRID Reply
1 | Technical specification Volume II Section 1A, Clause : 2.14.1 Conductor & OPGW for 220 kV line | Conductor & OPGW for 220 kV line | Cross section area, Modulus of elasticity and coefficient of thermal expansion details are not included. Kindly add details for ACSR DEER conductor. | Bidder may refer Amedment No-II
2 | Technical specification Volume II Section 1A, Clause 2.8 | Grillage Foundation | As per specification contractor may adopt grillage type foundation however in price schedule grillage type foundation not included. We understood that, If grillage type foundation required during project execution, PGCIL will provide the foundation design & drawing of the same. Please clarify. | Bidder's understanding is correct.
3 | Technical specification Volume II Section 1A, Clause 2.9 | Avalanche Protection | As specified in specification “The drawings for avalanche protection structure and tower foundation for avalanche protection (raised chimney foundation up to 9.5 m with/ without tie beam) shall be released to the contractor during execution stage”. For towers and foundation designs which included in bidders’ scope, there is no any additional loading consideration or structural provision required due to avalanche protection. Kindly clarify. | Bidder's understanding is correct.
4 | Technical specification Volume II Section 1A, Clause 2.11 | Use of Helicopter/ Helicrane for Transportation of Transmission Line materials from site store to tower location | We understood that Helicopter/Helicrane to be used for material transportation only. Assembly of tower panels to be done at tower location. Lifting of tower panels and tower erection with use of Helicopter/Helicrane not required. Kindly clarify. If lifting of tower panels required for erection purpose with use of Helicopter / Helicrane, kindly provide details of additional loading or additional provisions which are to be consider in tower design/drawing. | Bidder may refer clause no. 2.11 of Section -IA (Vol-II)
5 | General Queries |  | Request you to provide the kmz file for route of all three packages. | Link for the same is shared with this clarification. The shared KMZ file is for reference only. However, Bidders may visit the line route to acquaint themselves with terrain conditions and associated details of the proposed transmission lines.
6 | General Queries |  | Request you to provide Sag Tension Calculations. | The data shall be provided to successful bidder.
7 | General Queries |  | Request you to kindly provide Tower Spotting data. | The data shall be provided to successful bidder.
8 | General Queries |  | Request you to provide the Tower Outline Diagrams for towers which are in PGCIL scope. | Tower outline diagram enclosed in the drawing section of TS Vol-II may be refered.
9 | Technical specification Volume II Section 1A, Clause : 2.14.1 Conductor & OPGW for 220 kV line TL01 | Conductor & OPGW for 220 kV line | For ACSR Deer Conductor, Conductor spacing, Cross sectional area, Modulus of Elasticity and Coefficient of Thermal expansion have not been provided. Please provide the inputs. | Bidder may refer Amedment No -II other than conductor spacing. Transmission line envisaged under the package is single deer conductor. However, for phase to phase clearance, bidder may refer provision of TS/ IS 5613.
10 | General Query |  | Kindly provide the kmz file for the routes | Link for the same is shared with this clarification. The shared KMZ file is for reference only. However, Bidders may visit the line route to acquaint themselves with terrain conditions and associated details of the proposed transmission lines.