## .
Clarification No.- IV dated 28/10/2024 to the Bidding Documents for Transmission Line Tower Package- TL01 for 220 kV S/C (on D/C Tower) Pang- Upshi line (Part-1) and establishment of new 2 x 10 MVA 66/11kV GIS Sub Station at Pang for 220kV AC Transmission line between Pang and Phyang associated with Transmission system for evacuation of RE power from renewable energy parks in Leh (5 GW Leh-Kaithal transmission corridor).; Spec. No: CC/NT/W-TW/DOM/A06/24/11961
Sr. No. | Bidders Query no | Clause No / Page No | Description as per Bid Document | Bidder’s Queries | POWERGRID Reply
1 |  | 2 | 3 | 4 | 5
1 | 1 | Technical specification for 400kV GIS (GIS-REV 5A) Clause 5.2 c | 66kV GIS | Said clause states that "c. These compartments shall be such that maintenance on one feeder may be performed without de-energising the adjacent feeders." As offered GIS is single busbar scheme, this clause of service contunuity is not applicable. Please confirm. | Bidder to comply the requirement of Bidding document.
2 | 2 | Technical specification for 400kV GIS (GIS-REV 5A) Clause 5.21 | 66kV GIS / VFTO | As requirement is of 72.5 kV GIS, the effect of VFTO is negligible. Considering the said, we request PGCIL to exclude VFTO study from scope of deliverables. | Please refer clause no: 5.4 (xviii) of TS- GIS(Rev 05A).
3 | 3 | Technical specification for 400kV GIS (GIS-REV 5A) | 66kV GIS / CB | We understand that as the requirement is for three phase encapsulated GIS CB, which shall be electrically/mechanically ganged with common CB drive mechanism, the requirement of single phase auto reclosing is not applicable for Line and/or Transformer bays. Kindly confirm the same. | Please refer clause no: 3.1(B) ( e ) of TS, Section – Project (Rev.00) and TECHNICAL SPECIFICATION of Circuit Breaker in TS-33kV & 11kV Indoor Switchgear (GIS Type) Bidder to comply the requirement of Bidding document.
4 | 4 | Clarification-II, Sr.27 | Creepage | As per clarification-II, creepage of 31mm/kV shall be applicable for Insulator strings/Long rod insulators and outdoor bushings. Please confirm that outdoor bushings shall be only for Transformer. All other outdoor equipment including SF6 Gas-Air bushing shall be with 25mm/kV. Please confirm. | Creepage of 31mm/kV shall be applicable for Insulator strings /Long rod insulators and outdoor bushings including SF6 to Air bushing (wall bushing)
5 | 5 | Clarification-II, Sr.28, Amendment-III Sr.6 | Heating and ventilation | As per Amendment-III, minimum temperature has been revised to -35degC. Thi shall be applicable for all outdoor equipent and faclilties. However as in all buildings including GIS Hall, Panel area, Switchgear room, DG room etc, temperature shall be maintained upto -10 degC. Hence for all indoor switchgears, Panels, Distribution Boards etc temperature limit of -10degC shall be applicable. PLease review and confirm as vendors have expressed inabilty for suitabilty for temperatures below -25degC. | Please refere Annexure-III to TS, Section – Project (Rev.00) for heating and ventilation system requirement.
6 | 6 | Technical specification for 400kV GIS (GIS-REV 5A) | 66kV GIS / Bushings | Pleas confirm that horizontally mounted bushings on GIS building are acceptable. | Bidder to comply the requirement of Bidding document.
7 | 7 | Annexure-1 Mandatory Spares - 66kV GIS - 3.1 Disconnecting switches/Earthing switches | Spares for 66kV GIS DS/ES | As per Annexure-1, Sr. 3.1, Two sets of 1250A, 3 Phase 1250A Disconnecting switches are mentioned. Please confirm whether PGCIL requires 02 nos of DS of each type for one to one replacement OR Total 2 nos DS such that same can be used for replacement of any of offered DS. | Please refer clause no:9.0 of TS, Section – Project (Rev.00).
8 | 8 | Technical specifications for 33kV & 11kV GIS, Clause No. 9, d) LT Transformer Feeder | CT Ratio LT Trafo feeder- 40-20A Burden 7.5VA | As per panel manufacturers, CTs with such lower ratio is not feasible to provided as same are can not be accommodates in GIS panel due to size constraint. Minimum possible CT ratio shall be 100 / 200A. Other CT parameters can be confirmed during detailed engineering only. Please review and confirm. | Bidder to comply the requirement of Bidding document.
9 | 9 | Technical specifications for 33kV & 11kV GIS, Clause No. 9 | 11KV CT Parameters | According to the amendment in "Technical Specification, Section – Project (Rev.00) C/ENGG/SPEC/PANG/PROJECT/GIS, Rev 0": (D) 11 kV Current Transformers metering core accuracy class shall be 0.5S instead of 0.2S class as given at clause no 9.0 on page 19 of 21. Please confirm. | Bidder to comply the requirement of Bidding document.
10 | 10 | Technical specifications for 33kV & 11kV GIS, Clause No. 9, Clause No. 12.00 | Line isolator & earth switch | Panel manufacturers are offering GIS Panels without Line side earth switches as per their type tested product.. Line side earthing switch is not required, as the feeder earthing in GIS is via bus side three position switch through circuit breaker. Please review and accept. | Bidder to comply the requirement of Bidding document.
11 | 11 | Technical specifications for 33kV & 11kV GIS, Clause No. 9, Clause No. 10.00 | Bus VT | PTs shall be plug in desing for GIS, hence HV fuses are not feasible at primary circuit of PT in GIS. Instead MCB's can be provided in the secondary side of the PT. Please review and confirm. | Bidder to comply the requirement of Bidding document.
12 | 12 | Technical specifications for 33kV & 11kV GIS, 3.01- f)Clarification-II, Sr.39 | 11kV GIS - Service continuity | All GIS panel vendors are complying to LSC2 as per their standard type tested product. Please review and accept. | Bidder to comply the requirement of Bidding document.
13 | 13 | Refer Amendmend No-III for Clause 3.1 (III) Civil works, (II) (2) (V) - 2. 66 kV GIS building: (V) | Wall sheeting - PEB GIS builidng with brickwork | For Brickwork upto 3m height - To be covered with 2 nos of 80 mm thick sandwitched puff panels with additonal insulated material inbetween panels. For Height above Brickwork - To be covered with 2 nos of 80 mm thick sandwitched puff panels with additonal insulated material inbetween panels. For Roof - To be covered with 2 nos of 80 mm thick sandwitched puff panels with additonal insulated material inbetween panels. (Roof Slope to be maintained) . Please confirm. | Confirmed
14 | 1 | SCHEDULE OFRATES AND PRICES: Schedule:- 1 & 2 | BATTERY & BATTERY CHARGER And Mandatory Spares(AIS) | As per the price schedule, we understand that only 110V batteries are within the scope of works. However, for item no. 84, which refers to spares for 220V batteries, we believe this may be a typographical error. Kindly confirm if this item should refer to spares for 110V batteries instead.As 48V Batteries are Not in scope we understand there is no requirement of item no 86 as per price schedule -Spares for 48V Batteries | Please refer Amendment-III
15 |  | 5.2 | c. These compartments shall be such that maintenance on one feeder may be performed without deenergising the adjacent feeders | As offered GIS is single busbar scheme, this clause of service contunuity is not applicable | Bidder to comply the requirement of Bidding document.
16 | 2 | 5.21. | The GIS shall be designed, so as to take care of the VFT over voltages generated as a result of pre-strikes and re-strikes during isolator operation. Maximum VFT over voltages peak shall not be higher than rated lightning impulse withstand voltage (LIWV) of the equipment.Necessary measures shall be under taken by GIS manufacture to restrict maximum VFT over voltages lower than the LIWV. Manufacturer shall submit the study report of VFTO generated for GIS installation. | As requirement is of 72.5 kV GIS, the effect of VFTO is negligible. Considering the said, we request PGCIL to exclude VFTO study from scope of deliverables. | Please refer clause no: 5.4 (xviii) of TS- GIS(Rev 05A) regarding VFTO study requirement.
17 | 6 | Annexure I | Reclosing : Single phase &Three phase auto reclosing | We understand that as the requirement is for three phase encapsulated GIS CB, which shall be electrically/mechanically ganged with common CB drive mechanism, the requirement of single phase auto reclosing is not applicable. Kindly confirm the same. | Please refer clause no: 3.1(B) ( e ) of TS, Section – Project (Rev.00) and TECHNICAL SPECIFICATION of Circuit Breaker in TS-33kV & 11kV Indoor Switchgear (GIS Type). Bidder to comply the requirement of Bidding document.
18 | 2 |  | Wall bushing | The offered SF6-Air bushing shall be mounted horizontally and shall be suitable for customer applications. Request to kindly review and confirm. GTP for same is enclosed as part of technical offer. | Bidder to comply the requirement of Bidding document.
19 | 4 | BOQ | 3-phase of 1250A disconnector switch including main circuit, enclosure, driving mechanism and support insulator etc., complete in all respect as per TS | For the said clause we infer that PGCIL requires 02 nos of DS of each type for one-one replacement. Please confirm. | Please refer clause no:9.0 of TS, Section – Project (Rev.00).
20 | 1 |  |  | 66 KV GIS Specifications are not available in tender documents. Please arrange the same. | Please refer Amendment-III
21 | 2 | - | - | As per 3.0 GIS Rev-5A attachment, minimum temperature for equipment is 0°C but as per site parameters it is -28°C. Please confirm which temperature is to be considered by manufacturers. | Please refer Amendment-III
22 | 3 | - | - | Please clarify that the 2 set of Insulating Oil required for 10 MVA Transformer is part of Transformer or required extra other than first fill. | Bidder to quote as per BPS meeting the requirement of TS.
23 | 4 |  |  | JDU - Please clarify if JDU wit manufacturer is required or not. As per section-ll ITB clause 9, (vii) it is required. But in qualification requirement in Annexure-A (BDS) it is not mentioned. | Provisions of Bidding Documents are amply clear.
24 | 1 | Technical specification for 400kV GIS (GIS-REV 5A) - 2.3 | The equipment offered shall be protected against all types of voltagesurges and any equipment necessary to satisfy this requirement shall deemed to be included. | We understand that surge arrestors are required to cater the requirement and are of AIS type. | Bidder to comply the requirement of Bidding document.
25 |  | Technical specification for 400kV GIS (GIS-REV 5A)-5.2 | c. These compartments shall be such that maintenance on onefeeder may be performed without de-energising the adjacent feeders. | As offered GIS is single busbar scheme, this clause of service contunuity is not applicable. | Bidder to comply the requirement of Bidding document.
26 | 2 | Technical specification for 400kV GIS (GIS-REV 5A)-5.21 | The GIS shall be designed, so as to take care of the VFT over voltages generated as a result of pre-strikes and re-strikes during isolator operation. Maximum VFT over voltages peak shall not be higher than rated lightning impulse withstand voltage (LIWV) of the equipment. Necessary measures shall be under taken by GIS manufacture to restrict maximum VFT over voltages lower than the LIWV. Manufacturer shall submit the study report of VFTO generated for GIS installation. | As requirement is of 72.5 kV GIS, the effect of VFTO is negligible. Considering the said, we request PGCIL to exclude VFTO study from scope of deliverables. | Please refer clause no: 5.4 (xviii) of TS- GIS(Rev 05A) regarding VFTO study requirement.
27 | 6 | Technical specification for 400kV GIS (GIS-REV 5A)-Annexure-1 | Reclosing : Single phase &Three phase auto reclosing. | We understand that as the requirement is for three phase encapsulated GIS CB, which shall be electrically/mechanically ganged with common CB drive mechanism, the requirement of single phase auto reclosing is not applicable. Kindly confirm the same. | Please refer clause no: 3.1(B) ( e ) of TS, Section – Project (Rev.00) and TECHNICAL SPECIFICATION of Circuit Breaker in TS-33kV & 11kV Indoor Switchgear (GIS Type). Bidder to comply the requirement of Bidding document.
28 | 1 |  | CT parameters | Please find enclosed CT and VT parameters. Request customer confirmation on same. Any changes in the same shall be discussed for technical feasibilty and may have price and time implications. | Please refer Amendment-III
29 | 2 |  | Wall bushing | The offered SF6-Air bushing shall be mounted horizontally and shall be suitable for customer applications. Request to kindly review and confirm. GTP for same is enclosed as part of technical offer. | Please refer clause no: 4.6 of Technical Specification: GTR (Rev No:15) for system parameter of 66kV. For other parameters, please refer Annexure -6 of TS-GIS 5A, TECHNICAL PARAMETERS of 132kV SF6/AIR BUSHING. The necessary altitude correction factor shall be applicable for all outdoor insulations.
30 | 3 | BOQ | TESTING & MAINTENANCE EQPT FOR GIS | Optional prices for same shall be provided. | Bidder to comply the requirement of Bidding document
31 | 4 | BOQ | 3-phase of 1250A disconnector switch including main circuit, enclosure, driving mechanism and support insulator etc., complete in all respect as per TS. | For the said clause we infer that PGCIL requires 02 nos of DS of each type for one-one replacement. Please confirm. | Please refer clause no:9.0 of TS, Section – Project (Rev.00).
32 | 1 | 5.2,GIS Specification | c. These compartments shall be such that maintenance on one feeder may be performed without de-energising the adjacent feeders. | As offered GIS is single busbar scheme, this clause of service contunuity is not applicable. | Please refer the clarifications-II.
33 | 2 | 5.2,GIS Specification | The GIS shall be designed, so as to take care of the VFT over voltages generated as a result of pre-strikes and re-strikes during isolator operation. Maximum VFT over voltages peak shall not be higher than rated lightning impulse withstand voltage (LIWV) of the equipment. Necessary measures shall be under taken by GIS manufacture to restrict maximum VFT over voltages lower than the LIWV. Manufacturer shall submit the study report of VFTO generated for GIS installation. | As requirement is of 72.5 kV GIS, the effect of VFTO is negligible. Considering the said, we request PGCIL to exclude VFTO study from scope of deliverables. | Please refer the clarifications-II
34 | 3 | Annexure I | Reclosing : Single phase &Three phase auto reclosing. | We understand that as the requirement is for three phase encapsulated GIS CB, which shall be electrically/mechanically ganged with common CB drive mechanism, the requirement of single phase auto reclosing is not applicable. Kindly confirm the same. | Please refer the clarifications-II
35 | 4 | Annexure I | Wall bushing | The offered SF6-Air bushing shall be mounted horizontally and shall be suitable for customer applications. Request to kindly review and confirm. GTP for same is enclosed as part of technical offer. | Please refer the clarifications-II
36 | 5 | BOQ | 3-phase of 1250A disconnector switch including main circuit, enclosure, drivingmechanism and support insulator etc., complete in all respect as per TS. | For the said clause we infer that PGCIL requires 02 nos of DS of each type for one-one replacement. Please confirm. | Please refer the clarifications-II
37 | 6 | General | HVAC specifcation | We have considered split AC for Control Room,Battery Room,Office Room and Conference Room of Control Room Building.Further Split AC is considering for Relay Panel Room of GIS building only.No other room is considered for Air Conditioning. Please Confirm. | Please refer clause no: h(i) of TS - Section Project (Rev00)
38 | 7 | General | HVAC specifcation | Air- Conditioning heat load calculation shall be done on the basis of max site temperature and unit will statisfactory work upto ambient temperature. Please confirm. | Bidder to quote meeting the requirement as per TS.
39 | 8 | General | HVAC specifcation | The ventilation of the GIS hall shall be of a positive pressure type with minimum 2 air changes per hour. The pressure inside the GIS hall shall be maintained 5 mm of water above the atmospheric pressure.As we are taking only 20% outside fresh air, rest 80% is recirculation of inside air, so it is not possible to maintain 5mmwc positive pressure inside GIS Hall. For hilly area there is no dusty atmosphere, so 10Pa is sufficient just to restrict flow of outside air to inside. Pls accept the same. | Please refer the clarifications-II
40 | 9 | General | HVAC specifcation | For GIS Hall, only ventilation is considered. For Winter condition when temperature goes below 0 deg C, 20% fresh air (of GIS Hall Volume) is considered along with recirculation of air through Manual Damper. Pls Confirm. | Please refer the clarifications-II
41 | 10 | General | HVAC specifcation | To optimize the Battery sizing, battery room inside temperature shall be maintained between 20 - 24 deg C with Hot & Cold type AC units (working & standby) and battery design shall be done considering inside battery room temperature. Pls confirm. | Bidder to quote meeting the requirement as per TS.
42 | 11 | General | HVAC specifcation | During inspection, load test is conducted at shop and free run test for EOT Crane is conducted at site. Please confirm. | Please refer clause no:17.14 of TS - GIS 05A regarding tests shall be carried out on EOT Crane.
43 | 12 | General | HVAC specifcation | We assume that there is Provision in the SCADA to have signals of AC system and Fire fighting system as per TS. pls confirm. | Bidder to quote meeting the requirement as per TS.
44 | 13 | General | HVAC specifcation | Heat tracing system with insulation and aluminium sheet is considered for all water supply lines along with potable water tank. Pls confirm. | Bidder to quote meeting the requirement as per TS.
45 | 14 | General | Fire Fightig specifcation | Instead of portable water type 9 ltr extinguisher, we have considered DCP type 6 Kg portable extinguisher. Pls confirm. | Bidder to quote meeting the requirement as per TS.
46 | 15 | General | Fire Fightig specifcation | We understand that only Fire detection alarm system, Fire extinguisher system and NIFPS system (for Power Transformer) is envisaged for this tender. Please confirm. | Please refer claus no: K of TS-Section project (Rev00) regarding requirement of Fire detection and alarm system.
47 | 16 | Section Project Clause no. 3 3.1,(I),(B),k,(ii) | Fire Fightig specifcation | "Conventional type Smoke detection, Fire alarm & Annunciation System and Fire extinguishers for DG set building" is required as per Section Project. Same is not mentioned in BPS. Please confirm. | Fire alarm & Annunciation System not envisaged for DG set building. Bidder to quote as per BPS meeting the requirement as per TS.

## Sheet1 (hidden)
11KV XLPE CABLE TERMINATION EQUIPMENT ALONG WITH STRUCTURE ACCESSORIESFOR OUT DOOR TERMINATION (ONE SET CONSISTS OF COMPLETE & REQUIREMENTFOR ONE BAY) | SET | 2
11KV 3CX300SQMM XLPE AL ARMOURED CABLE | KM | 0.25
11KV XLPE CABLE TERMINATION EQUIPMENT ALONG WITH STRUCTURE ACCESSORIESFOR OUT DOOR TERMINATION (ONE SET CONSISTS OF COMPLETE & REQUIREMENTFOR ONE BAY) | SET | 6
11KV 3X95SQMM XLPE AL ARMOURED CABLE | KM | 0.4