| S. No. | Clause/ Drg. Sl. NO | Existing provision | Amended provision as Per Amendment-1 |
| --- | --- | --- | --- |
| 1. | TS-Section Project(Rev00) SECTION PROJECT Clause 3.1 (III) Civil works, (II) (2) | Clause no: 3.1 (III) Civil works, (II) (2) (V) 2. 66 kV GIS building: - ------. - -------. - -------. - -------. - New Claus added. | Clause 3.1 (III) Civil works, (II) (2) (V) Modified as 2. 66 kV GIS building: - ------. - ------. - -------. - ------- - Brickwork of minimum height of 3.0 m from FFL and 80mm thick sandwiched puff panel shall be provided in two layers with cavity in between to provide heat insulation. For the remaining height above 3.0 m, 80 mm thick sandwich panel shall be installed in two layers, maintaining the cavity in between for additional heat insulation. |
| 2. | TS-Section Project (Rev00) | Existing Clause no: 3.1 (I) (B) (d): Erection Hardware: Conductor(s), Al tube, bus-bar materials, cable trays & covers, Bay MB, spacers, clamps & connectors, junction box, earthwire, earthing material risers, auxiliary earthmat (excluding main earth mat), buried cable trenches/pipes for equipment & lighting, cable supporting angles/channels, insulating mats, cable sealing arrangement, insulator guy arrangement, all accessories etc. as required for the substation. Erection Hardware of a bay shall also include Earthing Materials and Clamps & Connectors for Transformers of that respective bay. | Existing Clause no: 3.1 (I) (B) (d) modified as: Erection Hardware: This item of BPS including Insulator strings, Conductor(s), Al tube, bus-bar materials, cable trays & covers, Bay MB, spacers, clamps & connectors, junction box, earthwire, earthing material risers, auxiliary earthmat (excluding main earth mat), buried cable trenches/pipes for equipment & lighting, cable supporting angles/channels, insulating mats, cable sealing arrangement, insulator guy arrangement, all accessories etc. as required for the substation. Erection Hardware of a bay shall also include Earthing Materials and Clamps & Connectors for Transformers of that respective bay. |
| 3. | TS-Section Project (Rev00) | Existing Clause no: 3.1(o): ----- - 11 kV, 1 run per phase – 3C x 300 Sqmm, XLPE AL cable (From 11 kV indoor switchgear panel to Six nos. of 630 KVA, 11/0.433kV LT transformer for auxiliary supply of substation) along with outdoor termination arrangement including cable support structure (if required) and all accessories as required for termination is in the present scope of work. - 11 kV, 2 runs per phase – 3C x 95 Sq.mm XLPE Al cable (From 11 kV side of 66/11 kV transformer to 11 kV Indoor GIS Switchgear) along with outdoor termination arrangement including structure (if required) and all accessories as required for termination is in the present scope of work - ----- - Termination kit & all other accessories required for direct termination to the 2 nos. of Spare Outgoing feeders in 11 kV Indoor Switchgear module is included in the present scope. The size and run of 11 kV HT cables required for Outgoing (line) feeders shall be provided to the contractor at the time of detailed engineering. - ------ | Existing Clause no: 3.1(o) Modified as: ------ - 11 kV, 1 run per phase – 3C x 95 Sqmm, XLPE AL cable (From 11 kV indoor switchgear panel to Six nos. of 630 KVA, 11/0.433kV LT transformer for auxiliary supply of substation) along with outdoor termination arrangement including cable support structure (if required) and all accessories as required for termination is in the present scope of work. - 11 kV, 2 runs per phase – 3C x 300 Sq.mm XLPE Al cable (From 11 kV side of 66/11 kV transformer to 11 kV Indoor GIS Switchgear) along with outdoor termination arrangement including structure (if required) and all accessories as required for termination is in the present scope of work - ------- - Deleted. - ----- |
| 4. | TS- Section Project(Rev00) | New clause no: 10.16 added in clause no:10.0 of Specific requirement. | Clause no 10.16 in clause no:10.0 Specific requirement 10.16. Technical Qualification requirement for 66/11kV Transformer shall be as follow: “The 66kV class Transformer shall be offered from manufacturer(s) who have designed, manufactured, type tested and supplied 66kV or above class Transformer which must be in successful operation for at least two (2) years on the original scheduled date of NOA”. Dynamic Short Circuit Test requirement: For 66 kV Class Transformer: Bidder / Manufacturer should have successfully carried out Dynamic Short Circuit Test on any rating of 66 kV or above voltage class transformer as on the originally scheduled date of bid opening and shall enclose the relevant Test Report / Certificate along with bid. In case bidder has not successfully tested 66 kV or above voltage class transformer for Dynamic Short Circuit Test, their bid shall be considered technically non-responsive. The offered transformer should comply the requirement of similarity clause specified in IS 2026 (PART 5) / IEC 60076-5 with respect to short circuit tested transformer. Further, design review of offered transformer shall be carried out based on the design of short circuit tested transformer. |
| 5. | Sch-1&2 of BPS Sch-3 of BPS | Long Text; Unit; Qty. Sch-1&2 of BPS. Spares for 220V Batteries; LS; 1. Spares for 48V Batteries; LS; 1. Sch-3 of BPS. Fire Detection and Alarm System for 220kV GIS Hall; LS; 1. 9kV Surge Arrester (1-Phase); EA; 9. Lighting Panel type ACP-2 as per technical specification; EA; 1. Lighting Panel type ACP-3 as per technical specification; EA; 1. LIGHTING FIXTURE LED LUMINAIRES TYPE FL-1 AS PER TECH.SPECIFICATIONS; EA; 1. LIGHTING FIXTURE LED LUMINAIRES TYPE FL2 AS PER TECH. SPECIFICATIONS; EA; 1. POLE MOUNTED LED POST TOP LUMINAIRE TYPE SL-D1 (= 30W)AS PER TECHNICALSPECIFICATION; EA; 1. LED STREET LIGHT LUMINAIRE TYPE SL-L1 (= 45W)AS PER TECHNICALSPECIFICATION; EA; 1. 15A, 240V: Outdoor Receptacle 2 pole, 3-pin modular (type RO) as pertechnical specifications; EA; 1. 125A, 415V : Interlocked switch socket outdoor Receptacle as pertechnical specifications; EA; 1.; LS; 1. | Long Text; Unit; Qty. Sch-1&2 of BPS. Spares for 110 V Batteries; LS; 1. Spares for 48V Batteries; LS; 0. Sch-3 of BPS. Fire Detection and Alarm System for 66 kV GIS Hall; LS; 1. 9kV Surge Arrester (1-Phase); EA; 6. Lighting Panel type ACP-2 as per technical specification; EA; 2. Lighting Panel type ACP-3 as per technical specification; EA; 2. LIGHTING FIXTURE LED LUMINAIRES TYPE FL-1 AS PER TECH.SPECIFICATIONS; EA; 8. LIGHTING FIXTURE LED LUMINAIRES TYPE FL2 AS PER TECH. SPECIFICATIONS; EA; 10. POLE MOUNTED LED POST TOP LUMINAIRE TYPE SL-D1 (= 30W) AS PER TECHNICAL SPECIFICATION; EA; 10. LED STREET LIGHT LUMINAIRE TYPE SL-L1 (= 45W)AS PER TECHNICAL SPECIFICATION; EA; 10. 15A, 240V: Outdoor Receptacle 2 pole, 3-pin modular (type RO) as per technical specifications; EA; 6. 125A, 415V : Interlocked switch socket outdoor Receptacle as per technical specifications; EA; 2. |
| 6. | TS-Section Project(Rev00) | Existing Clause no: 5.2 Meteorological data The meteorological data of the substation is given below. Parameter; 66 kV Pang SS. Max. Temperature; 30°C. Min. Temperarure; -28°C. Altitude of land plot; Approx. 4800 mtr above M.S.L. | Existing Clause no: 5.2 Meteorological data The meteorological data of the substation is given below. Parameter; 66 kV Pang SS. Max. Temperature; 30°C. Min. Temperature; -35°C. Altitude of land plot; Approx. 4800 mtr above M.S.L. Annual Rainfall; 51 mm. Maximum snow deposition; 50 mm. Solar radiation (for UV protection); High. GPS coordinates (Approx.); 761742.00 m E, 3677746.00 m N. |
| 7. | TS-Section Project(Rev00) | Annexure-VI: Description of GIS Module and Equipment. | Annexure-VI: Description of GIS Module and Technical parameter of (GIS & AIS) Equipment (Revised). |
| 8 | Second Envelope | In view of the above Amendments, the ‘Price_schedule’ excel stand revised as ‘Price_schedule_Rev01’. Note- Bidders are requested to consider the revised excel sheet(s) titled “Price Schedule_Rev01” for bid preparation/submission for the subject package. |  |