## Pre-bid Query
Clarification No.- II dated 11/10/2024 to the Bidding Documents for Transmission Line Tower Package- TL01 for 220 kV S/C (on D/C Tower) Pang- Upshi line (Part-1) and establishment of new 2 x 10 MVA 66/11kV GIS Sub Station at Pang for 220kV AC Transmission line between Pang and Phyang associated with Transmission system for evacuation of RE power from renewable energy parks in Leh (5 GW Leh-Kaithal transmission corridor).; Spec. No: CC/NT/W-TW/DOM/A06/24/11961
Sr. No. | Bidders Query no | Re. Clause no. | Existing provision | Bidder's Query/Comment | POWERGRID Reply
1 |  | 2 | 3 | 4 | 5
1 | 1 | - | - | Kindly provide the kmz file for the routes | Refer Clarification No-I
2 | 2 | Section IA, Vol (II), Cl. 2.14.1 | Conductor & OPGW for 220 kV line | For ACSR Deer Conductor, Conductor spacing, Cross sectional area, Modulus of Elasticity and Coefficient of Thermal expansion have not been provided. Please provide the inputs. | Refer Clarification No-I
3 | 3 | Tender Specification : Volume II, (1.0 Section-Project ( Rev00)-Part B), Page 5 of 14 | 3, III | Please provide the following details for the proposed substation. 1. Soil investigation report (if available) 2. Contour layout showing existing ground level (if available) 3. HFL Data (in order to finalize the FGL) 4. Site global co-ordinates for the proposed plot in order to estimate the quantum of work. | 1. Soil investigation is in the scope of bidder. 2. Site levelling and contouring is in the scope of bidder. 3. HFL data duly verified by POWERGRID Site is required to be arranged by contractor for finalization of FGL during detailed engineering. 4. Refer Amendment No-III
4 | 4 | Tender Specification : Volume II, (1.0 Section-Project ( Rev00)-Part B), Page 5 of 14 | 5.2 & 3, III, ii, e2iii | It is mentioned in the clause no.5.2 that, the Minimum temperature is -28°C for proposed substation. Snow fall is expected for the above temperature. Also, It is mentioned in the clause no.(3, III, ii, e2iii) that, The roofing of the GIS Hall, AHU Room and Panel Rooms shall be of puff sandwich panels and as per clause no. 11.3.1 of Civil specification, 50mm thick Puff sandwiched panel to be provided for roof & wall sheeting. It is considered that, 50mm thick Puff sandwiched panel for Roof & wall sheeting is suitable for use in the above environment. Please confirm. | Refer Amendmend No-III
5 | 5 | Tender Specification : Volume II, (1.0 Section-Project ( Rev00)-Part B), Page 5 of 14 | 3, t & 5.2 | It is mentioned in the referred clause that, All structures’ height shall be adequate to achieve required clearance considering the level of snowfall provided in meteorological data. However, snowfall data is not mentioned. Please mention the snow fall data. | Refer Amendmend No-III
6 | 6 | Tender Specification : Volume II, (1.0 Section-Project ( Rev00)-Part B), Page 8 of 14 | 3 iv | Its is mentioned in referred clause that, While calculating design wind speed (for designing of various structures) as per IS 875 Part 3, the Topography Factor (k3) shall be takes as 1.36. As per structure spec-Rev-7 clause no. 2.1, the wind load calculation for lattice structure shall be as IS 802 Part 4 and in this code, there is no provision of Topography Factor (k3) for the calculation of design wind pressure. Please confirm, the k3 factor has to be considered for only for buildings not for switchyard lattice structures. | In line with Technical Specification, Section: Structure, Rev 7 Topography Factor (k3) is not be considered for switchyard lattice structures. However, for other structures Topography Factor (k3) has to be considered in line with IS 875 Part 3.
7 | 7 | Tender Specification : Volume II, (1.0 Section-Project ( Rev00)-Part B), Page 6 of 14 | 3, III, ii, e2iii | As per referred clause, In the Control Room Building, 100 MM thick PIR panel having finished with 0.5 mm TCT PPI sheet shall be provided on all the walls externally. We trust that, 100mm thk. PIR panel shall be provided over the external brick wall. Please confirm. | In the Control Room Building, 100 MM thick PIR panel having finished with 0.5 mm TCT PPI sheet shall be provided on all the walls externally.
8 | 8 | Tender Specification : Volume II, (1.0 Section-Project ( Rev00)-Part B), Page 8 of 14 | 3, III, ii, e2iii | As per referred clause, All structural steel shall be of Grade C as per IS 2062. We understand that, structural steel for switchyard gantry, Equipment support structure are of Grade C and PEB Building & all other misc. structural steel are of Grade A. Please confirm. | All structural steel for switchyard gantry, equipment support structure,PEB building & all other misc. structural steel governed by IS 2062 as per TS and section project shall be of Grade C.
9 | 9 | Tender Specification : Volume II, (1.0 Section-Project ( Rev00)-Part B), Page 12 of 14 | 10.8 | As per referred clause, separate underground tank of 10KL Capacity for bulk diesel storage shall be provided and the scope of work shall also include associated Civil work & sand filling for underground tank. We trust that, Civil work & sand filling required for underground tank shall be paid under respective items(i.e: excavation, PCC, RCC, Reinforcement & sand filling) in BPS. Please confirm. | The Civil work & sand filling for underground tank (if required) shall also be deemed to be included in BPS item: 39 Sch-I. Hence, no additonal payment made against the same.
10 | 10 | Technical Specification Gas Insulated Switchgear Rev 05A (February 2019) |  | The referred specification available with Tender documents doesnot having the Technical Details/Parameters of 66kV GIS Equipment. In this regard, Kindly provide Technical Specification along GTP for 66kV GIS Equipment. | Refer Amendmend No-III
11 | 11 | Section-Project : clause 3.1.B.j |  | In continuation to the above query please provide Specifictaion for 66kV GIS Equipmemnt along with EOT carne requirements | Refer Amendmend No-III for Specification for 66kV GIS EOT Crane envisaged in 72.5 kV GIS HALL .Please refer clause no: 10.15 of Specific requirement of TS-Section Project(Rev00).
12 | 12 | Section-Project : clause 3.1.B.n | As per specified clause,it is specified that "The capacity of batteries and battery chargers shall be supplied as worked out by the contractor for the 66 kV and 11kV present and future bays as shown in the Single Line Diagram of the substation.." However, as per Tender SLD and Section-Project, clause 2, A ,The scope of work doesnot have any Future bay requirements. | We presume that there is no future bay requirement to be considered as per SLD & Scope of work specified in section project. Please confirm. | Confirmed.
13 | 13 | Sectional-Project: Clause 3.1.A | As per referred clause, it is specified as "The 72.5 kV SF6 gas insulated switch gear shall have double bus bar arrangement." However, as per tender SLD and Annexure-VI- Description of Module and Equipment, it is specified as single Main busbar scheme. | In this regard, We presuem that 66kV GIS shall be provided with Single main busbar scheme as per SLD & Annexure VI. Please confirm | Confirmed. Please refer Annexure-VI (DESCRIPTION OF GIS BAY MODULE & EQUIPMENTS ) to TS-Section Project(Rev00).
14 | 14 | Section-Project : clause 3.1.B.m | As per specified clause, it is specified as "LT Switchgear shall be taken from 2 no’s of 630 kV,11/0.433 kV LT Transformers" . | Kindly specify the purpose of remaining 4 nos. of LT transformers under scope and where to be connected. | Bidder may please quote as per BPS meeting requirement as per TS.
15 | 15 | Section-Project : clause 3.1.B.o | In referred clause, the 11kV cable details are specified as follows: i) 11 kV, 1 run per phase – 3C x 300 Sqmm, XLPE AL cable (From 11 kV indoor switchgear panel to Six nos. of 630 KVA, 11/0.433kV LT transformer for auxiliary supply of substation)... ii) 11 kV, 2 runs per phase – 3C x 95 Sq.mm XLPE Al cable (From 11 kV side of 66/11 kV transformer to 11 kV Indoor GIS Switchgear)... However, as per BPS, Sl.No. II, 78 to 81, it is specified as follows: i) Cable 1 & Accessories: 3Cx300Sq mm Cable Quantity and Termination kit is specified with 2 sets ii) Cable 2 & Accessories: 3Cx95Sq mm Cable Quantity and Termination kit is specified with 6 sets | As both the clauses are contradicting, kindly specify the actual requirement to be considered and quote accordingly. | Refer Amendmend No-III
16 | 16 | Section-Project : clause 3.1.B.n | As per referred clause,it is specified for requirement of both 110 V & 48 V Batteries. However, The BPS doesnot have any line item for Telecommunication Equipment and PLCC. | In this regard, We presume that 48V Battery and charger are not Required. Please confirm. | Confirmed.
17 | 17 | Section_Switchyard Erection: Clause 8.3 | The referred clause doesnot having the Technical Details/GTPof 66kV Bus Post Insulater (BPI) | In this regard, Kindly provide Technical Specification along GTP for 66kV BPI. | Please refer clause no:4.6 of along with Technical Specification: GTR (Rev No:15) for System parameter f meeting the requirement conform in general to latest IS: 2544, IEC-60168, IEC 60273 and IEC-60815 for 66 kV BPI & Hardware
18 | 18 | BPS, Sl.No. II, 66/11kV Pang S/S, Line side Insulator | In BPS (66/11kV Pang S/S), Qunatity for the line side Hardware & insulators are included. | If same to be included in present scope, Kindly include separate line item in BPS. In addition to above, please provide the technical specifications details for 66kV Insulators and Hardwares. | Refer Amendmend No-III Bidder shall quote meeting the requirement as per TS.
19 | 19 | Section-Project : Clause 3.1.I, B o, iv | As per referred clause, it is specified as "Termination kit & all other accessories required for direct termination to the 2 nos. of Spare Outgoing feeders in 11 kV Indoor Switchgear module is included in the present scope. The size and run of 11 kV HT cables required for Outgoing (line) feeders shall be provided to the contractor at the time of detailed engineering." However, there is no separate line item for Termination kit accessories og 11kV Switchgear (line). | Please include the same in BPS to quote accordingly. | Refer Amendmend No-III
20 | 20 | Section-Project : Clause 3.1.I, B f | As per referred clause, it is specified as "The necessary interface equipment (Router, Firewall, Ethernet Switches etc.) and integration work for transferring data to remote end(s) through optical fiber based SDH communication link is also under present scope." | However, the BPS doesnot have any line item for communictaion equipment. If same to be included in present scope, Kindly include separate line item in BPS to quote accordingly. | Provison for SDH communication Equipment is only envisaged under present scope.
21 | 21 | Section-Project : Clause 3.8 | As per referred clause, it is specified as "All 66 kV & 11 kV equipment insulation shall be designed to take care of high altitude (with correction factor as given in metrological data for respective substation)" . | However, the correction factor in not provided along with metrological data.Kindly provide the same to design accordingly. | Correction factor to be derived from the altitude of site mentioned in meterological data. This correction factor shall be applicable for all outdoor insulations.
22 | 22 | Power Transformer |  | Please specify the following details of 66/11kV Transformers: i) Type test requirements including short circuit ii) Bushing type & material iii) Cable box requirement details | i) Refer Amendment No-III ii) Clause no: Please refer clause no:10.2, TS: Section -Transformer (Upto 400kV Class) meeting Altitude correction as per clause no:4.6 of along with Technical Specification: GTR (Rev No:15) iii) Cable Box envisaged in 11 kV Side of 66/11 kV ICT.
23 | 23 | Creepage distance |  | Please specify the creepage distance to be considered for outdoor equipments. | Please refer clause no: 10.15 of Specific requirement of TS-Section Project(Rev00) and clause no:4.6 of along with Technical Specification: GTR (Rev No:15)
24 | 1 | Technical Specification, Section – Project (Rev.00) GENERAL ARRANGEMENT DRAWING DRAWING NO.: C/ENGG/GIS/PHANG/GA/00 SCHEDULE OF RATES AND PRICES: 66/11kV Pang S/S | Earthing | As per the site information, water is not encountered even at a depth of 250 meters, which presents a challenge for achieving satisfactory earthing values during execution. While the power grid has specified the main mat quantity as 5 KM, we believe that additional measures will be required to ensure compliance with the technical standards. Request for inclusion in the pricing schedule as a separate quantity for the following : Satellite Earthing: Since a water source is available at a distance of 5-6 km, we may need to lay a conductor up to the water source, installing 10-15 deep electrodes (3-4 in number) to achieve satisfactory values. | Design of Main Earthmat is under present scope of Bidder. Please refer clause no: 3.1(b)(P) of Specific requirement of TS-Section Project(Rev00) Bidder may please quote as per BPS meeting requirement as per TS.
25 | 2 | Technical Specification, Section – Project (Rev.00) GENERAL ARRANGEMENT DRAWING DRAWING NO.: C/ENGG/GIS/PHANG/GA/01 | Earthing | We understand that main earthing gird conductor shall be provided only in 66 kV switchyard bays in scope. Earthing grid for any future areas is not in scope. Please confirm. | Bidder may please quote as per BPS meeting requirement as per TS.
26 | 3 | Technical Specification, Section – Project (Rev.00) & SCHEDULE OF RATES AND PRICES: 66/11kV Pang S/S | Earthing | We understand that Earthing shall be with Mild Steel and Galvanised steel materials. Any copper conductors are not envisaged for earthing. | Bidder may please quote as per BPS meeting requirement as per TS.
27 | 4 | Technical Specification, Section – Project (Rev.00) | Creepage | We understand Minimum specified creepage distance for insulator string/ longrod insulators/ outdoor bushings shall be 31 mm/kV Please confirm creepage to be considered for oher outdoor equipments, We understand same shall be 25mm/kV being substations in non-costal area. | Please refer clause no: 10.15 of Specific requirement of TS-Section Project(Rev00) and clause no:4.6 of along with Technical Specification: GTR (Rev No:15)
28 | 5 | SCHEDULE OF RATES AND PRICES: 66/11kV Pang S/S- ANNEXURE-V-HEATING & VENTILATION SYSTEM FOR GIS HALL | Heating and ventilation | As per Technical Specification Annexure IV, we understand the temperature for the GIS Hall should not go below -10°C. Could you please confirm the required temperature limits for the DG Room and 11kV Indoor Panel Room | Please refer Amendment No-III
29 | 6 | SCHEDULE OF RATES AND PRICES: 66/11kV Pang S/S- | Heating and ventilation | As per price schedule we envisage there is no Heating system required for Security Room please confirm the same | Bidder may please quote as per BPS meeting requirement as per TS.
30 | 7 | Technical Specification-Section -LIGHTING SYSTEM (Rev.07) | Illumination | The standard PGCIL luminaires for specific areas have an operating temperature range of -5°C to 45°C. However, as per the meteorological data in the technical specification for the Pang substation, the temperature ranges from -28°C to 30°C. We understand that outdoor fixtures and luminaires must be capable of operating within this range (-28°C to 30°C).Please confirm And For indoor areas, since heating systems will be provided, we assume that the standard fixtures as per PGCIL Section - LIGHTING SYSTEM (Rev.07) will be acceptable. Please confirm if our understanding is correct. | Bidder may please quote as per BPS meeting requirement as per TS.
31 | 8 | Technical Specification-Section -LIGHTING SYSTEM (Rev.07) | Illumination | Please specify if any heating requirement for ACP -2 and ACP 3 panel | Bidder may please quote as per BPS meeting requirement as per TS.
32 | 9 | SCHEDULE OF RATES AND PRICES: 66/11kV Pang S/S- | Fire Detection and Alarm System | We noticed a typo error in the price schedule that specifies the fire alarm system for the 220kV GIS Hall. We understand this should refer to the fire alarm system for the 66kV GIS Hall. Please confirm if our understanding is correct | Please refer Amendment No-III
33 | 10 | Technical Specification, Section – Project (Rev.00) | 66 kV GIS | We seek clarification regarding the bus bar arrangement for the 72.5 kV switchgear. As the Technical Specification, Section – Project (Rev.00) Clause 3.1 (1) A specifies a double bus bar arrangement, while the SLD & ANNEXURE- III -DESCRIPTION OF GIS BAY MODULE & EQUIPMENTS describes a single bus arrangement. Please confirm the correct requirement. | Confirmed. Please refer Annexure-VI (DESCRIPTION OF GIS BAY MODULE & EQUIPMENTS ) to TS-Section Project(Rev00).
34 | 11 | SCHEDULE OF RATES AND PRICES: 66/11kV Pang S/S | 11 kV Surge Arrestors | The price schedule indicates a quantity of 11kV surge arrestors as 9 Nos. We understand that 6 Nos are required for the 11 kV side of 2 transformers. Please clarify the application of the remaining 3 surge arrestors, as they are not identified in the SLD or GA drawings. | Please refer Amendment No-III
35 | 12 | SCHEDULE OF RATES AND PRICES: 66/11kV Pang S/S | FOTE & PLCC equipment | As per the price schedule, we understand that FOTE and PLCC equipment are not required for the 66 kV Pang Substation. Please confirm | Confirmed.
36 | 13 | Technical Specification, Section – Project (Rev.00) | Cables | According to the Technical Specification, Section – Project (Rev.00), clause 3.1 (1) (B) (o) - 3C x 300 sqmm XLPE AL cable is specified from the 11 kV switchgear to the six Nos of 630 kVA transformers, while 2 Run 3C x 95 sqmm cable is used from the 66/11 kV transformer to the 11 kV Indoor GIS Switchgear. Please reconfirm the requirement as the- 3C x 300 sqmm XLPE AL cable should be used for 66/11 kV transformer to the 11 kV Indoor GIS Switchgear and the 2 Run 3C x 95 sqmm cable should be used for the 11 kV switchgear to the six Nos of 630 kVA transformers. | Refer Amendmend No-III
37 | 14 | Technical Specification, Section – Project (Rev.00) | Ice loading | Please confirm ice loading thickness to be considered for outdoor equipments | Refer Amendmend No-III
38 | 15 | SCHEDULE OF RATES AND PRICES: 66/11kV Pang S/S | Lightning Protection | We understand that any structure required for lightning protection of the substation is to be included under the Non-Standard Structure (Erection) item no. 50 of the price schedule. Please confirm. | Confirmed.
39 | 1 | 3.01, f & 2 of 22 Section-VI_TS_33_11 kv switchgear_GIS SECTION PROJECT | The Service Class Continuity of Switchgears shall be LSC 2B-PM (as per IEC 622771-200). | Loss of service continuity category with circuit breaker is LSC2 | Bidder to comply the requirement of Bidding document.
40 | 2 | 3.01, o & 3 of 22 Section-VI_TS_33_11 kv switchgear_GIS SECTION PROJECT | SF6 gas leakage rate should not exceed 0.5% per annum. | As per sealed pressure system defined in IEC 62271-1, leakage rate should not exceed 0.1% per annun. Kindly review and confirm the requirement | Bidder to quote as per requirement of TS.
41 | 3 | 7.5 & 12 of 22 Section-VI_TS_33_11 kv switchgear_GIS SECTION PROJECT | ON/OFF indicators for AIS Line Isolator &Line Earth Switch | We don’t have the Isolator or earth switch on line side in our design. | Bidder to comply the requirement of Bidding document.
42 | 4 | SLD & 22 of 22 Section-VI_TS_33_11 kv switchgear_GIS SECTION PROJECT | Isolator with one E/S at cable side | We don’t have the Isolator or earth switch on line side in our design. | Bidder to comply the requirement of Bidding document.
43 | 5 | 10.12 & 22 of 22 Section-I SECTION PROJECT | For 11 kV GIS type, indoor switchgear, manufacturer’s standard design i.e busbar (SF6/Solid core/epoxy insulated), various gas chambers, placing of various equipment in the panel etc shall also be acceptable | As per the clause referred, Busbar in SF6 or busbar solid insulated both are acceptable. However, these two are distinct technologies & also the price range for GIS & Hybrid GIS are highly different. Therefore, to promote fair tender evaluation and wider participation we recommend adoption of busbar in SF6 only. You may also refer CEA Notification ( File no CEA-GO-16/3/2020-DPT Division) which says Discom should choose single technology | Bidder may quote as per provisons of bidding document .
44 | 6 |  | Approved Make of GIS | Please share the approved Make of GIS | Bidder to visit compendium of vendors tab at POWERGRID website www.powergrid.in
45 | 7 |  | Single line Diagram | Please share Single line diagram of 33/11KV GIS substation with busbar configuration ( single /double) , number & type of feeders, protection &metering details, CT/PT details, cable termination details,surge arrestor ( if required) etc | Bidder Querry is not clear. The offered Susbstation at Pang, as per bidding document is 66/11 kV voltge level. Bidder may quote as per provisons of bidding document .
46 | 8 |  | Closed door operation- widely accepted industry safety feature | We recommend Manual operations of the different switches like breaker, disconnector, earthing switch of the switchgear should be possible without opening the front door. This important safety aspect is missing from the specification hence we request your consideration of the same and make part of the specification . | Bidder may quote as per requirement of TS.
47 | 9 |  | LinePT Isolation switch | Please confirm if LinePT isolation switch is required for the purpose of cable testing without the need to handle the PTs and thereby minimize the risk to operator safety | Please refer clause no : I(i)(iii) of Annexure-VI ( Discription of GIS bay module& Equipment) Bidder may quote as per provisons of bidding document .

## Sheet1 (hidden)
11KV XLPE CABLE TERMINATION EQUIPMENT ALONG WITH STRUCTURE ACCESSORIESFOR OUT DOOR TERMINATION (ONE SET CONSISTS OF COMPLETE & REQUIREMENTFOR ONE BAY) | SET | 2
11KV 3CX300SQMM XLPE AL ARMOURED CABLE | KM | 0.25
11KV XLPE CABLE TERMINATION EQUIPMENT ALONG WITH STRUCTURE ACCESSORIESFOR OUT DOOR TERMINATION (ONE SET CONSISTS OF COMPLETE & REQUIREMENTFOR ONE BAY) | SET | 6
11KV 3X95SQMM XLPE AL ARMOURED CABLE | KM | 0.4