## Pre-Bid Query
Clarification No.-IV dated 09/06/2024 to the Technical portion of Bidding Document for 400kV GIS Substation Package SS-123 for (a) Extn. of 400/220kV Rajarhat GIS S/S under ‘Eastern Region Expansion Scheme-XXXXI (ERES-XXXXI)’ and (b) Extn. of 400/220kV Magarwada GIS S/S under ‘Augmentation of Transformation Capacity at 400/220 kV Magarwada GIS substation in DD & DNH by 400/220 kV, 1x500 MVA ICT (3rd)’. [Spec. No.: CC/NT/W-GIS/DOM/A04/24/01196]
Sl. No. | Volume / Section | Clause No. | Description | Bidders Query | POWERGRID reply
1 | 1_Section Project_Rev-00_SS123 & Price_Schedule | 2. Scope of work | 2.2.1 A. b) Mandatory Spares for 400kV GIS as per BPS.and B. b) Mandatory Spares for 220kV GIS as per BPS. Item No. 50 to 56 | In the Price Schedule mandatory spares for 400kV, 500MVA, 3pH, ICT spares also specified along with quantity. As pe Section Project, supply, erection, testing and commissioning of Power transformer is covered under separate package. We understand that Mandatory spared mentioned for Power transformer shall not be applicable. Please confirm. | Please refer to Amendment No.-II
2 | 1_Section Project_Rev-00_SS123 | 2. Scope of work | 2.2.1 C. d) Supply, laying and termination of cables along with associated accessories from Marshalling box of 400/220/33kV Autotransformer to Local Control panel Rooms/Control Room as per requirement. | We understand that all LV Power & Control cables including illuminatin cables will be operated through the cable quantities given in the Bid Price Schedule except illumination wires. Please confirm our understanding. | Bidder to refer Specific requirement, Rev-08 of Technical specification for clarity regarding illumination cable scope.
3 | 1_Section Project_Rev-00_SS123 | 2. Scope of work | 2.2.2 B.Extension of 220kV RCC GIS Hall. Necessary Ventilation System, Illumination System, Fire Protection System, etc. for 220kV GIS Building extension portion will be designed and provided to meet the technical requirements. | We understand that extension of 220kV GIS hall is in scope only.We also understand that existing CRP room has adequate space for installation of CRP of 220kV GIS. Please confirm our understanding. | Existing CRP room has adequate space for installement of 220kV Protection panels under present scope of work. For more clarity, bidders are advised to visit the substation sites and acquaint themselves with the topography, infrastructure and also the design philosophy, as per clause no 1.5 of section project of TS.
4 | 1_Section Project_Rev-00_SS123 | Dwg.no. G71770-AD079-V021-A dated 21.04.15 & (1)-G71770-AC885-L152-3 dated 26.03.15 | Existing Overall plan view of 245KV GIS system-Rajarhat & Existing Overall Electrical layout-Rajarhat | There is difference between 220kV GIS bay location in Layout Existing Overall plan view of 245KV GIS system-Rajarhat and layout Existing Overall Electrical layout-Rajarhat. In the Existing Overall plan view of 245KV GIS system-Rajarhat layout, the ICT-3 bay marked in red adjacent to the existing Bus PT (bay 210) whereas in the Existing Overall Electrical layout-Rajarhat, the ICT-3 bay shown as last of of 220kV GIS. Please confirm which one to follow. | Location of ICT-3 has been marked in Red color in overall plan view of 245KV GIS system(Drg No. (0) G71770-AD079-V021-A, Rev A) & the Same shall prevail.
5 | 1_Section Project_Rev-00_SS123 | 2. Scope of work | 2.2.2 C. d) Supply, laying and termination of cables along with associated accessories from Marshalling box of 400/220/33kV Autotransformer to Local Control panel Rooms/Control Room as per requirement. | We understand that all LV Power & Control cables including illumination cables will be operated through the cable quantities given in the Bid Price Schedule except illumination wires. Please confirm our understanding. | Bidder to refer Specific requirement, Rev-08 of Technical specification for clarity regarding illumination cable scope.
6 | 1_Section Project_Rev-00_SS123 | 7.0 DIFFERENT SECTIONS OF TECHNICAL SPECIFICATION | In case of any discrepancy between BPS and other sections, BPS shall prevail over the other sections of the technical specifications. However, for rating of the BPS items, associated Section-Project shall be referred to. | In case of discrepancy in scope, rating and requirement between Section Project and Bid Price schedule, we understand bidder to follow & quote as per bid price schedule. We request you to please confirm our understanding. | Please refer to Amendment No.-II for FAQ.
7 | General | Shutdown |  | We understand that necessary shutdown at bith sites shall be provided as and when required within 3 days of notice. Please confirm. | Shutdown for the construction work shall be arranged by the employer in coordination with appropriate regulatory authority. Bidder to comply all other requirement as per the provisions of bidding documents.

## 35 PR BSPTCL 2018 (hidden)
|  |  |  | Date: | 2018-07-30
Project | Construction of (2x200MVA+3x50 MVA) 220/132/33KV GSS, Thakurganj(District-Kishanganj) with SAS under Turnkey basis.
Client |  | Bihar State Power Transmission Company Limited.
Contractor |  | Bajaj Electricals Limited.
S.No. | Tender document reference | Clause no. & page no. | Clarification by Contratcor | Response by client | Remarks
1 | General Plot plan |  | Kindly request to provide the general plot plan of the substation area ( length & breadth).
2 | Soil Investigation report |  | Please provide the soil investigation report if avialable for proposed substation area inorder to quantiy the foundation works or Kindly provide safe bearing capacity to be considered at 1.5m below existing ground level.
3 | Contour map |  | Kindly request to provide the contour map for the proposed substation area if available.
4 | Location of site |  | As geotechnical investigation & foundation design is included our scope of work, we would like to do following in proposed substation plot inorder to estimate foundation quantity. 1. Preliminary topographical survey 2. Bore log In this regards, kindly request to provide the plot location of the proposed substation.
5 | Changes in site location |  | We undestand that in case of changes in site location during detailed engineering due to that if we have any impact in foundation type and sizes will be paid as additional to the contarctor, please confirm.
6 | Price schedule -civil works, FFPH building with rest room | sl no. 5-b | Kindly request to provide the area of rooms required to be placed at first floor of pump house building.
7 | Price schedule -civil works, landscaping | sl no. 20 | Kindly request to provide the area required for landscaping and provide the type of landscaping required.
8 | Vol-2D, Civil works, High flood level. | sl no. 25, Page no.12 | In order to finalize the finished ground level of proposed substation, kindly request to provide the highest flood level for proposed substation.
9 | Vol-2D, Civil works, retaining wall/Stone pitching. | sl no. 24-b, Page no.12. | As per mentioned clause, we understand that retaining wall is not required incase of filling less than 2m, whereas for filling up to 2m will required stone pitching slope protection , which will also paid as extra to the contarctor , please confirm.
10 | Vol-2D, Civil works, retaining wall. | sl no. 24-b, Page no.12. | As per mentioned clause, we understand that retaining wall is not required incase of filling less than 2m, whereas for filling above 2m will required same and paid as extra to the contractor as per bihar PWD schdule of rates, please confirm.
11 | Retaining wall and stone pitching |  | In case the above clarification sl no.9 & 10 will not paid additional to contartor, we kindly request to include the item for stone pitching & retaining wall for different heights ( 2m, 2.5, 3m , 3.5m etc.) in price schdule.
12 | Vol-2D, Civil works, Tower and equipment support structure - Galvanization thickness. | sl no. 15-b, Page no.5. | Kindly request to provide the minimum galvanization thickness for structural steel members.
13 | Vol-2D, Civil works, Tower structure - standard drawing. |  | Standard drawings for substation gantry and towers are not avialable in BSPTCL website, kindly request to provide 220kV, 132kV & 33kV tower and gantry GA drawings.
14 | Price schedule -civil works, Boundary wall. | sl no. 21 | Kindly request to rovide BSPTCL standard boundary wall , since same is not available on BSPTCL website.
15 | Price schedule -civil works, dormatory building. | sl no. 18 | Kindly request to provide the standard drawing for dormatory building. OR Kindly provide the area required and type of structure to be considered for dormatory building.
16 | Firewall |  | Please clarify firewall will be paid under which item in price the schdule.
17 | Firewall |  | Kindly request to provide the BSPTCL standard drawings for firewall if any.
18 | Price schdule-Erection, Structural steel for lighting cum lighttning mast. | Sl no. R-2 page no.10 & Sl no. O-1 page no.10 | We understand that structure steel required for lighting cum lightning mast will be paid under Sl no. O-1, page no.10 of erection price schdule, no need to consider additional structural steel quantity for same, please confirm.

## 38 PR BSPTCL 2018 (hidden)
|  |  |  | Date: | 2018-07-30
Project | Construction of (2x200MVA+3x50 MVA) 220/132/33KV GSS, Karmnasha
Client |  | Bihar State Power Transmission Company Limited.
Contractor |  | Bajaj Electricals Limited.
S.No. | Tender document reference | Clause no. & page no. | Clarification by Contratcor | Response by client | Remarks
1 | General Plot plan |  | Kindly request to provide the general plot plan of the substation area ( length & breadth).
2 | Soil Investigation report |  | Please provide the soil investigation report if avialable for proposed substation area inorder to quantiy the foundation works or Kindly provide safe bearing capacity to be considered at 1.5m below existing ground level.
3 | Contour map |  | Kindly request to provide the contour map for the proposed substation area if available.
4 | Location of site |  | As geotechnical investigation & foundation design is included our scope of work, we would like to do following in proposed substation plot inorder to estimate foundation quantity. 1. Preliminary topographical survey 2. Bore log In this regards, kindly request to provide the plot location of the proposed substation.
5 | Changes in site location |  | We undestand that in case of changes in site location during detailed engineering due to that if we have any impact in foundation type and sizes will be paid as additional to the contarctor, please confirm.
6 | Price schedule -civil works, FFPH building with rest room | sl no. 5-b | Kindly request to provide the area of rooms required to be placed at first floor of pump house building.
7 | Price schedule -civil works, landscaping | sl no. 20 | Kindly request to provide the area required for landscaping and provide the type of landscaping required.
8 | Vol-2D, Civil works, High flood level. | sl no. 25, Page no.12 | In order to finalize the finished ground level of proposed substation, kindly request to provide the highest flood level for proposed substation.
9 | Vol-2D, Civil works, retaining wall/Stone pitching. | sl no. 24-b, Page no.12. | As per mentioned clause, we understand that retaining wall is not required incase of filling less than 2m, whereas for filling up to 2m will required stone pitching slope protection , which will also paid as extra to the contarctor , please confirm.
10 | Vol-2D, Civil works, retaining wall. | sl no. 24-b, Page no.12. | As per mentioned clause, we understand that retaining wall is not required incase of filling less than 2m, whereas for filling above 2m will required same and paid as extra to the contractor as per bihar PWD schdule of rates, please confirm.
11 | Retaining wall and stone pitching |  | In case the above clarification sl no.9 & 10 will not paid additional to contartor, we kindly request to include the item for stone pitching & retaining wall for different heights ( 2m, 2.5, 3m , 3.5m etc.) in price schdule.
12 | Vol-2D, Civil works, Tower and equipment support structure - Galvanization thickness. | sl no. 15-b, Page no.5. | Kindly request to provide the minimum galvanization thickness for structural steel members.
13 | Vol-2D, Civil works, Tower structure - standard drawing. |  | Standard drawings for substation gantry and towers are not avialable in BSPTCL website, kindly request to provide 220kV, 132kV & 33kV tower and gantry GA drawings.
14 | Price schedule -civil works, Boundary wall. | sl no. 21 | Kindly request to rovide BSPTCL standard boundary wall , since same is not available on BSPTCL website.
15 | Price schedule -civil works, dormatory building. | sl no. 18 | Kindly request to provide the standard drawing for dormatory building. OR Kindly provide the area required and type of structure to be considered for dormatory building.
16 | Firewall |  | Please clarify firewall will be paid under which item in price the schdule.
17 | Firewall |  | Kindly request to provide the BSPTCL standard drawings for firewall if any.
18 | Price schdule-Erection, Structural steel for lighting cum lighttning mast. | Sl no. R-2 page no.10 & Sl no. O-1 page no.10 | We understand that structure steel required for lighting cum lightning mast will be paid under Sl no. O-1, page no.10 of erection price schdule, no need to consider additional structural steel quantity for same, please confirm.

## 39 PR BSPTCL 2018 (hidden)
|  |  |  | Date: | 2018-07-30
Project | Construction of (2x160MVA+3x50 MVA) 220/132/33KV GSS, Garaul
Client |  | Bihar State Power Transmission Company Limited.
Contractor |  | Bajaj Electricals Limited.
S.No. | Tender document reference | Clause no. & page no. | Clarification by Contratcor | Response by client | Remarks
1 | General Plot plan |  | Kindly request to provide the general plot plan of the substation area ( length & breadth).
2 | Soil Investigation report |  | Please provide the soil investigation report if avialable for proposed substation area inorder to quantiy the foundation works or Kindly provide safe bearing capacity to be considered at 1.5m below existing ground level.
3 | Contour map |  | Kindly request to provide the contour map for the proposed substation area if available.
4 | Location of site |  | As geotechnical investigation & foundation design is included our scope of work, we would like to do following in proposed substation plot inorder to estimate foundation quantity. 1. Preliminary topographical survey 2. Bore log In this regards, kindly request to provide the plot location of the proposed substation.
5 | Changes in site location |  | We undestand that in case of changes in site location during detailed engineering due to that if we have any impact in foundation type and sizes will be paid as additional to the contarctor, please confirm.
6 | Price schedule -civil works, FFPH building with rest room | sl no. 5-b | Kindly request to provide the area of rooms required to be placed at first floor of pump house building.
7 | Price schedule -civil works, landscaping | sl no. 20 | Kindly request to provide the area required for landscaping and provide the type of landscaping required.
8 | Vol-2D, Civil works, High flood level. | sl no. 25, Page no.12 | In order to finalize the finished ground level of proposed substation, kindly request to provide the highest flood level for proposed substation.
9 | Vol-2D, Civil works, retaining wall/Stone pitching. | sl no. 24-b, Page no.12. | As per mentioned clause, we understand that retaining wall is not required incase of filling less than 2m, whereas for filling up to 2m will required stone pitching slope protection , which will also paid as extra to the contarctor , please confirm.
10 | Vol-2D, Civil works, retaining wall. | sl no. 24-b, Page no.12. | As per mentioned clause, we understand that retaining wall is not required incase of filling less than 2m, whereas for filling above 2m will required same and paid as extra to the contractor as per bihar PWD schdule of rates, please confirm.
11 | Retaining wall and stone pitching |  | In case the above clarification sl no.9 & 10 will not paid additional to contartor, we kindly request to include the item for stone pitching & retaining wall for different heights ( 2m, 2.5, 3m , 3.5m etc.) in price schdule.
12 | Vol-2D, Civil works, Tower and equipment support structure - Galvanization thickness. | sl no. 15-b, Page no.5. | Kindly request to provide the minimum galvanization thickness for structural steel members.
13 | Vol-2D, Civil works, Tower structure - standard drawing. |  | Standard drawings for substation gantry and towers are not avialable in BSPTCL website, kindly request to provide 220kV, 132kV & 33kV tower and gantry GA drawings.
14 | Price schedule -civil works, Boundary wall. | sl no. 21 | Kindly request to rovide BSPTCL standard boundary wall , since same is not available on BSPTCL website.
15 | Price schedule -civil works, dormatory building. | sl no. 18 | Kindly request to provide the standard drawing for dormatory building. OR Kindly provide the area required and type of structure to be considered for dormatory building.
16 | Firewall |  | Please clarify firewall will be paid under which item in price the schdule.
17 | Firewall |  | Kindly request to provide the BSPTCL standard drawings for firewall if any.
18 | Price schdule-Erection, Structural steel for lighting cum lighttning mast. | Sl no. R-2 page no.10 & Sl no. O-1 page no.10 | We understand that structure steel required for lighting cum lightning mast will be paid under Sl no. O-1, page no.10 of erection price schdule, no need to consider additional structural steel quantity for same, please confirm.

## 40 PR BSPTCL 2018 (hidden)
|  |  |  | Date: | 2018-07-30
Project | Construction of (2x200MVA+3x50 MVA) 220/132/33KV GSS, Raxaul
Client |  | Bihar State Power Transmission Company Limited.
Contractor |  | Bajaj Electricals Limited.
S.No. | Tender document reference | Clause no. & page no. | Clarification by Contratcor | Response by client | Remarks
1 | General Plot plan |  | Kindly request to provide the general plot plan of the substation area ( length & breadth).
2 | Soil Investigation report |  | Please provide the soil investigation report if avialable for proposed substation area inorder to quantiy the foundation works or Kindly provide safe bearing capacity to be considered at 1.5m below existing ground level.
3 | Contour map |  | Kindly request to provide the contour map for the proposed substation area if available.
4 | Location of site |  | As geotechnical investigation & foundation design is included our scope of work, we would like to do following in proposed substation plot inorder to estimate foundation quantity. 1. Preliminary topographical survey 2. Bore log In this regards, kindly request to provide the plot location of the proposed substation.
5 | Changes in site location |  | We undestand that in case of changes in site location during detailed engineering due to that if we have any impact in foundation type and sizes will be paid as additional to the contarctor, please confirm.
6 | Price schedule -civil works, FFPH building with rest room | sl no. 5-b | Kindly request to provide the area of rooms required to be placed at first floor of pump house building.
7 | Price schedule -civil works, landscaping | sl no. 20 | Kindly request to provide the area required for landscaping and provide the type of landscaping required.
8 | Vol-2D, Civil works, High flood level. | sl no. 25, Page no.12 | In order to finalize the finished ground level of proposed substation, kindly request to provide the highest flood level for proposed substation.
9 | Vol-2D, Civil works, retaining wall/Stone pitching. | sl no. 24-b, Page no.12. | As per mentioned clause, we understand that retaining wall is not required incase of filling less than 2m, whereas for filling up to 2m will required stone pitching slope protection , which will also paid as extra to the contarctor , please confirm.
10 | Vol-2D, Civil works, retaining wall. | sl no. 24-b, Page no.12. | As per mentioned clause, we understand that retaining wall is not required incase of filling less than 2m, whereas for filling above 2m will required same and paid as extra to the contractor as per bihar PWD schdule of rates, please confirm.
11 | Retaining wall and stone pitching |  | In case the above clarification sl no.9 & 10 will not paid additional to contartor, we kindly request to include the item for stone pitching & retaining wall for different heights ( 2m, 2.5, 3m , 3.5m etc.) in price schdule.
12 | Vol-2D, Civil works, Tower and equipment support structure - Galvanization thickness. | sl no. 15-b, Page no.5. | Kindly request to provide the minimum galvanization thickness for structural steel members.
13 | Vol-2D, Civil works, Tower structure - standard drawing. |  | Standard drawings for substation gantry and towers are not avialable in BSPTCL website, kindly request to provide 220kV, 132kV & 33kV tower and gantry GA drawings.
14 | Price schedule -civil works, Boundary wall. | sl no. 21 | Kindly request to rovide BSPTCL standard boundary wall , since same is not available on BSPTCL website.
15 | Price schedule -civil works, dormatory building. | sl no. 18 | Kindly request to provide the standard drawing for dormatory building. OR Kindly provide the area required and type of structure to be considered for dormatory building.
16 | Firewall |  | Please clarify firewall will be paid under which item in price the schdule.
17 | Firewall |  | Kindly request to provide the BSPTCL standard drawings for firewall if any.
18 | Price schdule-Erection, Structural steel for lighting cum lighttning mast. | Sl no. R-2 page no.10 & Sl no. O-1 page no.10 | We understand that structure steel required for lighting cum lightning mast will be paid under Sl no. O-1, page no.10 of erection price schdule, no need to consider additional structural steel quantity for same, please confirm.

## 41 PR BSPTCL 2018 (hidden)
|  |  |  | Date: | 2018-07-30
Project | Construction of (2x160MVA+3x50 MVA) 220/132/33KV GSS, Asthawan.
Client |  | Bihar State Power Transmission Company Limited.
Contractor |  | Bajaj Electricals Limited.
S.No. | Tender document reference | Clause no. & page no. | Clarification by Contratcor | Response by client | Remarks
1 | General Plot plan |  | Kindly request to provide the general plot plan of the substation area ( length & breadth).
2 | Soil Investigation report |  | Please provide the soil investigation report if avialable for proposed substation area inorder to quantiy the foundation works or Kindly provide safe bearing capacity to be considered at 1.5m below existing ground level.
3 | Contour map |  | Kindly request to provide the contour map for the proposed substation area if available.
4 | Location of site |  | As geotechnical investigation & foundation design is included our scope of work, we would like to do following in proposed substation plot inorder to estimate foundation quantity. 1. Preliminary topographical survey 2. Bore log In this regards, kindly request to provide the plot location of the proposed substation.
5 | Changes in site location |  | We undestand that in case of changes in site location during detailed engineering due to that if we have any impact in foundation type and sizes will be paid as additional to the contarctor, please confirm.
6 | Price schedule -civil works, FFPH building with rest room | sl no. 5-b | Kindly request to provide the area of rooms required to be placed at first floor of pump house building.
7 | Price schedule -civil works, landscaping | sl no. 20 | Kindly request to provide the area required for landscaping and provide the type of landscaping required.
8 | Vol-2D, Civil works, High flood level. | sl no. 25, Page no.12 | In order to finalize the finished ground level of proposed substation, kindly request to provide the highest flood level for proposed substation.
9 | Vol-2D, Civil works, retaining wall/Stone pitching. | sl no. 24-b, Page no.12. | As per mentioned clause, we understand that retaining wall is not required incase of filling less than 2m, whereas for filling up to 2m will required stone pitching slope protection , which will also paid as extra to the contarctor , please confirm.
10 | Vol-2D, Civil works, retaining wall. | sl no. 24-b, Page no.12. | As per mentioned clause, we understand that retaining wall is not required incase of filling less than 2m, whereas for filling above 2m will required same and paid as extra to the contractor as per bihar PWD schdule of rates, please confirm.
11 | Retaining wall and stone pitching |  | In case the above clarification sl no.9 & 10 will not paid additional to contartor, we kindly request to include the item for stone pitching & retaining wall for different heights ( 2m, 2.5, 3m , 3.5m etc.) in price schdule.
12 | Vol-2D, Civil works, Tower and equipment support structure - Galvanization thickness. | sl no. 15-b, Page no.5. | Kindly request to provide the minimum galvanization thickness for structural steel members.
13 | Vol-2D, Civil works, Tower structure - standard drawing. |  | Standard drawings for substation gantry and towers are not avialable in BSPTCL website, kindly request to provide 220kV, 132kV & 33kV tower and gantry GA drawings.
14 | Price schedule -civil works, Boundary wall. | sl no. 21 | Kindly request to rovide BSPTCL standard boundary wall , since same is not available on BSPTCL website.
15 | Price schedule -civil works, dormatory building. | sl no. 18 | Kindly request to provide the standard drawing for dormatory building. OR Kindly provide the area required and type of structure to be considered for dormatory building.
16 | Firewall |  | Please clarify firewall will be paid under which item in price the schdule.
17 | Firewall |  | Kindly request to provide the BSPTCL standard drawings for firewall if any.
18 | Price schdule-Erection, Structural steel for lighting cum lighttning mast. | Sl no. R-2 page no.10 & Sl no. O-1 page no.10 | We understand that structure steel required for lighting cum lightning mast will be paid under Sl no. O-1, page no.10 of erection price schdule, no need to consider additional structural steel quantity for same, please confirm.