| Sl. No. | Ref Section | Provision in bidding document | Bidders Queries | POWERGRID Reply |
| --- | --- | --- | --- | --- |
| 1. | Vol. II TS, Section Project clause 2.3.2.1 b) ii) Control, relay and protection and clause 2.3.1.1 B) e) ii) Control, relay and protection | Augmentation of 400kV Duplicate Numerical Bus Bar Protection scheme: | Our scope shall be limited to extension work of 765KV Bays only. Requirement of 400KV augmentation work is not clear. | Only 765kV bus bar augmentation is considered under present scope at Extension of 765/400 kV Kurnool (New) AIS Substation and 765/400 kV Maheshwaram GIS Substation. It is clarified that the text “Augmentation of 400kV Duplicate Numerical Bus Bar Protection scheme:” at referred clause may be read as “Augmentation of 765kV Duplicate Numerical Bus Bar Protection scheme:” in line with BPS |
| 2. | General | DSLP and Illumination layout (for Extension of 765/400 kV Kurnool (New) AIS Substation) | Please provide existing outdoor Illumination and DSLP Layout. | DSLP and Illumination layout shall be shared during detailed engineering, if required. However, bidder is advised to visit site as per cl. 2.5 of section Project. |
| 3. | General | LT SLD (for Extension of 765/400 kV Kurnool (New) AIS Substation) | Please provide existing LT SLD. | LT SLD shall be shared during detailed engineering, if required. However, bidder is advised to visit sites as per cl. 2.5 of section Project. |
| 4. | Vol. II, TS section project, Cl. 3 c | Following items of work are specifically excluded from the scope of the specifications: - Extension of LT Switchgear. | We are not considering any augmentation work of existing ACDB/DCDB for present scope bays (for Extension of 765/400 kV Kurnool (New) AIS Substation). | Spare feeders are available in existing LT switchgear for present scope works. Kindly refer to referred clause of TS wherein it is clearly specified that Extension of LT switchgear is excluded from present scope. |
| 5. | Vol. II, TS section project, Cl. 3 c | Following items of work are specifically excluded from the scope of the specifications: - Extension of LT Switchgear. | Please confirm the availability of LT Feeders at existing ACDB & DCDB for present scope of work in existing AIS SS(for Extension of 765/400 kV Kurnool (New) AIS Substation). We assumed that feeders available for present scope bays. Please confirm. | Spare feeders are available in existing LT switchgear for present scope works. Kindly refer to referred clause of TS wherein it is clearly specified that Extension of LT switchgear is excluded from present scope. |
| 6. | General | Existing battery and battery charger (for Extension of 765/400 kV Kurnool (New) AIS Substation) | We have not envisaged any 220V and 48 V battery/battery charger under present scope. We presume that existing batteries are sufficient to cater all the bays which are coming under present scope. Please confirm. | Confirmed. |
| 7. | General | Location of ACDB/DCDB (for Extension of 765/400 kV Kurnool (New) AIS Substation) | Please confirm the existing ACDB/DCDB location. Provide existing control room building panel arrangement and cable trench layout. | Existing ACDB/DCDB is placed in existing control room building. Cable trench layout is already enclosed along with tender drawings. For panel arrangement layout, bidder is advised to visit site as per cl. 2.5 of section Project. |
| 8. | General | Existing communication equipment (for Extension of 765/400 kV Kurnool (New) AIS Substation) | Please confirm the existing communication system make, model and serial no details for integration point of view. | Existing Communication Equipment Details: Tejas Make TJ 1400 STM -16 Equipment |
| 9. | Vol. II TS, Section Project clause 2.3.2.1 e) vii) | Integration of new Communication equipment in the existing regional NMS. All required support to existing NMS vendor for integration of new Communication equipment. | We understand that bidder have to provide support only to NMS vendor at the existing regional NMS. There are no supply work scope of bidder at the existing regional NMS. Please confirm. | AT Remote End/SS End : Bidder has to provide Telecom Equipment which can be integrated in the existing NMS. Configuration work for necessary integration with existing NMS in supplied FOTE shall be in scope of Bidder AT NMS Server End: Existing NMS Provider/Support team will do the necessary integration/Configuration in existing NMS, However, all necessary support to integrate new Telecom equipment in the existing NMS shall be ensured by the Bidder |
| 10. | Vol. II TS, Section Project clause 2.3.2.1 f) | The broad scope of the procurement of PMU shall include Planning, designing, engineering, supply, transportation, insurance, delivery at site, unloading handling, storage, installation, termination, testing and demonstration for acceptance, commissioning and documentation for PMU as per BPS and these PMU shall support IEEE C 37.118 protocols. These PMUs shall be integrated with Phasor data Concentrator (PDC) at RLDC/SLDC for the subject project. | We understand that PMU shall be integrated with phase data concentrator ( PDC) at RLDC/SLDC of this project. We assumed that there will be no present scope supply work at RLDC/SLDC of this project. Please confirm. | Confirmed. There is NO scope of work at PDC end (at RLDC/SLDC). The Bidder shall extend technical support at local end for seamless integration of PMU with PDC at SLDC/RLDC end |
| 11. | General | Nothing is specifically mentioned in section project about creepage to be consider for Kurnool (New). In GTR it is mentioned 25mm/kV | Please confirm that creepage of 25 mm/kV to be consider for Kurnool (New) AIS Station | Provision of bidding document is amply clear. Creepage of all equipment at Kurnool (New) AIS Station, other than hardware string insulator shall be 25mm/KV. Creepage for hardware string insulator shall be 31mm/kV |
| 13. | Vol. II TS, Section Project clause 2.3.1.1 e) | POWERGRID Maheshwaram Substation is equipped with existing M/s Schneider make Distributed Busbar Protection Type Micom P743. The same is to be suitably augmented for the present scope of work. | Please provide existing CRP & SAS Panel Arrangement Layout. | For existing panel arrangement layout, bidder is advised to visit site as per cl. 2.5 of section Project. |
| 13. | Vol. II TS, Section Project clause 2.3.1.1 e) | No supply item is envisaged for 765KV busbar protection augmentation. Minor supply item required for the augmentation of 765kV bus bar protection, shall be deemed to be included in service item of same. | PGCIL requested to clarify "minor supply" items for more clarity. | Minor supply items for augmentation of bus bar protection includes items like wiring, TBs, aux relay, trips relays etc. as per requirement. |
| 14. | Vol. II TS, Section Project clause 2.3.1.1 g) | LED based Lighting and illumination system for the switchyard area under present scope. | Please provide existing outdoor illumination layout. | Existing Illumination layout shall be shared during detailed engineering, if required. However, bidder is advised to visit site as per cl. 2.5 of section Project. |
| 15. | Vol. II TS, Section Project clause 2.3.1.1 i) | i) Lightning protection (DSLP) The lightning protection (DSLP) for complete switchyard is to be provided by the contractor. The contractor shall design the lightning protection by utilizing the structures and Lightning Mast being provided under present scope. | The lightning protection (DSLP) shall be considered for present scope of work only. Please provide existing DSLP Layout. | Only present area DSLP is included under present scope. Existing DSLP layout shall be shared during detailed engineering, if required. However, bidder is advised to visit site as per cl. 2.5 of section Project. |
| 16. | Vol. II, TS section project, Cl. 3 c | Following items of work are specifically excluded from the scope of the specifications: - Extension of LT Switchgear. | We are not considering any augmentation work of existing ACDB/DCDB for present scope bays (for Extension of 765/400 kV Maheshwaram (PG) GIS Substation). | Spare feeders are available in existing LT switchgear for present scope works. Kindly refer to referred clause of TS wherein it is clearly specified that Extension of LT switchgear is excluded from present scope. |
| 17. | General | Existing Drawings | Please provide existing GIS building Plan & section Layout (of Extension of 765/400 kV Maheshwaram (PG) GIS Substation). | Attached herewith for reference |
| 18. | General | Existing Battery & Battery Charger | We have not envisaged any 110V/220V and 48 V battery/battery charger under present scope. We assumed that existing batteries are sufficient to cater all the bays which are coming under present scope. Please confirm. | Confirmed. |
| 19. | Vol. II, TS section project, Cl. 3 c | Following items of work are specifically excluded from the scope of the specifications: - Extension of LT Switchgear. | Please confirm the availability of LT Feeders at existing ACDB & DCDB for present scope of work in existing GIS SS. We assumed that feeders available for present scope bays. | Spare feeders are available in existing LT switchgear for present scope works. Kindly refer to referred clause of TS wherein it is clearly specified that Extension of LT switchgear is excluded from present scope. |
| 20. | General | Existing Communication System | Please confirm the existing communication system make, model and serial no details for integration point of view (for Extension of 765/400 kV Maheshwaram (PG) GIS Substation).. | Existing Communication Equipment Details: Tejas Make TJ 1400 STM -16 Equipment |
| 21. | Vol. II TS, Section Project clause 2.3.1.1 r) | Integration of new Communication equipment in the existing regional NMS. All required support to existing NMS vendor for integration of new Communication equipment. | We understand that bidder have to provide support only to NMS vendor at the existing regional NMS. There are no supply work scope of bidder at the existing regional NMS. Please confirm. | AT Remote End/SS End : Bidder has to provide Telecom Equipment which can be integrated in the existing NMS. Configuration work for necessary integration with existing NMS in supplied FOTE shall be in scope of Bidder AT NMS Server End: Existing NMS Provider/Support team will do the necessary integration/Configuration in existing NMS, However, all necessary support to integrate new Telecom equipment in the existing NMS shall be ensured by the Bidder |
| 22. | Vol. II TS, Section Project clause 2.3.1.1 s) | The broad scope of the procurement of PMU shall include Planning, designing, engineering, supply, transportation,insurance, delivery at site, unloading handling, storage, installation,termination,testing and demonstration for acceptance, commissioning and documentation for PMU as per BPS and these PMU shall support IEEE C 37.118 protocols. These PMUs shall be integrated with Phasor data Concentrator (PDC) at RLDC/SLDC for the subject project. | We understand that PMU shall be integrated with phase data concentrator ( PDC) at RLDC/SLDC of this project. We assumed that there will be no present scope supply work at RLDC/SLDC of this project. Please confirm. | Please refer reply mentioned at Sl.No 10 above. |
| 23. | General | Nothing is specifically mentioned in section project about creepage to be consider for Maheswaram. In GTR it is mentioned 25mm/kV | Please confirm that creepage of 25 mm/kV to be consider for Maheswaram GIS Station | Provision of bidding document is amply clear. Creepage of all equipment at Kurnool (New) AIS Station, other than hardware string insulator shall be 25mm/KV. Creepage for hardware string insulator shall be 31mm/kV |
| 24 | Vol. II TS, Section-Project : clause 2.3.1.1.s) - PMU | Planning, designing, engineering, supply, transportation, insurance, delivery at site, unloading handling, storage, installation, termination, testing and demonstration for acceptance, commissioning and documentation for PMU as per BPS at and these PMU shall support IEEE C 37.118 protocols. These PMUs shall be integrated with Phasor data Concentrator (PDC) at RLDC/SLDC for the subject project. | As per referred clause, it is mentioned as "Planning, designing, engineering, supply, transportation, insurance, delivery at site, unloading handling, storage, installation, termination, testing and demonstration for acceptance, commissioning and documentation for PMU as per BPS at and these PMU shall support IEEE C 37.118 protocols. These PMUs shall be integrated with Phasor data Concentrator (PDC) at RLDC/SLDC for the subject project." However, we understand the same as follows: 1)PMU integration with PDC at RLDC end is not the present scope of bidder. 2)Technical support shall be extended for seamless integration with PDC at local end. In this regard, Please specify the make & model of Phasor Data concentrator at RLDC/SLDC. Further, we are not envisaging any hardware upgradation/new supply/Software upgradation at PDC. Please confirm. | - Yes, the work at RLDC end for PMU integration with PDC is not under the Scope of the Bidder. - Yes, the Bidder shall extend technical support at local end for seamless integration of PMU with PDC at SLDC/RLDC end. |
| 25 | Vol. II TS, Section-Project : clause 2.3.1.1.r) - PMU | Integration of new Communication equipment in the existing regional NMS. All required support to existing NMS vendor for integration of new Communication equipment. | We understand that NMS integration is limited to Kurnool New (Extn.) and Maheshwaram substation end configuration only. Any work at central NMS server is not in the present scope of bidder. Kindly confirm. | AT Remote End/SS End : Bidder has to provide Telecom Equipment which can be integrated in the existing NMS. Configuration work for necessary integration with existing NMS in supplied FOTE shall be in scope of Bidder AT NMS Server End: Existing NMS Provider/Support team will do the necessary integration/Configuration in existing NMS, However, all necessary support to integrate new Telecom equipment in the existing NMS shall be ensured by the Bidder |
| 26 | General | Tariff meters | Tariff meters are excluded from the present scope of work. We presume these are free issue items from central / state transmission utilities. Mounting & wiring in respective panels alone are considered in scope of this package. Please confirm. If Tariff meters are to be considered in this package please confirm the following: a) Accuracy class of Tariff meters b) specification detailing the requirements such as ABT & TOD features c) Whether separate CT & PT cores are required? d) Bays for which Tariff metering is required in each voltage level | Tariff meter is not envisaged under present scope. However, as per clause 37 of TS section CRP, “Cut-out and wiring with TTB for Employer supplied energy meter” shall be provided under present scope. |
| 27 | General | Order of precedence | In case of contradiction between Section-Project & BPS, please confirm the order of precedence to be followed. | Bid Price Schedule and Section project are generally in conjunction with each other. Bidder to quote as per provisions of bidding document |
| 28 | Vol. II TS, Section-Project : clause 2.0 | General | Please provide the following details for the proposed substation. 1. Soil investigation report (if available) 2. Contour layout showing existing ground level (if available) 3. Average depth of filling in the site 4. Drainage outfall point | 1. The same shall be shared with successful bidder during detailed engineering. 2. Levelling is in the scope of bidder. 3. The same shall be finalized by bidder at the time of detailed engineering. 4. It shall be provided during detailed engineering |
| 29 | Vol. II TS, Section-Project : clause 'Cl.no: 2.3.1.3 Civil works, 3 (x) and Cl.no: 2.3.2.3 Civil works, 3 (iv) | If any non-standard tower or equipment support structure is envisaged during detailed engineering, the same shall be designed by the contractor and submitted to Employer for approval. | As per referred clause, it is mentioned that "If any non-standard tower or equipment support structure is envisaged during detailed engineering, the same shall be designed by the contractor and submitted to Employer for approval.". However in price schedule there is no separate item for Non standard structure and foundation bolts. kindly include item for the same in price schedule. | Presently no non-standard structure is envisaged, bidder may quote as per BPS. |
| 30 | Vol. II TS, Section-Project : clause 'Cl.no: 2.3.1.3 Civil works, 3 (viii) and Cl.no: 2.3.2.3 Civil works, 3 (v) | The Quantity of earthwork cutting & filling, borrowed earth and FGL shall be proposed by vendor for approval of POWERGRID based on the approved contour level drawing and site HFL data. | It is mentioned in the refereed clause that the Quantity of earthwork cutting & filling, borrowed earth and FGL shall be proposed by vendor for approval of POWERGRID based on the approved contour level drawing and site HFL data. Kindly provide the HFL data for the proposed SS area. | The same shall be shared with successful bidder during detailed engineering. |
| 31 | Vol. II TS, Section-Civil Works: clause 20.1 | The quantity shall be measured in cubic meters as per following details: a) Excavation in all kind of soil including soft/ disintegrated rock, PCC, WBM, Brickwork/ stone masonry etc (excluding hard rock). b) Excavation in hard rock (required blasting) | In referred clause, it is mentioned that "The quantity (Excavation) shall be measured in cubic meters as per following details: a) Excavation in all kind of soil including soft/ disintegrated rock, PCC, WBM, Brickwork/ stone masonry etc. (excluding hard rock). b) Excavation in hard rock (required blasting)" However in price schedule, there is no separate item for excavation in hard rock (required blasting). Please include the item for the same in Price schedule. | Hard rock is not envisaged. |