| Sl. No. | Clause No./sections | Existing Clause/item | Amendment |
| --- | --- | --- | --- |
|  | 1.3.7 of Section IVC of Technical Specification | Bird Diverters -----------. The dynamic solar powered LED type Bird Flight Diverter shall be preferred in areas where foggy/dusty weather persists or intensity of light is low or the sections of the lines lying in the route of migratory birds. --------- Bird Diverters. For solar powered LED type diverter,..….The Bird Flight Diverter shall be lightweight (weight not more than 500 gm each), shall offer little wind resistance and should be easily installed by hand or by hot stick (under live line condition) or by any other suitable method. Length of bird diverter, from connection……used in the transmission line as bird diverters. | Bird Diverters -----------. The dynamic solar powered LED type Bird Flight Diverter, consist of warning disc (2-D or 3-D in design) and associated clamps & connectors, shall be preferred in areas where foggy/dusty weather persists or intensity of light is low or the sections of the lines lying in the route of migratory birds. BFD may be mixture of LED and Non-LED BFD, where on a line LED type BFD should be 20%. --------- Bird Diverters. For solar powered LED type diverter,..….The Bird Flight Diverter shall be lightweight (total weight for each Non LED & LED type BFD shall not more than 500 gm and 800 gm respectively), shall offer little wind resistance and should be easily installed by hand or by hot stick (under live line condition) or by any other suitable method. Length of bird diverter, from connection……used in the transmission line as bird diverters. |
|  | 1.3.7(a) of Section IVC of Technical Specification | LED shall be of Orange colour with adequate light intensity so that it is clearly visible to birds from a distance even during foggy/dusty weather/ under low intensity of light. | LED shall be of Orange colour with adequate light intensity so that it is clearly visible from a distance (>300 m) even during foggy/dusty weather/ under low intensity of light. |
|  | 1.3.7.1.1 of Section IVC of Technical Specification | Warning disk of Bird Flight Diverter must swing, sway and rotate and should have contrasting coloured (combination of any two colours from Red, Yellow, Orange, White) retro-reflective surface with Sun and Moon light reflectors on both faces. The colour change, while revolving, shall provide significant forewarning. Warning disk must glow in dark. If Glow in dark stickers are used, the same shall be laminated and suitable for all weather conditions. The Warning disc should be aerodynamically stable so that diverter faces minimum amount of drag force which provide swing and rotation effect under medium/strong wind speed. Diameter of circular warning disk shall not be less than 150 mm. If warning disk is quadrilateral or trapezoid, then shortest arm length should not be less than 90 mm and total surface area of warning disc should not be less that 15,000 mm2 (including air vents). Thickness of the warning disc shall not be less than 3 mm. Minimum reflective area on each face of warning disk shall not be less than 3500 mm2. Glow in Dark area also should not be less than 3500 mm2. All suspension hardware which are directly exposed (moving or static) must be corrosion free. Bearing swivel shall be made of stainless steel and should allow free spinning in minimum wind speed of 2 km/hour. | Warning disk of Bird Flight Diverter must swing, sway, must not flip on the powerline in high wind velocity, rotate and should have contrasting coloured (combination of any two colours from Red, Yellow, Orange, White) retro reflective surface with Sun and Moon light reflectors on both faces. The colour change, while revolving, shall provide significant forewarning. Warning disk must glow in dark & glow in the dark shall remain activated for at least 12 hours after exposure to sunlight and the warning disk in the BFD should have strong luminescence properties that emit immense light to provide enhanced visibility to the birds at night. If Glow in dark stickers are used, the same shall be laminated and suitable for all weather conditions. The Warning disc should be aerodynamically stable so that diverter faces minimum amount of drag force which provide swing and rotation effect under medium/strong wind speed. Diameter of circular warning disk shall not be less than 150 mm. If warning disk is quadrilateral or trapezoid, then shortest arm length should not be less than 90 mm and total surface area of warning disc should not be less that 15,000 mm2 (including air vents). Thickness of the warning disc shall not be less than 3 mm. Minimum reflective area on each face of warning disk shall not be less than 3500 mm2 & the reflective area for non LED type BFD shall not be less than 7500 mm2. Glow in Dark area also should not be less than 3500 mm2 for LED type BFD. All suspension hardware which are directly exposed (moving or static) must be corrosion free. Bearing swivel shall be made of stainless steel and should allow free spinning in minimum wind speed of 1 km/hour & be made of sealed bearing to avoid deposition of sand and/or soil particles and helps in smooth rotation. |
|  | 1.3.7.1.2 of Section IVC of Technical Specification | `The clamp of the Bird flight diverter shall be made of UV stabilized engineered composite plastic. Spring type clamp, suitable for holding earth wire/ OPGW shall be used. It shall-------------------500N. | The clamp of the Bird flight diverter shall be made of UV stabilized engineered composite plastic(polymer) or metal or carbon fibre. Spring type clamp, suitable for holding earth wire/ OPGW shall be used. It shall-------------------500N. |
|  | Vol II, Technical specification | Existing Section IA of Technical specification | Revised Section IA of Technical specification attached as “Section IA (standard)ScopeRev-3(Feb'2022)”. |
|  | Price Schedule | Price_schedule | “Price_schedule” stands replaced with “Price_schedule-rev01” |
|  | The ‘Price_schedule’ excel stand revised as ‘Price_schedule-rev01’. Bidders are requested to consider the revised excel ‘Price_schedule-rev01’ for bid preparation/submission. It may be noted that while submitting the bid, Bidders are required to change the excel file name from ‘Price_schedule-rev01’ to ‘Price_schedule’. As per the provisions of the portal, it is mandatory to upload excel file with titled ‘Price_schedule’ (Bidders may refer user manuals at the portal https://etender.powergrid.in regarding submission of bid). |  |  |