| Sl. No. | Details as per Technical Specification Document No / Clause No / | Description as per Bid Document | Remarks - Query / Clarification | POWERGRID’s clarification |
| --- | --- | --- | --- | --- |
| 1. | Clause 1.3. of Volume-II-Part 04 of 11, 07_3 Section VII B HTLS Conductor Rev-3(Jan'2022) | Sag of the offered HTLS conductor at designed maximum temperature should not be more than that specified in Section-I. Sag of the offered HTLS conductor at minimum temperature shall not be less than the minimum values specified in section-I. | Sag value is not specified in Section-I for HTLS conductor. Please provide the sag value. | As the design of Tower along with HTLS conductor is in the scope of bidder, Sag value to be considered by bidder to meet all technical requirements based on the wind pressure & Tension parameters given in Section -1A of Technical Specification. |
| 2 | Clause 1.3. S.No. 4 of Volume-II-Part 01 of 11, 01_1 Section IA (standard)Scope Rev-3(Feb'2022) | Tension at 32°C and full wind condition ≤ 11421 kg corresponding to wind pressure of [80.90X Gust Factor] kg/m2 as per IS802 & not exceeding 70% of UTS of proposed conductor | Please confirm the Wind Pressure of 80.90 kg/m2 is excluding Coastal factor, K4 = 1.3. After considering coastal factor, wind pressure workout as 136.68 kg/m2.Please confirm whether Coastal factor not to be considered and use 80.90 wind pressure or Coastal factor to be considered and use 130.68 kg/m2 wind pressure for Sag & Tension calculation & design. | Please refer clause No: 1.4.9 f) of Section – IV A of Technical specification |
| 3 | Vol II, SECTION-I B General Information 2.26 |  | Minimum Current carrying capacity/Ampacity at maximum design continuous operating temperature(A) for subject package is 1368A as per (VOLUME-II), SECTION-I A SCOPE. Please confirm will the type test be waived off in case bidder submits higher rating/specification type test report for HTLS Conductor. | Bidders to offer HTLS Conductor as per Technical Requirements stipulated in cl.1.3 of section IA of Technical Specification. |
| 4 | TECHNICAL SPECIFICATIONS Section -IA |  | Request to share termination point at 400 kV D/C RIL (Oil Refinery) (GIS). Also share layout/SLD of 400kV D/C RIL (Oil Refinery) (GIS). | Please refer Clause 1.4.1 of Section-IA of technical specifications. |