| Sl. No. | Details as per Technical Specification Document No / Clause No / | Description as per Bid Document | Remarks - Query / Clarification | POWERGRID’s clarification |
| --- | --- | --- | --- | --- |
| 1. | Technical |  | We understand that in case, some special arrangement viz. semi-strain assembly is required to maintain low sag behavior of offered HTLS conductor in longer spans, supply & installation of such arrangement shall be in the scope of the client /PGCIL. Kindly confirm. | Cost of supply and installation of required number of such arrangements (semi strain assembly) shall be deemed to be included in the total quoted price which is mentioned at Cl. 1.2 of section VI B. |
| 2 | BOQ/Spacer Damper Twin HTLS |  | While referring BOQ only spacer damper quantities has given in BOQ for Twin HTLS fittings, we recommended to use vibration damper along with spacer damper to control adequate Aeolian Vibration. In Twin HTLS conductor is very sensitive as compared Convectional Conductor, please suggest. | As per cl. 2.7 of Section VI B, Spacer damper shall be designed to effectively control Aeolian vibrations as well as sub span oscillation and to restore conductor spacing after release of any external extraordinary load |
| 3 | Section-VIB(Volume-II), Rev 2 (Jan-2022) Clause 1.14.3 steel sleeve of compression dead end/mild span joint shall be cl-II |  | The Steel sleeve of the compression dead end and MSCJ shall be CL-IV. The same material has been tested and supplied in various POWERGRID projects, kindly confirm. | Steel sleeve of the compression dead end and MSCJ shall be either mild steel as per IS-2062 or forged steel (Class-II) as per IS -2004 as specified in table-1 of cl. 1.14.3 of Section VIB. |
| 4 | Section-VIB(Volume-II), Rev 2 (Jan-2022) Clause 3.1.9 |  | Tests should have been conducted on the samples of clamps & accessories for HTLS conductor manufactured from same manufacturing works within last 7 years as on the date of NOA. In Power grid, type test done at once. This type test reports validity shall not be applicable for Power grid project, kindly confirm. | Validity of type test for offered design shall be as cl. 3.1.9 of Section VI B. |
| 5 | SECTION-VIII (VOLUME-II), Rev 2 (Jan’2022) Clause No 1.1.5 | The dimension tolerance is mentioned +10mm | As per the previous specification SECTION-VIII (VOLUME-II), Rev 1 (Oct’2021) page 1 of 32 Clause No 1.1.5, the dimension tolerance is mentioned as ± 50 mm (Copy attached) whereas as per the latest specification SECTION-VIII (VOLUME-II), Rev 2 (Jan’2022) Clause No 1.1.5, the dimension tolerance is mentioned +10mm (Copy attached). Please clarify that tolerance to be consider as ± 50 mm or +10mm | Maximum tolerance of +10mm as per cl. 1.1.5 of section -VIII. |
| 6. | SECTION-VIII (VOLUME-II), Rev 2 (Jan’2022) Clause No 1.1.5 | The dimension tolerance is mentioned +10mm | The PGCIL specification SECTION-VIII (VOLUME-II), Rev 1 (Oct'2021) page 1 of 32 Clause No 1.1.5, the dimension tolerance of composite insulator is mentioned as ± 50 mm whereas as per the latest PGCIL specification SECTION-VIII (VOLUME-II), Rev 2 (Jan'2022) page 1 of 32 Clause No 1.1.5, the dimension tolerance of composite insulator is mentioned ± 10mm. Please note as per IEC 61109 /2008 and IS 16784, the dimension tolerances of composite insulator are ± 50 mm. Kindly request you to amend the specification SECTION-VIII (VOLUME-II), Rev 2 (Jan'2022) page 1 of 32 Clause No 1.L.5, the dimension tolerance of composite insulator to be mentioned as ± 50 mm. | Please refer Sl. No. 5 above. |