| Sl. No. | Details as per Technical/Commercial Specification Document No / Clause No / | Remarks - Query / Clarification | POWERGRID’s Clarification |
| --- | --- | --- | --- |
| 1. | Volume II, Section IVA, Clause 1.4.9 | Kindly confirm following formula to be used on wind on tower for Oblique wind: - Fwt, Trans = Pd* (1 + 0.2 sin²2θ) (AeT*CdtT*cosθ)*GT Fwt Long = Pd *(1 + 0.2 sin²2θ) (AeL*CdtL*sinθ)*GT | Confirmed |
| 2. | Volume II, Section XI, Extension application scheme | Kindly confirm whether it is mandatory to use extension scheme provided or we can modify while maintaining all the extensions and max length of panel (14m) and unequal leg-extension criteria. | The extension scheme attached at Section XI is indicative in nature only. Bidder may adopt extension scheme as per their design complying with technical requirements given. |
| 3. | As per sl.26, lTB 24.1(c) "The time for completion for the subject work is only 12 Months”. | ln general practice, considering the ROW issue in the state of Gujarat, the completion period of 12 months is not sufficient for the above work. So we request you to kindly amend it for 18 months. | Provision of the bidding documents shall remain unchanged |
| 4. | As per Appendix-2, Price Adjustment, Sec-VI, Vol-1, Only “Fabricated Tower parts including Bolts & Nuts)" are variable and rest of the items including Installation (lncluding Civil works) Price component are Firm Basis. | As per standard practice of PGCIL RTM tender and considering in volatility in commodity prices, we request you to revise the Appendix-2 and make "price Variable” for Earthwire, HTLS Conductor, Hardware Fittings & Accessories for conductor, lnstallation (including Civil Works) | Provision of the bidding documents shall remain unchanged |