| S N | Clause Reference | Text as per TS/BDS | Bidder's Queries | POWERGRID Reply |
| --- | --- | --- | --- | --- |
| 1 |  |  | There are some reactor of 125MVAr, which have installation in Jammu & Kashmir, Himachal, for these locations we need environmental details like Minimum temperature, altitude and snowfall etc and Transport limitations. | 400 kV POWER GRID CHAMERA (CHAMBA) S/S : 1. Minimum/ Maximum Temperature : (-)1 Deg. C / (+)39 Deg. C 2. Altitude: 951 Metre. 3. Snowfall: Snowfall happens once in Three to Four years. 400 kV POWER GRID KISHENPUR S/S : 1. Minimum ambient Temperature- 0-2 degree C, Max. ambient Temperature- 46 deg. C 2. Altitude-443 Mtr. 3. Snowfall- Not reported till now. Further there are no transport limitations for above mentioned POWERGRID substations however Bidder shall be responsible to select and verify the route, mode of transportation and make all necessary arrangement with the appropriate authorities for the transportation of the equipments. |
| 2 | BOQ Mandatory Spares | Bushings – 1 Set per substation. | Please note that 3 Phase SR have 3 nos. of 420 kV & 1 no. of 145 kV bushing. We understand that 1 set of spare bushing means 1 no. of HV i.e 420 kV & 1 no. of Neutral i.e 145 kV bushing. Hence we shall be considering 1 HV & 1 Neutral bushing as spare per substation. Kindly confirm or define 1 set of spares bushing. | Bidders understanding is correct .1 set of Bushing consists One (1) No. of bushing of each rating. |
| 3 | Technical specification for RTV Silicone high voltage insulation coating (HVIC) Technical specification of Shunt Reactor – R10 – Cl. 11.2 : | Bushing for voltage of 52 kV and above shall be RIP bushing with composite insulator | Please note that as per Shunt Reactor specification bushing shall be RIP bushing. Along with specification a document titled as “Technical specification for RTV Silicone high voltage insulation coating (HVIC)” is also furnished. As per discussion held with RIP bushing suppliers RTV silicone coating is not applicable for RIP bushing. Hence we understand that document “Technical specification for RTV Silicone high voltage insulation coating (HVIC)” is not applicable for Shunt Reactor. Kindly confirm. | RTV Coating is not envisaged for RIP bushing with composite insulators .Hence Bidders understanding is correct. |
| 4 | Annexure B, No. 12, page 42 of 80 Annexure C, No. 7, page 45 of 80 | Test Plan Induced Over Voltage Test with Partial Discharge Measurement Test procedure Dielectric Tests Following Tests (as applicable) shall be performed in the sequence given below as per IEC 60076-3:2013 clause 7.2.3 shall be followed: a) Lightning impulse tests (LIC, LIN) b) Switching impulse (SI) c) Applied voltage test (AV) d) Induced voltage test with partial discharge measurement Testing shall be performed in line with IEC. DGA tests shall be performed before and after Dielectric Tests. | With reference to the requirement of Induced voltage test with partial discharge measurement and its defined procedure as per IEC 60076-3:2013, customer may note followings:- a) As per our existing testing practice and capability, IVPD (ACLD test with levels of IVPD test) test is conducted by single phase method in line IEC 60076-3: 2000. b) Our proposal for up gradation of Reactor Test facilities to meet the test requirement stipulated as per IEC 60076-3:2013 is presently under implementation and upgradation will take about 18 months. c) Under above circumstances we will not be able to conduct IVPD test as per POWERGRID spec. Therefore IVPD test shall be carried out by single phase method, as being done in the running contracts of PGCIL. | Bidder to follow IVPD test as per agreed methodology followed in earlier projects. |
| 5 | Location of Work (*) | Kishenpur,Jallandhar, Maharanibagh, Mandola, Hissar, Chamera, Moga, Patiala,Sikar, Allahabad and Meerut | We understand Kishenpur & Chamera are in hilly terrain and transportation of 125 MVAR will be difficult. It is proposed to take Bank of 3 x 41.66 MVAr shunt reactor in place of 125 MVAR SR for these sites as taken by other utilities like NHPC for Chamera. | The Bidder shall be responsible to select and verify the route, mode of transportation and make all necessary arrangement with the appropriate authorities for the transportation of the equipments.Further it is worthwhile to mention that in past at both Chamera and Kishenpur sites 105 MVA ,1Ph ,400/220/33 kV Transformers (which are approximately comparable in dimension and weight to 125 MVAr reactors) have already been transported and suceesfully installed. |
| 6 | Attachment-9, Bid Form, 1st Envelope |  | We would like to bring your notice that the discrepancy in project completion period between BDS document and First Envelop as mentioned below. | Please refer Sr .No.- 4 of Amendment-01 |