| POWER GRID CORPORATION OF INDIA LTD. (A Government of India Enterprise) |  |  |
| --- | --- | --- |
| TECHNICAL SPECIFICATION FOR ----------- |  |  |
|  | VOLUME-II |  |
| (This document is meant for the exclusive purpose of bidding against this specification and shall not be transferred, reproduced or otherwise used for purposes other than that for which it is specifically issued). |  |  |

TECHNICAL SPECIFICATION

(VOLUME-II)

CONTENTS

| SECTION-I A | SCOPE |
| --- | --- |
| SECTION-I B | GENERAL INFORMATION |
| SECTION-II | GENERAL TECHNICAL CONDITIONS |
| SECTION-III | SURVEY AND SOIL INVESTIGATION |
| SECTION-IV A | TOWER DESIGN* |
| SECTION-IV B | TOWER TESTING* |
| SECTION-IV C | FABRICATION, ERECTION AND STRINGING |
| SECTION-IV D | FOUNDATION (CONTRACTOR DESIGN)* |
| SECTION-IV E | FOUNDATION (EMPLOYER DESIGN) |
| SECTION-IV F | MONOPOLE STRUCTURE, FOUNDATION AND ERECTION* |
| SECTION-V | GALVANISED STEEL EARTHWIRE |
| SECTION-VI A | HARDWARE FITTINGS & ACCESSORIES |
| SECTION-VI B | CLAMP FITTINGS AND ACCESSORIES FOR HTLS CONDUCTOR* |
| SECTION-VII A | CONDUCTOR |
| SECTION-VII B | HTLS CONDUCTOR* |
| SECTION-VIII | COMPOSITE LONGROD INSULATOR |
| SECTION-IX A | PILE FOUNDATION* |
| SECTION-IX B | STONE COLUMN* |
| SECTION-X | OPGW |
| SECTION-XI | DRAWINGS |
| SECTION-XII | FAQ |
| SECTION-XIII | TOWER SCHEDULE OF EXISTING LINE* |

*Not Applicable

SECTION-I A

SCOPE

TECHNICAL SPECIFICATIONS

SECTION-I A

# SCOPE

# Revision History

| # Revision No. | # Date | # Clause Ref | # Description |
| --- | --- | --- | --- |
| # Rev-0 | # June’2021 |  | # First Release |
| # Rev-1 | # Sept’2021 |  | # First Revision |
| # Rev-2 | # Oct’2021 |  | # Second Revision |
| # Rev-3 | # Jan’2022 |  | # Third Revision |
| # Rev-4 | # Apr’2022 |  | # Fourth Revision |
| # Rev-5 | # July’2022 |  | # Fifth Revision |
| # Rev-6 | # Feb’2023 |  | # Sixth Revision |
| # Rev-7 | # Sept’2023 | # 2.1.1.1 | # Seventh Revision |
| # Rev-8 | # Dec’2023 | # 3.4 (v) | # Eighth Revision |
| # Rev-9 | # March’2024 |  | # Ninth Revision |
| # Rev-10 | # Jan’2025 |  | # Tenth Revision |
| # Rev-11 | # Jan’2025 | # 1.2 (xxvii) | # Eleventh Revision |

TECHNICAL SPECIFICATIONS

SECTION-I A

# SCOPE

CONTENTS

| Clause No. | Description | Page No. |
| --- | --- | --- |
| 1.0 | Scope | 1 |
| 2.0 | Qualification Requirements | 12 |
| 3.0 | Transmission towers & line data | 20 |
| 4.0 | Different Sections to Technical Specification | 30 |
| 5.0 | Service Condition | 32 |

# TECHNICAL SPECIFICATIONS

# SECTION- I A

SCOPE

  - Scope

  - The following transmission lines are included in the scope of the Contractor under various packages:

Package – TL01

- Construction of 400kV D/C Quad Bareilly- Bareilly Line

  - This Specification covers the following scope of works:

          - Detailed survey including route alignment, profiling, tower/ *pole structure spotting, optimization of tower/*pole structure locations, soil resistivity measurement & geotechnical investigation (including special foundation locations viz. pile/well foundation locations, whenever applicable & covered under BPS);

          - Check survey.

          - *Design and Proto type testing of transmission line towers

          - *Fabrication and supply of all type of transmission line Towers as per Employer’s design/drawings including River crossing towers (wherever applicable) including fasteners, step bolts, hangers, D-shackles etc.;

          - Supply of all types of tower accessories like phase plate, circuit plate (where ever applicable), number plate, pole plate (where ever applicable), danger plate, anti-climbing device, Bird guard, (where ever applicable);

          - Supply of

- Earth wire

- Hardware Fittings and accessories for Conductor/*Earth wire

- *Conductor (as per BPS)

- *Insulators

- *OPGW & associated fittings & accessories.

          - Classification of foundations for different type of towers and Casting of Foundations for tower/ *pole structure footings as per Employer’s foundation design/ drawing;

          - Supply & Installation of Tower/ *Pole structure Earthing.

          - Supply & installation of Insulated Conductor sleeve, (if required & covered under BPS);

          - Supply & installation of Bird Diverter, (if required & covered under BPS);

          - Erection of towers/ *pole structures by using crane (wherever feasible), tack welding of bolts and nuts including supply and application of zinc rich paint, fixing of insulator strings, stringing of conductors and earth wires/OPGW* along with all necessary line accessories. For transmission lines, to promote mechanization and safe working conditions, use of crane is being promoted.  However, where usage of crane is not possible, erection of towers has to be carried out by conventional method i.e using Gin pole, Derrick, Centre mast etc. through usage of Power Operated Winch Machines. No tractor shall be allowed for tower/ *pole structure erection.;

          - Destringing & dismantling of existing 765/400/220/132/66kV Transmission line. (whenever applicable & covered under BPS)

          - Stringing of Power line crossing section under Live Line Condition (where ever applicable & covered under BPS);

          - Cable bypass arrangement of 11KV/33KV/LT Powerline crossing. (wherever applicable & covered under BPS)

          - Stringing of transmission line through Drones (wherever applicable & covered under BPS).

          - Painting of towers/ *pole structures & supply and erection of span markers, obstruction lights (wherever applicable) for aviation requirements (as required)

          - Testing and commissioning of the erected transmission lines and

          - Other items not specifically mentioned in this Specification and/or BPS but are required for the successful commissioning of the transmission line, unless specifically excluded in the Specification.

          - The installation/stringing of OPGW cable along with associated fittings & accessories shall be carried out by the contractor. The scope of installation/stringing shall include splicing, termination, testing, demonstration for acceptance & commissioning as well as documentation. Splicing is preferred to be carried out at Tension towers locations. However, it shall be permitted at Suspension Tower locations also as required due to site conditions. The installation/stringing and splicing shall be carried out as per owner guidelines (provided as part of TS). The FODP & Approach cable shall also be installed by the Contractor (where ever applicable as per BPS).

  - Destringing/ Dismantling

    - The scope of works includes destringing of conductor, earthwire & OPGW, removal of hardware fittings, insulators, conductor, earthwire & OPGW accessories, etc. and dismantling of tower from some sections of existing 400kV line and transporting of dismantled materials to designated POWERGRID stores. The Employer shall arrange shut down of charged sections of existing transmission lines, if required, before carrying out destringing & dismantling works as per program finalized in co-ordination with site. Appropriate safety measures along with necessary safety tools and equipments to carry out destringing and stringing operations under the above conditions including mechanical/ structural safety of the towers shall be the responsibility of the contractor. The entire quantity of dismantled line materials viz. tower parts, conductor, earthwire, OPGW, hardware fittings, insulators and conductor, earthwire & OPGW accessories removed from the existing line shall be transported to the designated POWERGRID stores by the contractor at his own cost. The Bidder shall submit his offer taking into consideration transportation cost of the dismantled material.

    - The contractor shall inspect the affected stretch of transmission lines and shall accordingly devise appropriate methodology/procedure of carrying out the destringing/restringing works during detailed engineering & execution stage in consultation with the site-in-charge.

  - Details of Transmission Line Routes and Terrain

The detailed survey shall be carried out using Total stations along the approved route alignment. As an alternative, the contractor may also use ALTM (Airborne Laser Terrain Modeling) techniques of equal or better accuracy for the detailed survey.

The tower schedule of the transmission line prepared during its construction is enclosed for reference in Section-Tower Schedule of this Volume. During execution, Profiling of existing line route (quantity indicated in the BPS) covering ground profile, locating towers, verification of Sag profile of HTLS conductor at designed maximum temperature & verification of clearances etc. employing Total Stations & PLSS CAD software shall be carried out by the contractor. (applicable only for Re-conductoring packages)

Quantity of detailed survey including route alignment, profiling, tower/ *pole structure spotting, optimization of tower/ *pole structure locations, soil resistivity measurement & geotechnical investigation etc. of lines have been indicated in the BPS.

    - Bidders may visit the line route to acquaint themselves with terrain conditions and associated details of the proposed transmission lines. For this purpose they are requested to contact the following address:

Dy General Manager,

765/400kV Sub-Station,

Power Grid Corporation of India Ltd,

Bareilly- Nainital Road, Bareilly

  - Location Details and Terminal Points

    - The transmission line shall emanate from 400kV Sub-Station in the State of Uttar Pradesh and terminate at 765kV Sub-Station in the State of Uttar Pradesh.

The 400kV D/C Quad Bareilly- Bareilly transmission line is passing through Plain*/Hilly*/Snow Zone/Coastal/Creek/Marine* area.

    - The Contractor shall have to construct the transmission line portions, covered under the tower package, completely up to dead end towers at either/*substation end. Stringing shall also be carried out from dead end tower to terminal arrangements/terminal points.

- Qualification Requirements

QUALIFICATION OF THE BIDDER Qualification of bidder will be based on meeting the minimum pass/fail criteria specified below regarding the Bidder’s Technical Experience and Financial Position as demonstrated by the Bidder’s responses in the corresponding Bid Schedules. Subcontractors’ technical experience and financial resources shall not be taken into account in determining the Bidder’s compliance with the qualifying criteria. The bid can be submitted by an individual firm. The Employer may assess the capacity and capability of the bidder, to ascertain that the bidder can successfully execute the scope of work covered under the package within stipulated completion period. This assessment shall inter-alia include (i) document verification; (ii) bidders work visit; (iii) details of works executed, works in hand, anticipated in future & the balance capacity available for the present scope of work; (iv) details of plant and machinery, testing facilities, manpower and financial resources; (v) details of quality systems in place; (vi) past experience and performance; (vii) customer feedback; (viii) banker’s feedback etc. 2.1 Technical Experience The Bidder should have carried out the following as a prime contractor+: - Successfully completed$ physical construction of one (1) transmission line project of not less than 2.4 kms of 345kV S/C or 345kV D/C or higher voltage class transmission line within the last seven (07) years as on the originally scheduled last date of bid submission (soft copy) i.e. --------------- involving the following scope of work: - Tower foundation, erection and stringing - Supply of tower & tower parts - Supply of line material viz. Conductor or Insulator or Hardware Fittings Note + : In case the bidder has executed the work under a contract that had been awarded on a Joint Venture wherein the bidder was one of the partners, the experience of the bidder shall be considered limited to the scope executed by the bidder as a partner under the said contract. In case Bidder is a holding company, the technical experience referred to in clause 1.1 above shall be of that holding company only (i.e. excluding its subsidiary/group companies). In case Bidder is a subsidiary of a holding company, the technical experience referred to in clause 1.1 above shall be of that subsidiary company only (i.e. excluding its holding companies). $ Successfully completed means issue of provisional or final taking over certificate (TOC) by the Employer to the contractor for the referred contract.

2.2 FINANCIAL POSITION: a) Net worth of the bidder for last 3 financial years should be positive. b) Minimum Average Annual Turnover*(MAAT) for best three years i.e. 36 months out of last five financial years of the bidder should be Indian Rs. 12.89 crore for Package—TL01. * Note- Annual Gross Revenue from operations/Gross operating income as incorporated in the profit & loss account excluding other operative Income/ other income. c) Bidder shall have liquid assets (L.A) or/ and evidence of access to or availability of credit facilities of not less than Indian Rs. 2.15 crore for Package-- TL01. In case bidder is a holding company, the financial position criteria referred to in clause 1.2 above shall be of that holding company only (i.e excluding its subsidiary/ group companies). In case bidder is a subsidiary of a holding company the financial position criteria referred to in clause 1.2 above shall be of that subsidiary company only (i.e excluding its holding company) Note: Relaxation for STARTUPs ^/ MSEs Start-Ups^/ MSEs, meeting the specified requirements at Para 1.2 (a) in Financial Position shall also be considered qualified if they meet Eighty (80) % of the requirement specified at Para 1.2(b) & 1.2 (c) in Financial Position. ^Start-Ups as defined by DPIIT, applicable as on the originally scheduled date of bid submission (soft copy).

- Transmission towers and Line data

  - General Description of the Tower*

    - The transmission towers covered under the package are of self-supporting hot dip galvanized lattice steel type, designed to carry the line conductors with necessary insulators, earth wire*, OPGW*(If applicable) and all fittings under all loading conditions.  Outline diagram of towers are enclosed with the Specification.

    - The towers shall have mild steel or/and high tensile steel sections and shall be fully galvanized as specified in relevant clauses in section-IV. Bolts and nuts with spring washer are to be used for connections.

    - The towers are of the following types:

A) 	Double Circuit*

  - Classification of Towers

| Sl No | Type of Tower |  | Deviation Limit | Typical Use |
| --- | --- | --- | --- | --- |
| 1 | DA |  | 0 – 2 deg. | To be used as Tangent tower. |
| 2 | DB |  | 0 deg. | To be used as Section Tower. |
|  |  |  | 0 - 15 deg. | - Angle towers with tension Insulator string. |
|  |  |  |  | - Also to be used for uplift force resulting from an uplift span up to 200m under broken wire conditions. |
|  |  |  |  | - Also to be used for Anti Cascading Condition. |
| 3 | DC |  | 0 deg. | To be used as Section Tower. |
|  |  |  | 15-30 deg. | - Angle tower with tension insulator string. |
|  |  |  |  | - Also to be used for uplift forces resulting from an uplift span up to 200m under broken wire condition. |
|  |  |  |  | - Also to be used for anti-cascading condition. |
| 4 |  | DD | 30- 60 deg. | - Angle tower with tension insulator string. |
|  |  |  |  | - Also to be used for uplift forces resulting from an uplift span up to 300m under broken wire condition. |
|  |  |  | 0 deg. | - For river crossing anchoring with longer wind span |
| 5 |  | DDE |  | Dead end with 0 deg to 15 deg deviation both on line side and sub-station side (slack span) |
|  |  |  | 0 deg. | - Complete Dead end |

1.	The above towers can also be used for longer span with smaller angle of deviations without infringement of ground clearance.

2.  	The above table provides indicative classification of Towers. Tower spotting data for various towers to be used in the transmission lines under the specific package shall be given to the contractor during execution stage.

3.     The contractor is permitted to offer tower/foundation design of higher tower loading / higher Wind Zone / higher deviation angle than the details specified for the transmission lines in this section/BPS.  However, payment for supply , erection  & installation of the  offered  tower/foundation  shall  be restricted to the price quoted by the bidder against the required tower type specified in BPS.

6.     For Non-Snow Regions, the contractor may also use IS Steel Sections of any tested quality A or BR in conformity with IS 2062:2011 corresponding to grade E450 (Designated Yield Strength 450 MPa) in addition to provisions mentioned in clause 1.1.1 Section IV C for towers, extensions, stubs and stub setting templates (This clause is not applicable for projects through TBCB route).

    - Special Towers

The towers which will be specially designed for very long spans which cannot be crossed by normal tower with extensions as given in relevant clause like Major River crossings etc. shall be treated as special towers.

  - Electrical Clearances

    - Ground Clearance

The minimum ground clearance from the bottom conductor shall not be less than 8840 mm for 400KV lines at the maximum sag conditions i.e. at max temperature as indicated in tower spotting data and still air.

a) 	An allowance of 150mm shall be provided to account for errors in stringing.

b) 	Conductor creep shall be compensated by over tensioning the conductor at a temperature as mentioned in section IV of this specification.

- Different Sections to Technical Specification

  - For the purpose of present scope of work, technical specification shall consist of following parts and they should be read in conjunction with each other: -

| Sl. No. | Section Number | Name of Section | Rev No. |
| --- | --- | --- | --- |
| 1 | Section-IA | Scope | Rev-11 (Jan’2025) |
| 2 | Section-IB | General Information | Rev-11 (Jan’2025) |
| 3 | Section-II | General Technical Conditions | Rev-3 (Nov’2024) |
| 4 | Section-III | Survey and Soil Investigation | Rev-5 (Dec’2023) |
| 5 | Section-IVA | Tower Design (N/A) | Rev-6 (Dec’2023) |
| 6 | Section-IVB | Tower Testing (N/A) | Rev-3 (Dec’2023) |
| 7 | Section-IVC | Fabrication, Erection and Stringing | Rev-8 (Jan’2025) |
| 8 | Section-IVD | Foundation (Contractor Design) (N/A) | Rev-6 (Dec’2023) |
| 9 | Section-IV E | Foundation (Employer Design) | Rev-5 (Dec’2023) |
| 10 | Section-IV F | Monopole Structure, Foundation and Erection (N/A) | Rev-2 (Mar’2023) |
| 11 | Section-V | Galvanised Steel Earthwire | Rev-1 (May’2024) |
| 12 | Section-VIA | Hardware Fittings and Accessories for Conductor & Earthwire | Rev-3 (Dec’2023) |
| 13 | Section-VIB | Clamp Fittings and Accessories for HTLS Conductor (N/A) | Rev-2 (Jan’2022) |
| 14 | Section-VIIA | Conductor | Rev-3 (Dec’2023) |
| 15 | Section-VII B | HTLS Conductor (N/A) | Rev-5 (Sept’2024) |
| 16 | Section-VIII | Composite Longrod Insulators | Rev-4 (Oct’2024) |
| 17 | Section-IX A | Pile foundation (N/A) | Rev-6 (OCt’2024) |
| 18 | Section-IX B | Stone Column (N/A) | Rev-0 (Dec’2023) |
| 18 | Section-X | OPGW | Revision (June’2024) |
| 20 | Section-XI | Drawings | Rev-1 (Aug’2023) |
| 21 | Section-XII | FAQ | Rev 0 (June’2021) |
| 22 | Section-XIII | Tower Schedule of Existing Line (only applicable for Re-conductoring packages) (N/A) |  |

(to be modified as applicable for the package)

  - In case of any discrepancy between Section-IA (Scope) and Section-IB (General Information) and other technical specifications on scope of works, Section-IA (Scope) shall prevail over all other sections.

  - In case of any discrepancy between Section-IB (General Information) and individual sections for various equipment, requirement of individual equipment section shall prevail.

- Service Conditions:

Equipment/material to be supplied against this specification shall be suitable for satisfactory continuous operation under tropical conditions as specified below:

| Maximum ambient temperature (oC) | 50 |
| --- | --- |
| Minimum ambient temperature (oC) | 0 |
| Relative humidity (% range) | 10-100 |
| Wind zone (as per NBC) | 5 |
| Terrain Category | 2 |
| Maximum wind velocity (m/sec.) | 50 |
| Maximum altitude above mean sea level (Meters) | Below 1000m |

Annexure-A

PROFORMA OF UNDERTAKING BY THE PROPOSED AGENCY FOR PILE FOUNDATION

(On Non-Judicial Stamp Paper of appropriate value, wherever applicable)

To,

Power Grid Corporation of India Ltd.

B-9, Qutab Institutional Area

Katwaria Sarai

New Delhi - 110016

Dear Sir,

Whereas Power Grid Corporation of India Ltd., with its Registered Office at B-9, Qutab Institutional Area, Katwaria Sarai, New Delhi–110016 (hereinafter referred to be as the ‘’), having invited bids for ______________________  (Name of the package & Specification No.)_____________________________________, in response to which M/s._______________(Name of the Bidder), with its Registered office at _____________________________(Full Address _______________________________) are submitting the bid vide ref_________________ date___________________(hereinafter called the ‘Bid’).

We,__________________(Name of the Agency) with its Registered Office at___________________(Full Address____________________(hereinafter referred to as the ‘Agency’, which expression shall unless repugnant to the context and meaning therefore include its successor, administrator, executor and permitted assigns)do hereby undertake in the event of award of the Contract to execute the pile foundation  work covered under the scope of the Contract, fulfilling all the requirements and construction schedule agreed under the Contract.

Signed on this day of _________20__ at________________

(Signature)___________________

Authorised signatory on behalf of

M/s___________________

(Name)_________________

(Designation)__________________

Note: Separate undertaking to be provided in case of more than one agency proposed.

Annexure-B

PROFORMA OF UNDERTAKING BY THE PROPOSED AGENCY FOR STONE COLUMN

(On Non-Judicial Stamp Paper of appropriate value, wherever applicable)

To,

Power Grid Corporation of India Ltd.

B-9, Qutab Institutional Area

Katwaria Sarai

New Delhi - 110016

Dear Sir,

Whereas Power Grid Corporation of India Ltd., with its Registered Office at B-9, Qutab Institutional Area, Katwaria Sarai, New Delhi–110016 (hereinafter referred to be as the ‘’), having invited bids for ______________________  (Name of the package & Specification No.)_____________________________________, in response to which M/s._______________(Name of the Bidder), with its Registered office at _____________________________(Full Address _______________________________) are submitting the bid vide ref_________________ date___________________(hereinafter called the ‘Bid’).

We,__________________(Name of the Agency) with its Registered Office at___________________(Full Address____________________(hereinafter referred to as the ‘Agency’, which expression shall unless repugnant to the context and meaning therefore include its successor, administrator, executor and permitted assigns)do hereby undertake in the event of award of the Contract to execute the Stone column installation works covered under the scope of the Contract, fulfilling all the requirements and construction schedule agreed under the Contract.

Signed on this day of _________20__ at________________

(Signature)___________________

Authorised signatory on behalf of

M/s___________________

(Name)_________________

(Designation)__________________

Note: Separate undertaking to be provided in case of more than one agency proposed.