| Sl. No | Clause No | Existing clause | Proposed Revision |
| --- | --- | --- | --- |
| 1 | Vol. II Part-A Section-1 Clause 1.6 (oo) | Analytic tools through AI/ML based on reporting data to be implemented for precise and customized information as described in respective section of technical specifications. Some of the tools and dashboard to be developed are summarized below:….. | Replace with Rule Based analytic tools based on reporting data to be implemented for precise and customized information as described in respective section of technical specifications. Some of the tools and dashboard to be developed are summarized below: |
| 2 | Vol. II Part-A Section-1 Clause 1.6 (gg) | Scope of Work | Add after existing para Clause 1.6 (gg) The block diagram of the indicative architecture is shown in Appendix K, Part B. |
| 3 | Vol. II Part-B Section-4 Clause 4.8.3 (l) | 4.8.3 Other Utility Services Usage of AI/ML based analytics will be preferred in coding | Removed |
| 4 | Vol. II Part-C Clause 4.1.4.5 | 4.1.4.5. Fault Signature Analysis The AFAS system shall able to learn the behaviour using AI/ML from the previous incidents and build a database for the type of relay, transmission element and use this information to improve its prediction accuracy. | Replace with The AFAS system shall able to use the previous incidents and build a database for the type of relay, transmission element and use this information to improve its prediction accuracy |
| 5 | Vol. II Part-C Clause 4.1.5 | 4.1.5 Fault Statistics Reporting The system shall have facility to improve the fault distance based on expert system using AI/ML tool and generate a customized report. | Replace with The system shall have facility to improve the fault distance based on previous incidents and generate a customized report. |
| 6 | Vol. II Part-B 1.7.1 of Sec-1 | NTAMC Operation Philosophy | Insert a new Para above Table The RTU/ Gateways shall report independently to the three control centres of NTAMC system (Main NTAMC, Backup NTAMC & ER-RTAMC) simultaneously. There is a Control Center Authority Transfer logic implemented in the RTU/Gateways such that at a time, only one Control Center shall be able to Control the Substation. The corresponding logic at Control Centre shall be implemented by the contractor. Any Control center shall be able to takeover supervisory control authority from the substation gateway after substation is manually put in remote mode from local station. The information regarding which control center is having the control authority shall be known to all the other control centres through the Status of Control Authority Logic bits reporting to SCADA. |
| 7 | Vol. II Part-A 2.1.1.5 of Sec-2 & Appendix-J, Vol. II Part-B | 2.1.1.5. Front End and IEC 60870-5-104 Protocol Course e) Training for operation/functioning of Protocol Analyzer. Schedule C- Third party Software license SI.no (17) - Protocol Analyzer | Removed |
| 8 | Vol. II Part-B 2.4.1 of Sec-2 | 2.4.1 NTAMC SCADA Operator Training Simulator An Operator Training Simulator (OTS) shall be provided for training the operators of NTAMC & RTAMC. The OTS shall be able to simulate the various scenarios encountered by the Operators such as events under normal, emergency, and restoration activities of substation and involving multiple substations/elements within and across regions. Few use cases have been specified later in the specification. The OTS shall be installed at the NTAMC where it will be used to train Employer personnel. | Replaced with 2.4.1 NTAMC SCADA Operator Training Simulator An Operator Training Simulator (OTS) shall be provided for training the operators of NTAMC & RTAMC. The OTS shall be able to simulate the various scenarios encountered by the Operators such as events under normal, emergency, and restoration activities of substation and involving multiple substations/elements within and across regions. Few use cases have been specified as per Appendix-M of Part-B of specification. The OTS shall be installed at the NTAMC where it will be used to train Employer personnel. The specifications mentioned here under are indicative only, however, Bidder has to provide the solution for test cases as per Appendix-M of Part-B or similar. |
| 9 | Vol. II Part-A 4.5 of Sec-4 | 4.5. Hours of Cover and Manpower - One SCADA software engineer round the clock shall always be available at the Main Control centre i.e. 24 X7 hours for all days. - One cybersecurity engineer round the clock shall always be available at the Main Control centre i.e. 24 X7 hours for all days. He shall also be able to handle the networking and hardware maintenance. - One SCADA software/hardware engineer shall be available at each Regional Control centre i.e. 8 office hours (Monday to Saturday). - One engineer of RAS/AFAS shall always be available at Main Control centre i.e. 8 office hours (Monday to Saturday). - One engineer of VMS shall always be available at Main Control centre i.e. 8 office hours (Monday to Saturday). | Replace with 4.5. Hours of Cover and Manpower - One SCADA software engineer round the clock shall always be available at the Main Control centre i.e. 24 X7 hours for all days. - One cybersecurity engineer round the clock shall always be available at the Main Control centre i.e. 24 X7 hours for all days. He shall also be able to handle the networking and hardware maintenance. - One SCADA software/hardware engineer shall be available Regional Control centre (Back up NTAMC & ER-RTAMC) i.e. 8 office hours (Monday to Saturday). - One engineer of RAS/AFAS shall always be available at Main Control centre i.e. 8 office hours (Monday to Saturday). - One engineer of VMS shall always be available at Main Control centre i.e. 8 office hours (Monday to Saturday). - One cybersecurity engineer shall always be available at Back up Control Centre i.e. 8 office hours (Monday to Saturday). The Cybersecurity engineer shall also be able to handle the networking and hardware maintenance. |
| 10 | Vol. II Part-A Clause-4.12 of Section-4. | 4.12. Video Projection system / Video Wall Any dead pixel or LED module defect observed shall be considered under severity level 1. | Replaced with 4.12. Video Projection system / Video Wall Any dead pixel or LED module defect observed shall be considered under severity level 3. |
| 11 | Vol. II Part-B 1.10 of Sec-1 (BOQ) | 1.10. NMS Operational Philosophy | Adding a new line Electric Regional RTAMC(ER-RTAMC)’s NMS system shall be responsible for monitoring all devices of respective client regional RTAMC (CR-RTAMC) |
| 12 | Vol. II Part-B 2.3.1 of Sec-2 Pg. 33 of 52. | The data historian shall be supplied at the Main NTAMC and Backup NTAMC. The configuration shall contain Main-Standby data historian servers at each NTAMC (Main & backup). | Replaced with The data historian shall be supplied at the Main NTAMC and Backup NTAMC. The configuration shall contain Main-Standby data historian servers at each NTAMC (Main & backup). In addition, there shall be a Corporate Data historian in non-redundant configuration at Main NTAMC which shall get data from the Control centre data historians over a secure link following Security guidelines specified in TS. The data of Corporate Historian shall be auto-propagated from Main Data Historian. The Corporate Historian shall have all the features and External data communications Interfaces /Data Exchange protocols as the Main Historian except for the Data Acquisition. The Corporate Historian Shall get data from Main Historian. |
| 13 | Vol. II Part-B 2.3.3(a) of Sec-2 | 2.3.3 Sizing of the Data historian a. The sizing requirement for SCADA and Historian points will be same as per the Appendix-F System Sizing. | Replaced with 12.3.3 Sizing of the Data historian a. The sizing requirement for Historian points shall be as per the Appendix-F System Sizing. |
| 14 | Vol. II Part-B Section-5, Clause 5.2.1 | 5.2.1 Servers/Processors Bidder can shall offer blade servers at Main and backup NTAMC’s and Rack servers at all RTAMC’s to meet the requirement of all servers in consultation with Employer. In general, blade server will be preferred at main and backup NTAMC to cater most of the requirement and high-end rack server swill be preferred at RTAMCs. In case of blade servers, all blades shall be hot swappable, having backplane redundancy and capable to operate on single power supply module. Table: The minimum requirement of some of the blade servers is specified as below: | Replaced with 5.2.1 Servers/Processors Bidder shall offer Rack servers at Main NTAMC, Backup NTAMC and at RTAMCs to meet the requirement of all servers in consultation with Employer. References to Blade servers shall be deleted Table: deleted |
| 15 | Vol. II Part-B Clause 5.13, Section-5. | 5.13. Routers The two Ethernet interfaces for WAN connection shall be suitable for fibre and support 1Gbps or 100Mbps | Removed. |
| 16 | Vol. II Part-B Section-5, Point 5.2.3.1 (s) | All firewalls shall be hardware box firewall with the following requirements Protection against Antivirus, anti-worm, Email security, anti-spam and anti-spyware as applicable | Replaced with Protection such as Antivirus, anti-worm, Email security, anti-spam and anti-spyware as applicable |
| 17 | Vol. II Part-B Section-5, Point 5.2.3.1 (w) | All firewalls shall be hardware box firewall with the following requirements Support assigning of zones to virtual and physical interfaces and assigning of firewall policies between zones, physical interfaces and virtual interfaces | Replaced with All firewalls shall be hardware box firewall with the following requirements Support assigning of zones to virtual and physical interfaces and assigning of firewall policies between zones. |
| 18 | Vol. II Part-B Section-5, Point 5.2.3.2 (f) Point 5.2.3.4 (o) | Additional Features in Type-I External Firewall & Type-III External Firewall Minimum no.of VMs shall be 10. | Replaced with Additional Features in Type-I External Firewall & Type-III External Firewall Minimum no. of VMs shall be 6. |
| 19 | Vol. II Part-B Section-5, Point 5.2.4.1(b) | 5.2.4.1. Network based Intrusion prevention system Logging capabilities – It shall have extensive logging of data related to detected events. This data shall be used to confirm the validity of alerts, to investigate incidents and to correlate events. The logging capabilities shall include – timestamp, Connection or session ID, Rating (priority, severity, and confidence factor), Network/Transport/application layer protocols, Source and destination IP address and ports, No. of bytes transmitted over the connection, state related information etc.) | Replaced with Logging capabilities – It shall have extensive logging of data related to detected events. This data shall be used to confirm the validity of alerts, to investigate incidents and to correlate events. The logging capabilities shall include – timestamp, Connection or session ID, Rating on the basis of severity, Network/Transport/application layer protocols, Source and destination IP address and ports, No. of bytes/packets transmitted over the connection, state related information etc.) |
| 20 | Vol. II Part-B Section-5, Point 5.2.4.1(d) | Prevention Capabilities – The following shall be supported (i) Ending the current TCP session (ii) Altering malicious content (iii) Throttling bandwidth usage (iv) Performing inline firewalling | Replaced Bullet (ii) (ii) Stop malicious content. |
| 21 | Vol. II Part-B Section-5 Point 5.2.4.2 | 5.2.4.2. Host based Intrusion prevention system In an event where user accounts are added, deleted, or modified, changes to key system files and executables are done by unauthorized account or there is an un-authorized attempt to overwrite vital system files, to install Trojan horses or backdoors, suitable action shall be taken such as: - Terminate User (intruder) Login - Disable User (intruder) Account Forge a TCP FIN packet to force intruder connection to terminate | Deleted - Disable User (intruder) Account |
| 22 | Vol. II Part-B 5.2.6 of Sec-5 & Appendix-P Vol. II Part-B | 5.2.6 Security Information and Event Management (SIEM) SIEM shall have support for User and Entity Behaviour Analysis (UEBA) for minimum 50nos Consoles as decided by Employer/Owner. Shall have SOAR features to provision the use external threat intelligence, endpoint security software, and other third-party resources to get a better overall picture of the security landscape inside the network and out. It shall also automate investigation path workflows. | Replaced with SIEM shall have support for various User Behaviour Analysis (UBA). Deleted. |
| 23 | Vol. II Part-B 5.2.6 of Sec-5 & Appendix-P Vol. II Part-B | 5.2.6 Security Information and Event Management (SIEM) The SIEM shall able to integrate with future SOC / SOAR applications procured by Employer. Necessary support for integration shall be provided by Contractor. | Replaced with SIEM shall be integrated with SOAR or another SOC in future and provision of bidirectional message exchange in SYSLOG, CEF and LEEF format shall be provided along with the supplied SIEM system. Necessary support for integration shall be provided by Contractor. |
| 24 | Vol. II Part-B Clause 5.18.1(p) of Sec-5 Pg. 41 of 41 | The panels must have 28.5 dB(A) sound reduction | Deleted. |
| 25 | Vol. II Part-B Appendix-P Point (5) | 5. HIPS (Host based Intrusion Prevention System) (3) Power Supply – Redundant AC Power Supply (11) Power Supply (In watts) (12) Heat Load | 5. HIPS (Host based Intrusion Prevention System) (3) Removed (11) Removed (12) Removed |
| 26 | Vol. II Part-B Appendix-P & Vol. II Part-B Section-5 | HW DRS 15. Routers (Type-1 & Type-2) Sl.no.8. Support NetFlow- Yes Sl.no.14. Operating Temperature 0-45deg 9. Local Area network (LAN) Layer-3 Switch and Device Interface Sl.no.12 Operating Temperature 0-45deg Sl.no.6 Layer-2 Layer 3 features - Support for IEEE …..802.1ad, 802.1p, 802.1q,…… | HW DRS 15. Routers (Type-1 & Type-2) Sl.no.8. Support Netflow / sFlow- Yes Sl.no.14. Operating Temperature 0-40deg 9. Local Area network (LAN) Layer-3 Switch and Device Interface Sl.no.12 Operating Temperature 0-40deg Sl.no.6 Layer-2 Layer 3 features - Support for IEEE …..802.1ad/802.1q, 802.1p, ,…… |
| 27 | Vol. II Part-B Section-9 Clause 9.5.4 | 9.5.4 Security Information and Event management (SIEM) SIEM shall have the features of SOAR (Security Orchestration, Automation & Response) like: - Not only detection of threat but also recommending appropriate response in case of any security incidents. - Usage of variety of advanced detection and investigative controls to detect abnormal activity which is often associated with any compromised systems. - Easy to install, configure, use, and maintain. - Integration with external threat intelligence, user and entity behavior analytics (UEBA) etc. | Removed. |
| 28 | Vol. II Part-B Section-9 Clause 9.5.6 | 9.5.6 End Point Security Whitelisting of applications shall be supported for the proper functioning of NTAMC system. The features shall include: It shall run in all nodes i.e., servers, workstations….. Logs shall be maintained in the endpoint centralized management system for a duration of at least 6-months. | Complete Sub Section Deleted |
| 29 | Vol. II Part-B Appendix-C Pg. 5 of 8 | TABLE 1 – DESIGN PARAMETERS FOR SCADA FUNCTIONS Power Flow Check before Control On demand :10 sec | Deleted |
| 30 | Price Schedule & Appendix-G of Vol. II Part-B | - | Insert a new Line item in BOQ: (H/W) Main NTAMC: 1nos Server for Corporate Historian |
| 31 | Part-A, 1.7 & Price Schedule & Appendix-G of Vol. II Part-B | NMS Operational Philosophy BOQ: (H/W) Main NTAMC & Back up NTAMC: 2nos Servers (S/W) Main NTAMC & Back up NTAMC: 1 Lot each. | Insert a new Line item in BOQ: (H/W) ER-RTAMC: 1nos Servers (S/W) ER-RTAMC: 1 Lot each. |
| 32 | Appendix-F of Vol. II Part-B | - | Insert a New Table Table-3: Typical Point Count for Data Historian (Ultimate): Analog Signals: 250000 Digital Signals: 250000 Selected Analog and Digital points from SCADA Shall be considered to Historian. The Point Count/ Points of Corporate Historian shall be same as Main Data Historian. |
| 33 | Vol. II Part-C Clause 1.1 | 1.1. System Architecture - | Insert a new Para A Separate Auto DR system runs in existing substation computer and transfers DR in COMTRADE format to control centre using SFTP/HTTP protocol in the naming format as defined in Appendix-B of Part-C. RAS server at control centre shall collect this received DR and shall display in the web-portal for user download and simultaneously share to AFAS server for analysis. Provision shall be made for integrating the status of Substation Auto DR system and Relays through Web-API. |
| 34 | Vol. II Part-C Clause 8.3(e) | 8.3. Availability Test The RAS & AFAS system shall demonstrate an availability of 99.95% and under the following conditions: (e) Any failure/problem at the main NTAMC is to be attended immediately, whereas a period of 12 hours (from the time of reporting) shall be provided to attend failure/problem at Backup NTAMC and RTAMCs. This 12hour period shall be considered as hold time and will not be part of the Availability calculation. | Replace with The RAS & AFAS system shall demonstrate an availability of 99.95% and under the following conditions: (e) Any failure/problem at the Main NTAMC, Back up NTAMC & RTAMCs is to be attended immediately. |
| 35 | Vol. II Part-D Appendix-A & Appendix-G, Vol II Part-B & Price Schedule | UPS at 9 RTAMC locations - 40kVA (32 kW at 0.8pf) UPS running in parallel. -18Nos - VRLA type battery banks for above UPS (each bank of 76.8kVAH) – 18Nos Remote monitoring PC with required software – 9no. | Replace with UPS at 5 ER-RTAMC locations - 40kVA (32 kW at 0.8pf) UPS running in parallel. -10 Nos - VRLA type battery banks for above UPS (each bank of 76.8kVAH) – 10 Nos Remote monitoring PC with required software – 5no. UPS at 4 CR-RTAMC locations - 20kVA (16 kW at 0.8pf) UPS running in parallel. - 8 Nos - VRLA type battery banks for above UPS (each bank of 38.4kVAH) – 8 Nos Remote monitoring PC with required software – 4no. |
| 36 | Vol. II Part-E Clause 3.8.3 (n) | - Retrieval: The VMS application shall allow retrieval of data instantaneously or any date and time interval chosen through search functionality of the application software. In case data is older than 15 days and available, the retrieval shall be possible. The system shall also allow for backup and export of specific data on any drives like, NAS, DVD’s or any other device in a format which can be replayed through a standard PC based software like windows media player, etc. Log of any such activity shall be maintained by the system. | Retrieval: The VMS application shall allow retrieval of data instantaneously………………………………… The system shall also allow for backup and export of specific data on any drives like, NAS, DVD’s or any other device in non-proprietary format which can be replayed through a standard PC based software like windows media player, etc. The VMS software shall be capable to compress the video in non-proprietary format while exporting the video. Log of any such activity shall be maintained by the system. |
| 37 | Vol. II Part-E Clause 3.11 | 3.11. Technical Specifications of Network Video Recorder (NVR) (13) GPU- NVIDIA RTX A4000/RTX A5000/ GTX 1080 Ti or Better compatible with VCA of VMS application | Replaced with (13) Graphics Card GPU: 4GB |
| 38 | Vol. II Part-E Clause 4.1.9 | ### Reporting tool: The video content analysis system shall include a reporting tool that shall allow the user to generate interactive reports of event counts presented as tables or charts. The report formats shall include text, PDF and Excel data. It shall include a report scheduler, which will periodically generate event count reports in a format specified by the user. | Insert a new Clause: Alerts shall be generated and sent to the respective user through email/SMS based on criteria customized and user configurable |
| 39 | Vol. II Part-E Clause 4.1.10 & 4.1.11 | 4.Video Content Analysis (VCA) requirements 4.1.10 Smoke and Fire Detection: The video content analysis system shall have the facility to detect Smoke and Fire accurately in the camera field view. Alarms shall be triggered when flames or smoke are detected for the minimum predefined time as set by the user. The delivered feature shall accurately detect the presence of flames, reflected fire light, smoke clouds, and ambient smoke, alerting users in real-time. 4.1.11 Personal protective equipment (PPE) Violation Detector The VCA shall be capable of detecting and tracking the presence of employees/personnel in switchyard without a helmet, person working at height without safety belts and other personal protective measures, depending on the instructions. In case of detecting any “inconsistency abnormality”, the system shall send an alarm to the operator’s screen in the client machine at control center. The VCA shall capable of detecting the following: - Safety helmet detection - Safety vest and harness detection - Gloves and shoe detection | Complete points deleted. |
| 40 | Vol. II Part-E Clause 6.2(b) Pg. 27 of 28 | b) UTILISATION (2) NVR Processor & Memory utilization at each Substation (Less than 30%) | Replaced with (2) NVR Processor & Memory utilization at each Substation for 30 Cameras (Less than 30%) |
| 41 | (Schdule-6) Price Schedule | BUY BACK OF EXISTING HARDWARE AS PER APPENDIX-A OF PART-A SECTION-1 OF TS. – 9 Lot | Replaced with BUY BACK OF EXISTING HARDWARE AS PER APPENDIX-A (SI.no 1-11) OF PART-A SECTION-1 OF TS. – 9 Lot BUY BACK OF UPS AS PER APPENDIX-A OF PART-A SECTION-1 OF TS. – 9 Nos BUY BACK OF UPS VRLA BATTERIES AS PER APPENDIX-A OF PART-A SECTION-1 OF TS. – 9 Lot. |
| 42 | Vol. II Part-B Clause 9.5.4 | SIEM Complete network-based scanning enabling assessment and analysis of threats impacting network. | Removed. |
| 43 | Schedule-QR, Volume-III |  | Schedule-QR has been provided in the Bidding Documents in Volume-III |
| 44 | Price Schedules and Bid Form, Volume-III of the Bidding Documents | Based on the above, the Price Schedule has been revised and is enclosed herewith, which shall replace the previous Price Schedule of the Bidding Documents. Note- Bidders are requested to consider the revised excel sheet(s) titled “Price Schedule_rev01” for bid preparation/submission for the subject package. It may be noted that while submitting the bid(s), bidders are required to change the excel file name to ‘Price_Schedule’. As per the provisions of the portal, it is mandatory to upload excel file with titled ‘Price_Schedule’ (Bidders may refer user manuals at the portal https://etender.powergrid.in regarding submission of bid). |  |
| 45 | 1st Envelope Bid Form and Attachments, Volume-III of the Bidding Documents | The existing excel sheet(s) titled “01_First_Envelope_and_Bid_Forms_NTAMC” for 1st Envelope Bid Form and Attachments as available in Volume-III of the Bidding Documents, stands replaced with file(s) titled “01_First_Envelope_and_Bid_Forms_NTAMC_rev01” and attached herewith. Note- Bidders are requested to consider the revised excel sheet(s) titled “01_First_Envelope_and_Bid_Forms_NTAMC_rev01” for bid preparation/submission for the subject package. It may be noted that while submitting the bid(s), bidders are required to change the excel file name to ‘First Envelope and Bid Forms’. As per the provisions of the portal, it is mandatory to upload excel file with titled ‘First Envelope and Bid Forms’ (Bidders may refer user manuals at the portal https://etender.powergrid.in regarding submission of bid). |  |