| S N | Clause | Provision of Bidding Documents | Bidder’s Query | POWERGRID's Reply |
| --- | --- | --- | --- | --- |
| 1 | Vol. II Part-A Clause 1.3(a) of Sec-1 Pg. 9 of 32 | Rule based expert systems send email/SMS alerts from OT domain to IT domain. Examples are: - Drift in CVT voltages & CT Current. - Blocked relays. - Fault location coordinate & other information. - Alarms | ## We understand that events / alarms reported to control center shall be send via Email / SMS on priority basis. We request PGCIL to confirm our understanding. | Alarms generated form Rule based expert systems like Dashboards shall be send via Email from OT domain to IT domain. POWERGRID will configure the E-mail to send SMS through external Service provider. |
| 2 | Vol. II Part-A Clause 1.3(a) of Sec-1 Pg. 10 of 32 | MPLS based telecommunication link has been established by Employer/Owner at Control Centers as follows: i. 10 Mbps (2Mbps for Data & 8Mbps for Video) connectivity between substations & control centers NTAMC, BNTAMC and respective RTAMC | We understand that 10 Mbps connectivity is provided between substation and each control center i.e NTAMC, BNTAMC and respective RTAMC. Please confirm our understanding. | Confirmed. |
| 3 | Vol. II Part-A Clause 1.4(e) of Sec-1 Pg. 12 of 32 | Dismantling of the existing System. | 1) As POWERGRID is the owner of the existing system including all hardware, software, data, files etc., we request this shall be in the scope of POWERGRID. 2)The bidder shall not be responsible for any data in any form that might be residing/stored in these old systems that needs to be dismantled. Bidder shall not be liable against any data protection, privacy, IP etc. related responsibilities and shall not have any legal/non-legal obligations towards the same. As this part of cyber security for POWERGRID as the owner of the existing system, request POWERGRID to consider the above and confirm. | Bidders shall comply TS. |
| 4 | Vol. II Part-A Clause 1.6(qq) of Sec-1 Pg. 17 of 32 | The Contractor Shall Dismantle the existing NTAMC systems as per Appendix-A of Part-A at control centers (NTAMC, Backup NTAMC & RTAMCs) after successful shifting of operation to the new system being installed under this project. The existing systems after dismantling shall be taken away (buy-back) by the contractor within one month from TOC and this factor shall be taken in to consideration while quoting the price bid. The data stored in the existing systems shall be destroyed by the Contractor as per the technical specification. The new system and existing system shall run in parallel at least 03 months before the dismantling of the system |  |  |
| 5 | Vol. II Part-A Clause 1.6(z) of Sec-1 Pg. 16 of 32 | (z) Supply, Installation and Commissioning of Auxiliary Power System Comprising of UPS with Battery sets and distribution board wherever applicable. | We request PGCIL to confirm if existing UPS at NTAMC, Backup NTAMC and RTAMC can be utilized in case found healthy and extended warranty from the original supplier is available. | Bidder to Comply TS. |
| 6 | Vol. II Part-A Clause 1.6(oo) of Sec-1 Pg. 16 of 32 | Analytic tools through AI/ML based on reporting data to be implemented for precise and customized information as described in respective section of technical specifications. Some of the tools and dashboard to be developed are summarized below: Point: i to viii | The requirement is not clear. Is a separate tool required and also there may not one tool for all the requirements. We request the same shall be deleted. | Dashboards are to be implemented as per TS. Refer Amendment No 1 for AI/ML. |
|  |  |  | We understand that AI/ML capabilities pertaining to use cases mentioned in technical specifications only and no third-party AI/ML system is expected as part of supply and commissioning. We request PGCIL to confirm. |  |
| 7 | Vol. II Part-A Clause 1.6(ww) of Sec-1 Pg. 18 of 32 | System shall be designed to have security level 3 as per IEC 62443-3-3 standard as per appendix-D of Part-A. | The mentioned Appendix D is not available in the tender. Please share the same. | Refer the extract of standard IEC 62443-3-3 attached (Pdf page 99 of 102) of Vol-II Part 1 of 7. These 4 pages shall be referred as Appendix-D. |
| 8 | Vol. II Part-A Clause 1.10.2(bb) of Sec-1 Pg. 26 of 32 | The Contractor and its personnel have to perform the responsibilities as defined in Cyber Crisis Management plan (CCMP) of NTAMC systems. | Request POWERGRID to share the CCMP as the same is not available in the tender. | The Contractor responsibility shall be limited to the scope of works/activities defined in TS. |
| 9 | Vol. II Part-A Clause 1.10.3(d) of Sec-1 Pg. 27 of 32 & Vol. II Part-A Clause 4.2 of Sec-4 Pg. 5 of 25 | The contractor has to ensure with OEM for maintenance and services support for the hardware and software delivered under this project till the completion of AMC period. In case, any hardware / software / equipment /component items of the systems supplied under the contract shall reach its End-of-Life (EOL) or End-of-Support (EOS) whichever is earlier, the contractor shall replace such item with new Hardware or Software without any financial implication to employer. The contractor shall have to submit the documentary evidence certified by OEM for the validity of End-of Life/End-of-Support along with quarterly invoice. & Support in case of End of Life or End of Support | All OEMs have a product refresh cycle of up to a year now and new products are introduced on ongoing basis to keep up with changing technology landscape. While we appreciate PGCIL's intent, this criteria is strenuous and complicating considering the mix of technologies and vendors required at NTAMC. Considering the above, we request to delete this clause as we may not be in position to bid if this remains. As an alternate we suggest following: The contractor has to ensure with OEM for maintenance and services support for the hardware and software delivered under this project till the completion of AMC period. | The Contractor shall replace the EOL and EOS Hardware/software if it has become either non-functional or the patches/updates have been discontinued from the OEM. |
|  |  |  | We understand that End of Life or End of Sale is declared musch earlier but support continues for most of the equipment , request you to remove depencecny on these declaration End of Life or End of Sale will always be earlier than End of Support hence this clause require your review. | Refer above |
| 10 | Vol. II Part-A Clause 1.10.3(h) of Sec-1 Pg. 27 of 32 | 1.10.3 Availability of spares and service support for the system (h)-Irrespective to of commissioning of system in progressive manner, entire the Defect Liability Period (DLP)…. | We understand that contractor libality to ensure uninterrupted service & functional requirement of delivered system shall start only after DLP starts. Kindly confirm | Bidder to comply TS. DLP period is included in AMC. |
| 11 | Vol. II Part-A Clause 1.7.1 of Sec-1 Pg. 19 of 32 | NTAMC Operation Philosophy | The described operation philosophy is not clear and is not in line with the functionalities mentioned in clause 1.7. For Eg: ICCP data is required for only MCC and BCC. Also it is not recommended to have the SCADA & CFE in another location for the main functions of the monitoring and control. Further in the specification the ERTAMCs have only SCADA and no historian, which means the historian is centralized whereas the SCADA is not. Request POWERGRID to relook into the operational philosophy for the Main & Backup centers for NTAMC and Main & Backup RTAMCs operating as independent standalone control centers with data exchange b/w them on ICCP. Other option would be to have the SCADA, Historian etc. centralized at Main NTAMC & Backup NTAMC and the RTAMCs can have only the distributed workstations at their respective independent control center connecting to the NTAMC SCADA. Request POWERGRID to relook into the operational philosophy as above and clarify. | Refer Amendment-1 for data reporting Philosophy. Bidder to Comply TS. |
| 12 | Vol. II Part-A Clause 1.10.3(i) of Sec-1 Pg. 28 of 32 | POWERGRID reserves the right to upgrade/replace Hardware/ Software, Vendor needs to provide services/support required to do the upgrade during the AMC period. | The bidder scope for this requirement is not clear. Request POWERGRID to explain the same. | POWERGRID may upgrade/replace Hardware/software to have additional features/functions, which is not originally envisaged in the Scope of Work, at its own cost. Bidder’s scope includes providing services/support in delivered system for integration/interfacing such hardware/software. |
|  |  |  | Equivalent compensation as agreed mutually shall be paid to contractor against the said upgrade/ replacement if the same is not mandatory to fulfil SLA obligations of AMC. Please confirm. |  |
| 13 | Vol. II Part-A Clause 1.13.5 of Sec-1 Pg. 31 of 32 | Technical requirements for VMS The manufacturer whose Visual Monitoring System (VMS) is being offered should have experience in the design, supply, Integration, testing and commissioning of at least two numbers of VMS systems completed within last seven (7) years and at least one such system shall be under successful operation for at least one (1) year as on the date of NOA. One of the VMS system shall have been installed at multi-site location with at least two level of hierarchy and have at least 500 cameras | Does the VMS experience in Metro (Transportation) projects domain having multiple stations consider as multisite project, as it also has two level of hierarchy at station level and at OCC (Operation Control Room) and Back up at BCC (Back up control room). | Bidder to Comply TS. |
| 14 | Vol. II Part-A Clause-1.13.6 of Sec-1 Pg. 32 of 32 | 1.13.6 Technical requirements for RAS The manufacturer whose Remote Accessibility System (RAS) is being offered should have experience in the design, supply, Integration, testing and commissioning of at least two numbers of RAS systems completed within last seven (7) years and at least one such system shall be under successful operation for at least one (1) year as on the date of NOA. One of the RAS system shall have been installed at multi-site location with at least 10 nos. of Substations and with at least 500 nos. of Relay | Request you to kindly amend the clause as below: The manufacturer whose Remote Accessibility System (RAS) is being offered should have experience in the design, supply, Integration, testing and commissioning of at least two numbers of RAS systems completed within last Two (2) years and at least one such system shall be under successful operation for at least one (1) year as on the date of NOA. One of the RAS system shall have been installed at multi-site location with at least 10 nos. of Substations and with at least 500 nos. of Relay | Bidder to comply TS. |
| 15 | Vol. II Part-A Clause 2.1.1.5 of Sec-2 Pg. 7 of 12 | 2.1.1.5. Front End and IEC 60870-5-104 Protocol Course: e) Training for operation/functioning of Protocol Analyzer. | We understand that protocol analyzer is not part of supply. Hence we request PGCIL to remove training on protocol analyzer from the training scope. | Refer Amendment no-1 |
| 16 | Vol. II Part-A Clause 3.7.3 of Sec-3 Pg. 15 of 18 | Software Design | Mentioned Software Design for documentation purpose should not be applicable for COTS (Commercially Off the shelf available) software. | Bidder to comply TS. This is applicable for all Software applications. |
| 17 | Vol. II Part-A Clause 4.2 of Sec-4 Pg. 5 of 25 | Support in case of End of Life or End of Support: The contractor has to ensure with OEM for maintenance and services support for the hardware and software delivered under this project till the completion of AMC period. In case, any hardware / software / equipment /component items of the systems supplied under the contract shall reach its End-of-Life (EOL) or End-of-Support (EOS) whichever is earlier, the contractor shall replace such item with new Hardware or/and Software without any financial implication to employer. | - Contractor proposes to continue service support of End-of-Life product with help from third party supplier in case OEM support is not available. We request PGCIL to confirm acceptance. - We request PGCIL to list out the equipment for which this clause will apply. Kindly exclude Printers, Furniture, Workstation Monitor, passive equipment like cables, racks, aux supply peripheries and perpetual software. | The Contractor shall replace the EOL and EOS Hardware/software if it has become either non-functional or the patches/updates have been discontinued from the OEM. |
|  |  |  | It's very difficult to estimate the EOL of any component / hardware / software and therefore estimate the costing. In order to overcome such situation Siemens proposes two options. OPTION 1: Any hardware / component reaching EOL, Siemens will intimate Power grid well in advance and Power grid can procure the hardware/component either directly or via Siemens that will be finalized via mutual discussion. Any additional efforts for integrating the new hardware / component with SCADA system will be in scope of Siemens. Regarding the software upgrade, basically two types of components are offered in this embedded solution. Few licenses are subscription based and with a valid subscription Siemens can adopt any upgrade of the product. For such component Siemens will maintain subscription during the complete Life Cycle of the project. Embedded component like RHEL, JBOSS, Oracle etc. will be part of this component and any version upgrade is offered free of cost. However, some components are license based and requires purchasing of additional licenses in case of version upgrade. If any point of time during any system update/upgrade it is required purchasing of additional licenses, then that will be informed to Powergrid and Powergrid will purchase those licenses either directly or via Siemens that will be decided via mutual discussion at the time of such need. Components like Windows OS, NMS, SIEM etc. comes under this category. Powergrid needs to support Siemens by providing necessary software/hardware to maintain the regular updates/upgrades of the system which is very essential from Cyber Security point of view. Also, with this strategy system will always be closer to the latest version of all components and therefore no limitation in Lifecycle duration. OPTION 2: Powergrid should modify this clause and include that after 3 years (maximum 4 years) of Operational Acceptance, Contractor should replace all the hardware / software / component etc. used in this delivered solution, and therefore, all the contractors cancompile the costing properly. | Refer above |
| 18 | Vol. II Part-A Clause 4.4 of Sec-4 Pg. 6 of 25 | Preventive Maintenance (PM) Activity | Tender asks to restore all database and all image backups as part of Preventive Maintenance activity. We request PGCIL to remove this requirement since the overall size of system is considerable and this requires dedicated manpower resource at each control center specifically for this activity along with provision of Offline Backup tools in Price Schedule(other than online backup tool) and Spare hardwares with exact same configuration. Hence we request PGCIL to remove the requirement for restoration of all backups and images. | Bidder to comply TS. |
| 19 | Vol. II Part-A Clause 4.5 of Sec-4 Pg. 6 of 25 | 4.5. Hours of Cover and Manpower | We request PGCIL to clarify the manpower requirement at client RTAMC. We also request PGCIL to consider General Shift deployment of manpower at control center instead of round the clock. | - No manpower envisaged at Client RTAMCs. - Bidder to comply T.S. Also, Refer Amendment No 1 |
| 20 | Vol. II Part-A Clause 4.5 of Sec-4 Pg. 6 of 25 | These engineers must have the experience of working in the relevant field for at least 3 years out of which one-year experience should be on the delivered system. | We request PGCIL to confirm 1. One Year Experience on delivered system should be preference not mandatory. 2. Non-Availability of Man-power should not be treated as Severity level- 2 outage. | Bidder to Comply TS. |
|  |  |  | We request PGCIL to specify if Backup Control Center Man power requirement is same as Master Control Center. | Refer Amendment no-1 |
| 21 | Vol. II Part-A Clause 4.5(b) of Sec-4 Pg. 7 of 25 | BYOD Policy The Contractor and its personnel have to follow all rules and regulations of owner’s office premises such as BYOD policy, PTW procedures etc. and other compliance to owner’s certifications of ISO-9001, ISO-14001, 45001/OHSAS- 18001 and ISO 27001 including any other future guidelines/rules issued by Organization or any guidelines issued by Govt agencies. | Any other future guidelines/rules is an open ended clause and this can not be ensured as this stage. Therefore, we request Powergrid to change this clause as contractor should comply with all the guidelines/rules applicable for SCADA system at the time of handover. However, contractor has to evaluate any future guidelines/rules to be implemented in accordance with the employer. In case, any additional appliance or third -party hardware or third-party software is required for implementing the guidelines/rules of the Authority, the same shall be provided by the Employer (Same as Vol II, Section-4.9 - Cyber Security Audit). | Bidder to Comply TS. |
|  |  |  | We request to include the Four Management Consoles at NTAMC, 2 Management console at RTAMC and 2 laptops at each control center in BoQ. If not, it is understood that all these devices will be treated as returnable property of contractor and hence contractor is free to choose the specification as per their requirement since the device falls under Bring Your Own Device (BYOD). Please Confirm. | These maintenance consoles and Laptops are part of the BOQ. |
| 22 | Vol. II Part-A Clause 4.10 of Sec-4 Pg. 11 of 25 | 4.10. Patch Management and Mitigation Measures “Anti-Virus/Firewall Signatures Daily” Non-deployment of patch within the stipulated time above shall be treated as Severity Level-2 | We request PGCIL to exclude non- working day for manual updating activities | Bidder to Comply TS. |
| 23 | Vol. II Part-A Clause 4.14 of Sec-4 Pg. 14 of 25 | Table – 4-2 Mandatory Spares inventory at Control centers Mandatory Spares inventory at Control centers | 1No mandatory spare is required in each NTAMC, Backup NTAMC, ER-RTAMC and CR-RTAMC as mentioned in table- 4.2, We request PGCIL to confirm. | Bidder to Comply TS. |
| 24 | Vol. II Part-A Clause 4.15.2 of Sec-4 Pg. 17 of 25 | 4.15.2 Integration of Relays/IEDs with RAS/AFAS Integration of Relays/SDC/DR/IEDs with RAS/AFAS - 15 days | Please provide relaxation on the timeline to 40 days | Bidder to Comply TS. |
| 25 | Vol. II Part-A Clause 4.15.3 of Sec-4 Pg. 17 of 25 | 4.15.3 Integration of NVR/Cameras with Visual Monitoring system The Cameras (fixed and/or PTZ IP camera), Server with operating system for NVR shall be procured along with the substation by the Employer. The SDK/API of the cameras for integration with supplied VMS shall be provided by the Contractor without any financial implications. | SDK/API of cameras to be provided by camera supplier. VMS OEM/contractor cannot be held responsible for the availability of SD/API from camera supplier end. | SDK/API shall be provided by Contractor of Substation package period for new camera integration. |
| 26 | Vol. II Part-A Sec-4 4.3 Pg. 5/25 4.4 Pg. 6/25 4.5 Pg. 7/25 4.8 Pg. 9/25 4.9 Pg. 10/25 4.10 Pg. 11/25 4.13 Pg. 13/25 4.15.3 Pg. 18/25 | - | There are multiple clauses which specify Severity-2 level breach, eg. - Manpower unavailability - Preventive maintenance steps - Report for Monitoring Activity - New report format creation - UPS maintenance report and it's implementation - EoL and EoSL report unavailability every quarter The stated clause is not affecting the system performance and availability, contractor requests PGCIL to consider these clauses under severity 3 level breach. | Bidder to Comply TS. |
| 27 | Vol. II Part-A Appendix-A Pg. 1 of 1 | LIST OF DEVICES FOR BUYBACK | We understand buyback does not entail issuing any scrap certificates or any other statutory certificates, if the buyback hardware is not discarded but repurposed/ reutilized elsewhere by any vendor for other uses. Please confirm. | Bidder to Comply TS. |
| 28 | Vol. II Part-B Clause 1.3.2 of Sec-1 Pg. 5 of 11 | The required configuration of ICCP (both conventional and secure) between main control centre and other control centres shall be demonstrated during Technical | The other control centers will not be connected during the FAT as the same will conducted in Bidder's factory, checking the ICCP during FAT may not be possible. Request POWERGRID to clarify. | Bidder shall demonstrate the ICCP communication on dummy setup between Main NTAMC and Backup NTAMC during Factory Acceptance test. |
| 29 | Vol. II Part-B Clause 1.4 of Sec-1 Pg. 6 of 11 | Many of the SAS substations have IP addressing which may be overlapping as these were designed for local communication. The Remote accessibility of the relays in these substations shall require changes in the IP address for unique addressability such as NAT (Network Address Translation) in the firewall. | All activities related to the substations shall be in POWERGRID's scope. Please confirm | Confirmed. However, “Items at Substations”, mentioned in BoQ shall be part of Contractor’s scope under this project. |
| 30 | Vol. II Part-B Clause 1.5 of Sec-1 Pg. 6 of 11 | These users shall have the access to same display as that of the SCADA system but shall not be allowed to change any data or do supervisory controls. | We understand the displays mentioned here are the report and trend displays that needs to be made accessible to the external users. Please confirm. | Refer clause 1.5 and 1.5.1. All SCADA displays including Alarm/events, Trends and Reports shall be made available to external users. |
| 31 | Vol. II Part-B Clause 1.6 of Sec-1 Pg. 7 of 11 | Email System | Need a detailed specification for Email System with architecture. | Bidder to Comply TS. |
| 32 | Vol. II Part-B Clause 1.10 of Sec-1 Pg. 10 of 11 | 1.10. NMS Operational Philosophy | We understand that Network Management System is required to be installed at Main and Backup control center and shall monitor all hardware / equipment installed at Main Control Center, back up control center, electric regional control center and client regional control center. Considering count of equipment installed at these control center NMS at MCC & BCC need to monitor huge no of devices which may burden the system. Instead we propose to have NMS at MCC, BCC and Electric Regional CC to monitor equipment at respective control center. Electric Regional control center NMS system will monitor equipment installed at respective client regional control centers well. We request PGCIL to confirm | Refer Amendment-1 |
| 33 | Vol. II Part-B Clause 2.2.4.1 of Sec-2 Pg. 13 of 52 | 2.2.4.1. Analog Data Processing It shall include at a minimum the following conversion function: ii. Two- or three-degree polynomial calculation or linear interpretation | Please elaborate requirement with some use case of required calculations. | Bidder to Comply TS. |
| 34 | Vol. II Part-B Clause 2.2.5.5 of Sec-2 Pg. 23 of 52 | 2.2.5.5. ISR Data Processing The ISR system shall also support program like visual basic for complex calculations. | Along with Visual Basic. Please confirm that industry standard language such as C, C++,C#.net, Python, Perl, etc programming for scripting can be used to meet this requirement. | Confirmed. |
| 35 | Vol. II Part-B Clause 2.2.5.7 of Sec-2 Pg. 24 of 52 | 2.2.5.7 ISR User interface (UI) The user shall be able to view and edit the stored data on displays and reports | This point is not clear. Should the report be editable? Please confirm | Confirmed. However, the changes done in the report shall be available in logs for Audit purpose. |
| 36 | Vol. II Part-B Clause 2.2.5.9 of Sec-2 Pg. 26 of 52 | 2.2.5.9. Reports The user shall be able to examine and modify the contents of reports for the current period and for previous report periods using displays. | This point is not clear. Should the report be editable? Please confirm | Confirmed. However, the changes done in the report shall be available in logs for Audit purpose. |
| 37 | Vol. II Part-B Clause 2.2.6 of Sec-2 Pg. 26 of 52 | 2.2.6 Network Status Processor This topology and the associated model parameters shall be based on: (3) Manually entered in-service or out-of-service designations for bus oriented model elements (e.g., branches) where switches are not represented. | Please elaborate requirement with some use case. | The Topology modelling shall be done in such a way with provision for manually changing of status from in-service or out-of-service where equipment like CB, Isolators are not telemetered. |
| 38 | Vol. II Part-B Clause 2.3.2(c) of Sec-2 Pg. 34 of 52 | 2.3.2 Features required with the Data Historian It shall have interfaces compatible with DAS (1.0a and 2.0) compliant servers, SQL, ODBC, OLEDB, Modbus, ASCII, and text. | We understand that DAS is nothing but Data Acquisition System. Please confirm | Refers to Data Access Protocols. |
| 39 | Vol. II Part-B Clause 2.3.2(d) of Sec-2 Pg. 35 of 52 | 2.3.2 Features required with the Data Historian d) Alarms and Events The data historian shall have generic data access and template-driven capabilities of the modeling engine so that users can redeploy alarm parameters to similar assets across the Enterprise without requiring to go to each and every point. | Data Historian receives Alarm & Events data from SCADA. Please confirm if this is part of SCADA or Data Historian. | Data Historian shall it’s have Alarms & Events processing capabilities as per TS. |
| 40 | Vol. II Part-B Clause 2.3.2(K) of Sec-2 Pg. 37 of 52 | k) Condition Monitoring Applications. k1) Comparison k2) Pattern matching | The requirement is not clear as these are taken care in SCADA functions like trending, alarms/events etc. Please elaborate. | These features are additionally required in the Data Historian software for historical & Real Time data Analysis. |
| 41 | Vol. II Part-B Section-2 Point 2.3.3(a) Pg. 37 of 52 | Sizing of the Data historian The sizing requirement for SCADA and Historian points will be same as per the Appendix-F System Sizing. | Please specify the number of data tags for data historian. | Refer Amendment No 1. |
| 42 | Vol. II Part-B Clause 2.3.5 of Sec-2 Pg. 38 of 52 | Previous experience requirement The data historian application & size to be offered under this project shall be operational in production environment at similar entities for at least One (1) year. In addition, recommendation letters/work orders/Letter of Award or other relevant supporting documents from at least Three customers shall be provided, of which, at least One should be from a Transmission utility or System operator. | While the offered historian shall be sized with 100% tag expansion, we understand the project references to be used to fulfil this criteria can be with actual tag capacity approximately in line with present system (without expansion). Please confirm. | Refer Amendment No 1. Bidder to Comply TS. |
|  |  |  | In reference to this clause, we understand that COTS based historians experience certificate is required to be submitted. Please clarify | Confirmed. |
| 43 | Vol. II Part-B Clause 2.4.1, 2.4.3, 2.4.4, 2.4.5 of Sec-2 Pg. 39 of 52 | 2.4.1 NTAMC SCADA Operator Training Simulator 2.4.3 OTS as a Test Bench 2.4.4 Integration of New RTU 2.4.5 Integration of new control Centre on ICCP/Proprietary protocol | As there the scope of NTAMC is only SCADA and no EMS functions are included, the power system network model, simulator load modelling, network simulation etc. are not applicable and possible without building the EMS network model. Hence, for only SCADA OTS is not applicable and request the same to be removed. Instead a training RTU can be included and the operators can get trained on the SCADA software including execution of commands on the training RTU. As part of SCADA function, it’s possible to include a RTU in "Test Mode" which will be treated separately without disturbing the realtime operations. As these are not specific to OTS and part of the SCADA function itself, these can be removed. The "Test Mode" mentioned above is applicable for ICCP transfer as well and hence can be removed. | The requirements here are Indicative only. The Bidder has to offer the solution to meet the requirement of Test Cases mentioned in TS. Refer Amendment No 1. |
| 44 | Vol. II Part-B Clause 3.6.2 of Sec-3 Pg. 16 of 28 | Alarm Priority levels Each alarm shall be assigned to an alarm priority level. Up to 8 alarm priority levels shall be supported. | We understand Alarm levels defined in the section 3.6.2 Alarm priority level shall be considered. Please confirm. | The alarm priority levels shall be 10. Refer 3.6.2 & Appendix-C, Vol-II, Part-B. |
| 45 | Vol. II Part-B Clause 4.1 of Sec-4 Pg. 3 of 21 | 4.1 Software Standards In areas where these organizations have not yet set standards, the software shall comply with those widely accepted de- facto standards put forth by industry consortiums, such as OSF and X/Open. The Contractor shall commit to meet the "open systems" objective promoted by industry standards groups. The software shall adhere to Software Development Life Cycle (SDLC) and IEC 62443-4 standard. | Is this applicable for Data Historian platform? Please confirm | Confirmed. |
| 46 | Vol. II Part-B Clause 4.7 of Sec-4 Pg. 16 of 21 | Inventory Management Software CVE ID, CVE/CVSS related points within TS for Inventory management software | CVE identification is feature of VA tools, hence CVE/CVSS related points may be excluded. Please confirm. | As per Clause, Identification feature not required but suitbale provision for maintaining CVE… records for all software. |
|  |  | Process for maintaining the records for Architectural changes, cyber Security policy modification, configuration changes etc. | Please remove this clause as this is not feature of Inventory management. | Bidder to comply T.S |
| 47 | Vol. II Part-B Clause 4.7 of Sec-4 Pg. 16 of 21 | Software: - Process for maintaining the records for Name of software and its components, Version Control System (version installed, date on which version upgraded), date on which update installed, CVE ID along with CVSS base, temporal and environmental scores, Software integrity check using checksum/hash (SHA 256) of All software including Application Software, Inventory etc | We request to delete sub-points 4, 5, & 6 as this is restricting competition. | Bidder to comply TS |
| 48 | Vol. II Part-B Clause 5.2.1 of Sec-5 Pg. 6 of 41 | 5.2.1 Servers/Processors Bidder can shall offer blade servers at Main and backup NTAMC’s and Rack servers at all RTAMC’s to meet the requirement of all servers in consultation with Employer | Considering the following points: 1) Different zone in system architecture 2) Shared resources among various servers 3) Single point of failure can affect availability of multiple and critical application. 4) Sharing of resources can degrade the performance of the application. It is recommended to use standard enterprise server instead of Blade servers. | Refer Amendment-1. |
| 49 | Vol. II Part-B Clause 5.2.1 of Sec-5 Pg. 6 of 41 | Servers/Processors: The Servers shall have provision for expansion of the Processor, auxiliary memory and main memory (RAM) by 100% of the delivered capacity | Request for Changes: The Servers shall have provision for expansion of the auxiliary memory and main memory (RAM) by 100% of the delivered capacity Justification: As per Industry Std. only | The model proposed shall support expansion either by addition or by Upgrading. |
|  |  |  | Change Required: The Servers shall have provision for expansion of the Processor, auxiliary memory and main memory (RAM) by 100% of the delivered capacity…...This expandability shall be possible at site with addition of plug-in modules only without changing the existing components such as processor, memory. Justification/Clarification: We understand to meet expansion of processor, memory bidder can not replace processor, memory offered on day 1. Kindly confirm. | Refer Above. |
| 50 | Vol. II Part-B Clause 5.2.1 of Sec-5 Pg. 6 of 41 | 5.2.1 Servers/Processors: Bidder can shall offer blade servers at Main and backup NTAMC’s and Rack servers at all RTAMC’s to meet the requirement of all servers in consultation with Employer. In general, blade server will be preferred at main and backup NTAMC to cater most of the requirement and high-end rack server swill be preferred at RTAMCs. | Change Required: Bidder shall have option to quote either blade servers or Rack servers at Main and backup NTAMC’s and rack server at all RTAMC’s to meet the requirement of all servers in consultation with Employer. In general, blade server will be preferred at main and backup NTAMC to cater most of the requirement and high-end rack server will be preferred at RTAMCs Justification/Clarification: As it is mentioned blade server is preferred for main and backup site, we understand that Blade servers or rack servers can be offered for Main and backup site. Kindly confirm. | Refer Amendment-1.. |
|  |  | In case of blade servers, all blades shall be hot swappable, having backplane redundancy and capable to operate on single power supply module. | Blade chassis have many power supply like 4 or 6 and operate on N+N configuration and can sustain failure of half of the power supply. |  |
| 51 | Vol. II Part-B Clause 5.2.1(4) of Sec-5 Pg. 6 of 41 | 5.2.1 Servers/Processors: 4) Flash drive shall be preferred over hard disk for OS installation | Change Required: 4) Flash drive shall be preferred over hard disk for OS installation Justification/Clarification: As it is mentioned flash drive is preferred for OS disk, we understand that spinning hard disk can not be offered for OS installation. Kindly confirm. | SSD type disk is Envisaged for OS Installation as per TS. |
| 52 | Vol. II Part-B Clause 5.2.1 of Sec-5 Pg. 7 of 41 | Blade Chassis: Chassis should support simultaneous housing of Ethernet FC, SAS, iSCSI, IB interconnect fabrics, offering hot pluggable & redundancy as feature | Change Required: Chassis should support simultaneous housing of Ethernet FC, SAS, iSCSI, IB interconnect fabrics, offering hot pluggable & redundancy as feature. Justification/Clarification: IB switches are not available in the Blade Architecture, So requesting to Remove the same. | Refer Amendment-1 |
| 53 | Vol. II Part-B Clause 5.2.1 of Sec-5 Pg. 7 of 41 | Blade Chassis: Enclosure should have at least 8 (eight) interconnect bays | Change Required: Enclosure should have at least 6 (Six) interconnect bays Justification/Clarification: 8 Interconnect Bays are not Industry standard, max 6 interconnect bays are available as Industry standard. | Refer Amendment-1 |
| 54 | Vol. II Part-B Clause 5.2.1 of Sec-5 Pg. 7 of 41 | Blade Chassis: There should be at least two number of blade Ethernet switches each having 14/16 nos. of 1/10Gbps downlink ports and 6x1/10Gbps uplink ports and 2x10/100 Gigabit uplinks FC ports along with SFP modules per switch. | Change Required: There should be at least two number of blade Converged switches each having 8/12 nos. of 25Gbps downlink ports and 6x 100 Gbps uplink ports and 3 Ports Populated with 40G/4x10G cable per switch and 3 Ports Populated with 100G/4x 32G FC Uplink Ports for SAN connectivity. Justification/Clarification: 1G/10G are not available in the latest Blade Switches. For all new deployments LAN fabric is becoming standardized at 25 Gbps and SAN fabric at 32 Gbps. Looking at long term plan of PGCIL request to go with prevailing technology standard. | Refer Amendment-1 |
| 55 | Vol. II Part-B Clause 5.2.1 of Sec-5 Pg. 7 of 41 | Blade Chassis: There should be at least two number of (redundant) enabled blade SAN switches each having 20/24 ports (10/40Gbps auto negotiation) which shall connect to uplink external storage / switch and downlink to internal servers | Change Required: It should support at least two number of (redundant) enabled blade SAN switches which shall connect to uplink external storage / switch and downlink to internal servers. Justification/Clarification: Request to please modify the clause as Converge Switches are providing both Ethernet & FC connectivity as per latest industry trends and in future PGCIL can add SAN Switches for higher bandwidth | Refer Amendment-1 |
| 56 | Vol. II Part-B Clause 5.2.1 of Sec-5 Pg. 8 of 41 | Blade Server: It should have minimum two nos. of x86 64-bit family minimum 2.30GHz or higher | Change Required: It should have minimum two nos. of x86 64-bit family minimum 2.20GHz or higher Justification/Clarification: Looking at currently available processors request to modify clock speed to 2.2 GHz | Refer Amendment-1 |
| 57 | Vol. II Part-B Clause 5.2.1 of Sec-5 Pg. 8 of 41 | Blade Server: Server should have OEM chipset or x86 64-bit family C621A chipset or higher | Change Required: Server should have OEM chipset or x86 64-bit family C621 chipset or higher Justification/Clarification: Each OEM uses different sub series of chipset hence request to modify the clause. | Refer Amendment-1 |
| 58 | Vol. II Part-B Clause 5.2.1 of Sec-5 Pg. 8 of 41 | Blade Server: Server should have minimum 250GB DDR4-3200MHz RAM | Change Required: Server should have minimum 256GB DDR4-2933MHz RAM Justification/Clarification: Request to change bandwidth so that bidder can choose either 2P or 4P blade servers | Refer Amendment-1 |
| 59 | Vol. II Part-B Clause 5.2.1 of Sec-5 Pg. 8 of 41 | Blade Server: Storage should be of SSD type with minimum capacity of 2TB each with minimum warranty of 5 years. It should be allowed to configure the total harddisks in RAID-6 or better configuration to protect minimum double disk failure | Change Required: Storage should be of SSD type with 2x 1.9TB with minimum warranty of 5 years. It should be allowed to configure the total hard disks in RAID-1 or better configuration. Justification/Clarification: As the SSD in the Blade Server is for the Boot purpose only, as the Data will be in SAN Storage, So 2 Drives in RAID 1 is Recommended and that is the Industry Standard available solution. | Refer Amendment-1 |
| 60 | Vol. II Part-B Clause 5.2.1 of Sec-5 Pg. 9 of 41 | Blade Server: Blade should have dual port 8Gbps Fibre Channel HBA | Change Required: Blade should support dual port 16 Gbps Fibre Channel HBA using PCI slots Justification/Clarification: Now Converge Ports are Industry Standard and used to make flexible Network and bandwidth can be share between Network & SAN traffice and can be distributed as per requirment. | Refer Amendment-1 |
| 61 | Vol. II Part-B Clause 5.2.1 of Sec-5 Pg. 9 of 41 | Blade Server: It should have 2x 1 Gb network ports | Change Required: It should have Converge Network Adaptor with 2 x 50Gb Ports or 4 x 25Gb Ports to give both Network & FCoE SAN bandwidth. Justification/Clarification: Asked Specs are not aligned with latest generation application and hardware. Now Converge Ports are Industry Standard and used to make flexible Network bandwidth that can be share between Network & SAN traffice and can be distributed as per requirment. | Refer Amendment-1 |
| 62 | Vol. II Part-B Clause 5.2.1 of Sec-5 Pg. 9 of 41 | Blade Server: INDUSTRY STANDARD COMPLIANCE It should have ACPI 2.06.3 It should have USB 2.0 and 3.0 Support It should have IMPI 2.0 It should have secure Digital 2.0 It should have TMP 1.2 Support It should have Latest TLS and above It should have PCIE 34.0 ISO 14001-2004, ISO 9001-2008 | Change Required: INDUSTRY STANDARD COMPLIANCE It should have ACPI 2.06.3 or higher It should have USB 3.0 Support It should have IPMI 2.0 It should have secure Digital 2.0 It should have TPM 1.2 Support It should have Latest TLS and above It should have PCI E 3.0 ISO 14001-2004, ISO 9001-2008 Justification/Clarification: Request to modify as per the latest available industry standards | Refer Amendment-1 |
| 63 | Vol. II Part-B Clause 5.2.3.1(a) of Sec-5 Pg. 11 of 41 | Both Internal and External firewall shall have redundant power supplies. | We understand that power supply required on Internal & External firewall should be Internal Hot Swappable so that power supply failure can be rectified without impacting the firewall operation. Kindly confirm. | The firewall operations should not be impacted in case of failure of any one of the redundant power supply. Also, there shall not be any interruptions in data flow while changing the failed power supply. |
| 64 | Vol. II Part-B Clause 5.2.3.1(c) of Sec-5 Pg. 11 of 41 | All firewalls shall be hardware box firewall with the following requirements. Support Active-Active/Active-Standby mode | We suggest that both Active-Active and Active-Standby mode operations should be supported on firewall for supporting different use case scenarios. Kindly amend the clause as below - Support Active-Active and Active-Standby mode | Bidder to comply TS |
| 65 | Vol. II Part-B Clause 5.2.3.1(h) of Sec-5 Pg. 12 of 41 | All firewalls shall be hardware box firewall with the following requirements: Support IPv6 features like NAT66, NAT64, NAT46/IPv4 over IPv6. | Type-I and Type-III firewall are external firewalls which are supposed to handle DNS traffic also. Hence we recommend to consider IPv6 feature of DNS64 in order to handle DNS communication between IPv4 and IPv6. Kindly amend the clause as below - Support IPv6 features like NAT66, NAT64, NAT46/IPv4 over IPv6, DNS64 | Bidder to comply TS |
| 66 | Vol. II Part-B Clause 5.2.3.1(l) of Sec-5 Pg. 12 of 41 | All firewalls shall be hardware box firewall with the following requirements Host-access control to permit access from limited hosts | "The clause to be deleted". Justification: - The requested specification is related to Host level firewall and may cover under Endpoint Security solution. This section is related to Network firewall hence remove this clause or do clarify if host/endpoint security is also expected from NGFW vendor? and confirm the number of lines for host/endpoint security to be provided by NGFW vendor with Proposed NGFW firewalls. Moreover this specifications is not available in part 4 of Vol ll. | The Firewall shall permit its access from specified hosts (systems) over the network. Access to all other hosts shall be denied. |
|  |  |  | Host based control is in the purview of Endpoint Detection and Response software and not related to network firewall. Hence please delete this from Firewall specifications. |  |
| 67 | Vol. II Part-B Clause 5.2.3.1(w) of Sec-5 Pg. 12 of 41 | All firewalls shall be hardware box firewall with the following requirements Support assigning of zones to virtual and physical interfaces and assigning of firewall policies between zones, physical interfaces and virtual interfaces | "Support assigning of zones to virtual and physical interfaces and assigning of firewall policies between zones" Justification:- Restricted clause for Participation:- The designing of firewall policies must be done based on Zones however physical or virtual interface based policy designing is giving unnecessary advantage to specific OEM and restricting leader OEM to participate hence request you to please neutralize this requirement. | Refer Amendment-1 |
|  |  |  | Please amend this specification with following language: "Support assigning of zones to virtual and physical interfaces and assigning of firewall policies between zones" |  |
| 68 | Vol. II Part-B Clause 5.2.3.1(hh) of Sec-5 Pg. 13 of 41 | All firewalls shall be hardware box firewall with the following requirements. Common Criteria Certification for minimum EAL4+ level | ICSA and Common Criteria Certification for minimum EAL4+ level Justification: - The ICSA certification is one of the known certification to test the NGFW features and performances. This is the third party certification standard and followed by all Leader OEM of NGFW and in addition to that EAL4+ certification provide the security assurance of engineering and source code of product itself hence incorporate the certification requirement in combination of both the certificate to ensure that product meets the security requirement of SDLC (Firewall Code) as well as Product features are also tested and recognized by industry known third party programs. | Bidder to comply TS. |
| 69 | Vol. II Part B Clause 5.2.3.5.3 of Sec-5 Pg. 17 of 41 | Firewall Features for NTAMC & RTAMC(Minimum Requirements): Minimum IPSec VPN Peers = 10000 | IPSec VPN Peers criteria determine the no. of peers one box can terminate VPN connections. This criteria is not applicable for Internal Firewall, hence we request to remove this criteria from Internal Firewall specifications. | Minimum IPsec VPN peers 10000 are mentioned for External Firewall Only. The Internal Firewall shall also support IPSec VPN feature. However, It Shall not be Configured for this purpose. |
| 70 | Vol. II Part-B Clause 5.2.3.2 of Sec-5 Pg. 14 of 41 | Additional Features in Type-I External Firewall Additional 1no. Hardware Based (purpose-built appliance) shall be provided along with 1 pair of Firewall of same OEM at Main NTAMC & Back up NTAMC for a) Anti-APT (Advanced Persistent Threat) | The clause mentions Anti-APT (advanced persistent threat) solution from Firewall OEM. This prohibits vendor participation other than Firewall vendors. Request you to modify the clause as below:- " 1 pair Hardware Based (purpose-built appliance) shall be provided at Main NTAMC & Back up NTAMC for Anti-APT (Advanced Persistent Threat)" | Bidder to comply TS. |
| 71 | Vol. II Part-B Clause 5.2.3.2(f) of Sec-5 Pg. 14 of 41 | Additional Features in Type-I External Firewall Minimum no.of VMs shall be 10. | "Minimum no.of VMs shall be 8" Justification: - (Restricted clause) The Number of VM requested are not aligned with the required throughput of File processing. The Sandboxing throughput is driven from the Number of unique file analysis by the Anti-APT device hence requesting you to please remove this clause as mention the minimum number of VM to enable the Leader OEM participation. | Refer Amendment-1 |
| 72 | Vol. II Part-B Clause 5.2.3.2(i) of Sec-5 Pg. 14 of 41 | Additional Features in Type-I External Firewall Shall integrate with other OEM Firewalls to perform various activities mentioned in Sr.no 5.2.3.2 a, b & c. | The clause mentions to integrate OEM Firewall to integrate with Sandbox Solution. This specification gives an additional advantage to firewall OEM's. Request you to make this clause loosely coupled for maximum Anti-APT vendor participation and modify as below:- "(i) Shall integrate with other leading OEM Firewalls like Checkpoint, Palo Alto to perform various activities mentioned in Sr.no 5.2.3.2 a, b & c." | Bidder to comply TS. |
|  |  |  | Requesting to remove this point - Considering every Firewall OEM will work with native OEM only for the features mentioned in this clause. |  |
| 73 | Vol. II Part-B Clause 5.2.3.2(h) of Sec-5 Pg. 14 of 41 | Additional Features in Type-I External Firewall Shall also support Mail attachment/ Mail Inspection/Mail integration. | Email attachment inspection is a part of email security solution and emails don't traverse through a Firewall, hence requesting to remove this point. | Bidder to comply TS. |
| 74 | Vol. II Part-B Clause 5.2.3.4(o) of Sec-5 Pg. 15 of 41 & Vol. II Part-B Appendix-P Pg. 6 of 27 | Additional Features in Type-3 External Firewall Minimum no.of VMs shall be 10. & a. Additional features in Control Centre Firewalls (f) Minimum no.of VMs shall be 10. | "Minimum no.of VMs shall be 8" Justification: - (Restricted clause) The Number of VM requested are not aligned with the required throughput of File processing. The Sandboxing throughput is driven from the Number of unique file analysis by the Anti-APT device hence requesting you to please remove this clause as mention the minimum number of VM to enable the Leader OEM participation. | Refer Amendment-1 |
| 75 | Vol. II Part-B Clause 5.2.3.4(r) of Sec-5 Pg. 15 of 41 | Additional Features in Type-3 External Firewall (r) Shall integrate with other OEM Firewalls to perform various activities mentioned in Sr.no 5.2.3.2 a, b & c. | The clause mentions to integrate OEM Firewall to integrate with Sandbox Solution. This specification gives an additional advantage to firewall OEM's.Request you to make this clause loosely coupled for maximum Anti-APT vendor participation and modify as below:- "(r) Shall integrate with other leading OEM Firewalls like Checkpoint, Palo Alto to perform various activities mentioned in Sr.no 5.2.3.2 a, b & c." | Bidder to comply TS. |
|  |  |  | Requesting to remove this point - Considering every Firewall OEM will work with native OEM only for the features mentioned in this clause. |  |
| 76 | Vol. II Part-B Clause 5.2.3.4(j) of Sec-5 Pg. 15 of 41 | Additional Features in Type-3 External Firewall Anti-APT (Advanced Persistent Threat) | The clause mentions Anti-APT (advanced persistent threat) solution from Firewall OEM. This prohibits vendor participation other than Firewall vendors. Request you to modify the clause as below:- " 1 pair Hardware Based (purpose-built appliance) shall be provided at Main NTAMC & Back up NTAMC for Anti-APT (Advanced Persistent Threat)" | Bidder to comply TS. |
| 77 | Vol. II Part-B Clause 5.2.3.4(q) of Sec-5 Pg. 15 of 41 | Additional Features in Type-3 External Firewall Shall also support Mail attachment/ Mail Inspection/Mail integration. | Email attachment inspection is a part of email security solution and emails don't traverse through a Firewall, hence requesting to remove this point. | Bidder to comply TS. |
| 78 | Vol. II Part-B Clause 5.2.3.5.3 of Sec-5 Pg. 17 of 41 & Vol. II Part-B Appendix-P Pg. 7 of 27 | Table-1: Firewall features for RTAMC and NTAMC (Minimum requirements) Sr.no 5 Minimum Threat Prevention Throughput with Firewall, AVC, IPS, VPN, gateway Antivirus with logging operational & Sr.no 5 Minimum Threat Prevention Throughput with Firewall, AVC, IPS,VPN, gateway Antivirus with logging operational | 5. Minimum Threat Prevention Throughput with Firewall, AVC, IPS, VPN, gateway Antivirus, Anti-bot, Anti-Spam, DNS Security with logging operational: - NTAMC/BNTAMC: - Type 1: (4 GB), Type 2: (4 GB), Type 3: (4 GB) ER-RTAMC: - Type 1: (4 GB), Type 2: (4 GB) CR-RTAMC: - 1. Gbps Justifications: - The requested number of ports at NTAMC/BNTAMC & ER-RTAMC are 14 x 10 = 140 Gbps. However, requested throughput is around 12.5 Gbps with 100%. This is on very lower end and may create bottleneck in network. On the other hand, Threat Prevention common blades are (Firewall + IPS + Application + Anti-Virus + DNS Security + Anti bot + Zero Day Protection with logging enabled) hence section to be clearly defined as Threat Prevention throughput requirements (without any additional features in specific firewall type else this may contradict with security requirement in RFP) including all features must be available on public Datasheet/websites. Another reason to remove features in specific firewall type throughput section is, Type 3 firewall require to be integrated with Anti-APT devices which means Firewall must have Threat Prevention blades enabled to process the file towards the Anti-PT device. | Bidder to comply TS. |
| 79 | Vol. II Part-B Clause 5.2.3.5.3 of Sec-5 Pg. 17 of 41 & Vol. II Part-B Appendix-P Pg. 8 of 27 | Table-1: Firewall features for RTAMC and NTAMC (Minimum requirements) Sr.no 8b Minimum number of 1Gbps SFP based CU Ethernet ports (For CR-RTAMCs)-10 | Minimum number of 1Gbps SFP ports (For CRRTAMCs) - 8 copper Ports and 4 x 1 SFP ports Justifications: - Need clarity as the requested ports are SFP based CU Ethernet, the requirement is only for Copper Ethernet ports or Fiber ports? If the Fiber only then The number of requested Fiber ports may require very higher model to be quoted and may impact the overall budgeting of the firewall hence requesting you to incorporate the changes to quote the right sized and budgetary appliance. | 10SFP based CU ports are envisaged. |
| 80 | Vol. II Part-B Clause 5.2.2 of Sec-5 Pg. 10 of 41 | Archive & Configuration server …The frequency of image back up shall be monthly twice automatically with incremental back up. The backup shall be stored on SAN (Storage Area Network). It shall keep minimum two (02) set of image backup of all servers and selected workstations. The SAN shall have sufficient array of disks to meet the requirement of two (02) image backup of all the servers in RAID-6 configuration… | (1) We recommend full image backup biweekly/bimonthly for servers in place of incremental backup as it is intensively taxing on system resources. Pls confirm. (2) Please exclude workstations from backup as it is not critical, and storage infrastructure proposed as part of TS is not adequate to handle all workstations. Pls confirm | 1) Bidder to comply TS. 2)Selected workstations One(1) of each type of Function/System envisaged which shall be finalized as per detail engineering. At ER-RTAMCs, NAS Shall be used for Image back up. |
| 81 | Vol. II Part-B Clause 5.2.3.1(s) of Sec-5 Pg. 12 of 41 | All firewalls shall be hardware box firewall with the following requirements.: Protection against Antivirus, anti-worm, Email security, anti-spam and anti-spyware as applicable | Protection against malware based attacks like viruses, worms, ransomware, C&C etc. | Refer Amendment No 1 |
| 82 | Vol. II Part-B Clause 5.2.3.1(ii) of Sec-5 Pg. 13 of 41 | All firewalls shall be hardware box firewall with the following requirements: Data Loss Prevention | Firewall shouldn't drop any packets while inspecting a malware or a traffic, hence please remove this clause. | Bidder to comply TS. |
| 83 | Vol. II Part-B Clause 5.2.4.1 of Sec-5 Pg. 20 of 41 | NIPS installed in line with external Type-I firewall shall be of different make than the one from external Type-I, Type-II & Type-III firewall. | The clause asks for different make of NIPS used in Type-I firewall then the one from external Type-I, Type-II & Type-III firewall. Having different make of NIPS within the Infrastructure will increase the complexity of management & will work in Siloes without sharing IOC,Threat Intel among themselves. Request you to modify the clause as " NIPS installed in line with external Type-I, Type-II & Type-III firewall shall be of same make & must share IOC, Threat Intelligence among themselves " | Bidder to comply TS. |
| 84 | Vol. II Part-B Clause 5.2.4.1(b) of Sec-5 Pg. 20 of 41 | The NIPS shall have logging capabilities: It shall have extensive logging of data related to detected events. This data shall be used to confirm the validity of alerts, to investigate incidents and to correlate events. The logging capabilities shall include – timestamp, Connection or session ID, Rating (priority, severity, and confidence factor), Network/Transport/application layer protocols, Source and destination IP address and ports, No. of bytes transmitted over the connection, state related information etc.) | The clause asks for Logging capabilities w.r.t. rating on priority & confidence factor which is very subjective and couldn’t be shown on the portal. Also logging w.r.t. no of bytes transmitted over the connection is depicted in no of packets. Request you to modify the clause as " Logging capabilities – It shall have extensive logging of data related to detected events. This data shall be used to confirm the validity of alerts, to investigate incidents and to correlate events. The logging capabilities shall include – timestamp, Connection or session ID, Rating on the basis of severity, Network/Transport/application layer protocols, Source and destination IP address and ports, No. of bytes/packets transmitted over the connection, state related information etc.)" | Refer Amendment-1 |
| 85 | Vol. II Part-B Clause 5.2.4.1(d) of Sec-5 Pg. 20 of 41 | Prevention Capabilities – The following shall be supported (i) Ending the current TCP session (ii) Altering malicious content (iii) Throttling bandwidth usage (iv) Performing inline firewalling | The clause asks to Alter the malicious content as a preventive capability. But NIPS does deep packet inspection & can stop the malicious traffic. Altering of malicious content is not a function NIPS. Request you to modify the clause as below:- "Prevention Capabilities:- Stop malicious content/traffic" | Refer Amendment-1 |
| 86 | Vol. II Part-B Clause 5.2.4.2 of Sec-5 Pg. 21 of 41 | The Host-based Intrusion Prevention System shall be of different make as compared to NIPS. | The clause asks for different make of HIPS & NIPS. HIPS & NIPS from same OEM will help ensure achieving connected threat defense approach & mitigating vulnerabilities both at network and server in a robust manner. Request clarification if different make of HIPS & NIPS means from separate OEM solution. If yes, Request to delete the clause for maximum vendor participation. | Bidder to comply TS. |
| 87 | Vol. II Part-B Clause 5.2.4.2 of Sec-5 Pg. 21 of 41 | In an event where user accounts are added, deleted, or modified, changes to key system files and executables are done by unauthorized account or there is an un-authorized attempt to overwrite vital system files, to install Trojan horses or backdoors, suitable action shall be taken such as: - Terminate User (intruder) Login - Disable User (intruder) Account - Forge a TCP FIN packet to force intruder connection to terminate | The clause asks to Terminate User (Intruder Login), Disable User (Intruder Account) in case of unauthorized attempt to change the files. The action expected to be taken here is not a HIPS function. The role of HIPS in the scenario becomes to prevent malicious activity & intrusion attempts. Terminate User & Disable User is administrative action, generally done by domain controller. Therefore, request you to modify the clause as "In an event where user accounts are added, deleted, or modified, changes to key system files and executables are done by unauthorized account or there is an un authorized attempt to overwrite vital system files, to install Trojan horses or backdoors, suitable action must be taken such as: - Terminate/Stop User Intrusion attempt - Forge a TCP FIN packet to force intruder connection to terminate" | Refer Amendment-1 |
| 88 | Vol. II Part-B Clause 5.2.6 of Sec-5 Pg. 23 of 41 | SIEM The solution shall provide tool for developing collection and parsing capabilities for any unsupported or unknown IP applications and the OEM shall integrate this with the SIEM application. | Typically, SI develops custom parser during implementation of SIEM. Please change this requirement from OEM to bidder. | Bidder to comply TS |
| 89 | Vol. II Part-B Clause 5.5 of Sec-5 Pg. 28 of 41 | Last Para …. In general, number of SFP/SFP+ for fibre optic and Cu Ethernet type has been given in the BOQ for indicative purpose. Number of SFP/SFP+ shall be finalized during detailed Engineering. The minimum hardware configuration of shall be as per Appendix-P of Part-B. | 1.0 Please clarify how many 1G and 10G, CU and FO optics fiber required. 2.0 Please also clarify weather need single or multimode fiber | 1.0 As per Detail Engineering. 2.0 Multimode for Local LAN Connectivity & Single mode for MPLS connectivity in the Routers. |
|  |  |  | We understand, 1. "Copper SFP for LAN" is 1G transceiver. 2. "Fiber Optic for LAN" is 10G transceiver. 3. We do not foresee the requirement of 1G transceivers for NTAMC Main & Backup and ER-RTAMC, since the networks shall be on 10G FO. Hence same may be removed. | Bidder to comply TS. |
| 90 | Vol. II Part-B Clause 5.13 of Sec-5 Pg. 37 of 41 | Routers: The two Ethernet interfaces for WAN connection shall be suitable for fibre and support 1Gbps or 100Mbps | We are assuming in Interface ports (Type-2) router we need 4 CU and 2 Fibre port as mention in clause | Refer Amendment-1 |
| 91 | Vol. II Part-B Clause 5.13 of Sec-5 Pg. 38 of 41 | 15. Routers (Type-1 & Type-2): Support Net Flow | Change Required: Request to change the clause as " Support NetFlow or sFlow" Justification/Clarification: Reason: HPE proposed router support sFlow. sFlow is a multi-vendor, packet sampling technology used to monitor network devices including routers, switches, host devices and wireless access points. | Refer Amendment-1 |
| 92 | Vol. II Part-B Clause 5.13 of Sec-5 Pg. 38 of 41 | 5.13 Routers: For normal operation, router shall use all channels between two location and in the event of any channel failures, traffic shall be re-routed to the remaining healthy channels with an attempt to generally balance the load. | Change Required: Request to change the clause as "For normal operation, router shall use all channels/links between two location and in the event of any channel/links failures, traffic shall be re-routed to the remaining healthy channels/links with an attempt to generally balance the load." Justification/Clarification: Reason: Here understanding of channel is service provider link only. | Channel / Link refer to multiple connections between the two locations over the WAN. |
| 93 | Vol. II Part-B Clause 5.5 of Sec-5 Pg. 27 of 41 | 5.5 Local Area network (LAN) Layer-3 Switch and Device Interface==> under Layer-2 and Layer-3 features required: Support for IEEE 802.1d, 802.1w, 802.1s, 802.1ad, 802.1p, 802.1q, 802.1ab | Change Required: Request to change the clause as " Support for IEEE 802.1d, 802.1w, 802.1s, 802.1p, 802.1ad or 802.1q, 802.1ab" Justification/Clarification: Reason: Request to relax on the 802.1ad for clause no. 5a mentioned switches(Interface ports (For Main NTAMC, Back up NTAMC and ER-RTAMC)). HPE proposed switch support 802.1q for vlan tagging. | Refer Amendment-1 |
| 94 | Vol. II Part-B Appendix-P | 9. Local Area network (LAN) Layer-3 Switch and Device Interface==> Operating temperature: 0° to 45° C | Change Required: Request to change the clause as " 0° to 40° C" Justification/Clarification: Reason: Since technology and architecture differs from OEM to OEM. this is standard temperature tolerance range for data center switches, hence request to change the operating temperature to 0° to 40° C . | Refer Amendment-1 |
| 95 | Vol. II Part-B Clause 5.15.1 of Sec-5 Pg. 38 of 41 | Workstation/Server desk Adjustable (Height) Desks (sit-and-stand with step-less automatic height adjustment) | Specifications of Furniture are not matching with Appendix -I Document. Clause No. 5.15 specs are asked with Height Adjustable Desks whereas Appendix -I asks for Normal Semi-Circular desk, request you to check and confirm what needs to be considered. | Adjustable (Height) Desks are envisaged. Bidder to comply TS. |
|  |  | Workstation/Server desk | We understand Height adjustable desk is not required and Appendix-1 shall supersede in case of any ambiguities when compared with Section 5. Please confirm. | Required. Bidder to comply TS for Section 5.15 & Appendix-I |
| 96 | Vol. II Part-B Clause 5.18.1(a) of Sec-5 Pg. 40 of 41 | Enclosures (except for server racks) shall confirm to IP31 degree of protection. All the louvers shall be provided with suitable wire mesh. | Please remove IP31 for IT racks since it is not recommended for IT racks and it does not allow for adequate cooling and system performance. | Bidder to comply TS. |
| 97 | Vol. II Part-B Clause 5.18.1(p) of Sec-5 Pg. 41 of 41 | Panels The panels must have 28.5 dB(A) sound reduction | Not valid point for IT Racks as they are open to circulate the air | Refer Amendment-1 |
| 98 | Vol. II Part-B Clause 8.2 of Sec-8 Pg. 3 of 11 | Connection with other telephone Systems : The VoIP (example: configured in H.323) shall also be connected to the other VoIP system (example: SIP) through standard protocol such as SIP as well as H.323. The VoIP system shall support call exchange with a different VoIP system. | Kindly confirm exact requirement. The VoIP set which is working on H.323 cannot be configured with SIP at same time. However, if requirement is to network two systems over SIP protocol is possible. So Any VoIP set confirmed with H3.323 can call to another system user over SIP trunking between two systems. Please confirm if our understanding is clear. | Bidder to comply TS. Some Handsets shall be configured on SIP and Some are on H.323. |
| 99 | Vol. II Part-B Clause 8.10 of Sec-8 Pg. 8 of 11 | VOIP System performance and sizing The VoIP system shall be designed to cater about 800 IP telephones. | Please confirm total number of user license required from day one & expandability of user in future. Do we require 800 IP users license from day one? | Confirmed. |
| 100 | Vol. II Part-B Clause 8.11.1 of Sec-8 Pg. 8 of 11 | VOIP System Factory Acceptance Test The factory acceptance test shall comprise of functional tests on all the components of the VoIP system to demonstrate the features defined in the Technical specification. The actual condition shall be simulated to the extent possible in the factory environment. The system shall be then integrated at site and then tested for its full functionality. | We understood that we have to do an FAT before delivering system/material at project specific sites. The FAT will be done at certified partners placed in India and same is acceptable by PGCIL, please confirm. | Confirmed. |
| 101 | Vol. II Part-B Clause 9.5.1 of Sec-9 Pg. 14 of 20 | Firewall shall be able to receive threat intelligence feeds from time to time to detect threats and prevent attacks. | We understand that Firewall must be able to ingest threat intelligence from OEM and third party sources on industry standard STIX/TAXII format. Kindly confirm | Confirmed. |
| 102 | Vol. II Part-B Clause 9.5.3(a) of Sec-9 Pg. 15 of 20 | The NIPS shall provide complete inline protection from network-based application layer threats by scanning packet payloads for malicious traffic. It shall detect, classify and stop malicious application, viruses, worms and spyware/adware etc. The NIPS shall be tightly integrated /in-built with the firewall | The clause mentions for NIPS to have tight integration with Firewall. This specification gives an additional advantage to firewall OEM's having NIPS functionality . Request you to make this clause loosely coupled for maximum Standalone NIPS vendor participation and modify as below:- "The NIPS shall allow integration with the firewall OEM's" | Bidder to Comply TS. |
| 103 | Vol. II Part-B Clause 9.5.4 of Sec-9 Pg. 15 of 20 | SIEM Complete network-based scanning enabling assessment and analysis of threats impacting network. | Network scanning is not a feature of SIEM and require 3rd party vulnerability solution, it is thus requested to kindly remove the following point | Refer Amendment-1 |
| 104 | Vol. II Part-B Clause 9.5.4 of Sec-9 Pg. 16 of 20 | SIEM solution shall be able to integrate with all security solutions provided including Firewall, Server security and Endpoint security solutions through standard protocols. The solution shall be able to not only detect threat but also shall be able to recommend appropriate response. | Please share the list of devices which are planned to be integrated. | All IT assets as per BoQ including substation items of BoQ. |
| 105 | Vol. II Part-B Clause 9.5.4 of Sec-9 Pg. 16 of 20 | Security logs should be generated at application level, in addition to Operating System / network layer, for interfacing with SIEM. The application security logs shall comply with IEC 62351-14 standard requirements. | Not applicable to SIEM. SIEM can collect the application logs but application need to generate the logs. | SIEM shall be able collect the logs as per as per IEC 62351-14. |
| 106 | Vol. II Part-B Clause 9.5.4 of Sec-9 Pg. 16 of 20 | SIEM shall have the features of SOAR (Security Orchestration, Automation & Response) like: - Not only detection of threat but also recommending appropriate response in case of any security incidents. - Usage of variety of advanced detection and investigative controls to detect abnormal activity which is often associated with any compromised systems. - Easy to install, configure, use, and maintain. - Integration with external threat intelligence, user and entity behaviour analytics (UEBA) etc | Not all OEMs provide inbuilt SOAR along with SIEM. Hence we request you to generalize this clause as suggested below to allow better participation - - Proposed Solution shall have the features of SOAR (Security Orchestration, Automation & Response) like: - Not only detection of threat but also recommending appropriate response in case of any security incidents. - Usage of variety of advanced detection and investigative controls to detect abnormal activity which is often associated with any compromised systems. - Easy to install, configure, use, and maintain. - Integration with external threat intelligence, user and entity behaviour analytics (UEBA) etc. | Refer Amendment-1 |
| 107 | Vol. II Part-B Clause 9.5.4 of Sec-9 Pg. 16 of 20 | SIEM shall have the features of SOAR (Security Orchestration, Automation & Response) like: | SIEM & SOAR are 2 separate product | Refer Amendment-1 |
| 108 | Vol. II Part-B Clause 9.5.6 of Sec-9 Pg. 18 of 20 | It shall have facility to enable control on USB ports for disabling unauthorized usages. Its functional specifications shall be as follows: - It shall block USB devices based on device identity, port identity, device type (e.g., allowing all keyboards, etc.) | The clause asks to Block USB devices on the basis of Port identity apart from device ID, Serial ID. The feature asked here favors a specific vendor only. Request you to modify the clause for maximum vendor participation as "It shall block USB devices based on device identity/port identity/device type (e.g., allowing all keyboards, etc.)" | Port Identity refer to Physical ports of respective System. |
| 109 | Vol. II Part-B Clause 9.5.6 of Sec-9 Pg. 18 of 20 | End Point Security: It shall be capable to provide baseline configuration of systems on which it is installed | The clause asks endpoint security solution to provide baseline configuration of the system. We provide OS version, MAC address, host name, IP Address, username etc. as baseline configuration. Request to provide clarification whether some other details are also expected from the ask. | Bidder to comply TS. |
| 110 | Vol. II Part-B Clause 9.5.6 of Sec-9 Pg. 18 of 20 | End Point Security: It shall be capable to identify the list of installed security and application patches | The clause asks for list of installed security & application patches. The functionality can be achieved with patch management software. Request to delete this clause. | Bidder to comply TS. |
| 111 | Vol. II Part-B Clause 9.5.6 of Sec-9 Pg. 19 of 20 | Whitelisting of applications shall be supported for the proper functioning of NTAMC system. The features shall include: - It shall run in all nodes i.e., servers, workstations. - It shall be able to discover applications running in the network | The clause asks for list of installed applications on all nodes. The functionality can be achieved with asset management software. Request to delete this clause. | Refer Amendment-1 |
| 112 | Vol. II Part-B Appendix B Pg. 23 of 23 | Display design and development shall be in line with latest BIS standard | The referred BIS standard is not available in the tender documents. Please share the same. | As prevail during Detailed Engineering. |
| 113 | Vol. II Part-B Appendix-C Pg. 5 of 8 | TABLE 1 – DESIGN PARAMETERS FOR SCADA FUNCTIONS Power Flow Check before Control On demand :10 sec | We understand that none of the transmission network application including Power flow is required over here and hence this requirement is not applicable over here. Please confirm our understanding. | Refer Amendment-1 |
| 114 | Vol. II Part-B Appendix-F Pg. 2 of 2 | Appendix F Typical point count for ICCP Data Exchange (Initial sizes) DATABASE SIZING – ICCP Point Count- with 200% as final count. Analog-35000 Status - 110000 | Please specify the current and ultimate number of tags for which the COTS based data historian system is to be designed for. | Refer Amendment-1 for Data Historian point Count. |
| 115 | Vol. II Part-B Appendix-G Pg. 2 of 16 | Appendix-G BOQ FOR SUPPLY FOR UPGRADATION OF NTAMC SYSTEM. 13.DIRECT VIEW VIDEO WALL | We understand that total 6 nos 17 meter square video wall will be required in NTAMC, total 1 No 17 meter square will be required in Backup NTAMC and total 1 No each of 17 meter square will be required in 5 No's ER-RTAMC and 6 No's CR-RTAMC. Please confirm our understanding. | Confirmed. |
|  |  |  | Also in NTAMC specify configuration of video wall if there will be one controller for all 6 video wall or separate 6 no of controllers required for each video wall, We request PGCIL to confirm | Separate controller for each Video wall. |
| 116 | Vol. II Part-B Appendix-G Pg. 1 of 16 | Appendix-G BOQ FOR SUPPLY FOR UPGRADATION OF NTAMC SYSTEM. Sr no Item description UNIT Total ER RTAMC Qty 4.4 FRONT END SERVER EA 22 | As per BoQ there are 22 no of FEPs required in total 5 no of ER-RTAMC. Please provide distribution of 22 FEPs in each ER-RTAMC. We request PGCIL to confirm if 22 no of FEPs required at NTAMC & Back up NTAMC. | The FEPs of CR-RTAMCs is envisaged at respective ER-RTAMC. Two (2) FEP for each region (Total- 11 region) is envisaged at Main and Back up NTAMC. |
| 117 | Vol. II Part-B Appendix-G Pg. 1 of 16 | Appendix-G BOQ FOR SUPPLY FOR UPGRADATION OF NTAMC SYSTEM. 4.17 SIEMCORRELATIONENGINE | As per BOQ, SIEM Correlation engine is include only in NTAMC & Backup NTAMC. Also syslog server is included in NTAMC, Back up NTAMC and each ER-RTAMC. We understand that syslog servers at NTAMC & Back up NTAMC collects data from all ER-RTAMC syslog server and send them to SIEM Correlation engine at NTAMC & Back up NTAMC for further analysis. We request PGCIL to confirm our understanding. | Please refer Part-B, Clause 5.2.6 of Technical Specifications. |
| 118 | Vol. II Part-B Appendix-G Pg. 3 of 16 | Appendix-G BOQ FOR SUPPLY FOR UPGRADATION OF NTAMC SYSTEM. 15.1.7 REMOTE MONITORING PC WITH REQUIRED SOFTWARE | We understand that this remote PC will be only limited to Auxiliary supply monitoring software. We request PGCIL to confirm. | Please refer Part-D, Clause 2.5 of Technical Specifications. |
| 119 | Vol. II Part-B Appendix-G Pg. 4 of 16 | Appendix-G BOQ FOR SUPPLY FOR UPGRADATION OF NTAMC SYSTEM. ll SOFTWARE FOR CONTROL CENTRE 1.5 SOFTWARE FOR HOSTING CUSTOM APPLICATION | We request PGCIL to specify functionality expected by this software. | Please refer Part-B, Clause 4.8.3 (l) of Technical Specifications. |
| 120 | Vol. II Part-B Appendix-G Pg. 4 of 16 | Appendix-G BOQ FOR SUPPLY FOR UPGRADATION OF NTAMC SYSTEM. 5.1 WEB AND SECURITY HIDS APPLICATION SOFTWARE | In BOQ, WEB AND SECURITY HIDS APPLICATION SOFTWARE is mentioned We request PGCIL to confirm on what all servers this software is expected to be installed. | Envisaged for all Servers. |
| 121 | Vol. II Part-B Appendix-P Pg. 12 of 27 | 5. HIPS (Host based Intrusion Prevention System) | In software specification, there are some points related to hardware specification such as power supply, heat load. We request PGCIL to confirm whether HIPS hardware is to be supplied. | Refer Amendment-1 |
| 122 | Vol. II Part-B Appendix-G Pg. 1 of 16 | Appendix-G BOQ FOR SUPPLY FOR UPGRADATION OF NTAMC SYSTEM. 4.13 HIDS Server | As per BoQ, 2 quantity of HIDS Server required at NTAMC & Back up NTAMC. We request PGCIL to specify purpose of this server and what all functionalities / software expected to install on this server. | Centralized HIDS Server is envisaged for HIDS/HIPS Software, EDR & Antivirus applications. |
| 123 | Vol. II, Part-B Appendix-I Pg. 1 of 1 | 1.0 Workstation desk Each workstation shall be provided with a suitable desk as follows: - The Desk shall be arranged in a semi-circular shape. - Sectional frame suitably clad with hardwood or hard-wearing material. | Points of clarification required: The Control Desk shall conform to high standard of engineering as mentioned in the document; meeting the specified codes, standards and designs. It shall be capable of performing 24X7 operations under the specified environmental condition in compliance to control room ergonomic norms i.e. ISO 11064. All the certificates and reports mentioned below and in BOQ shall be submitted along with the technical bid. Structure shall be made of heavy-duty extruded vertical and horizontal aluminium profiles. The extrusions shall be duly powder coated with 40+ microns over all surfaces. All sheet metal parts shall be finished with a durable, black, electrostatic powder coating. OEM shall have a valid trademark registration certificate issued by the Government of India for the Control Desk proposed in this tender. Valid Trademark registration certificate to be submitted along with the technical bid. | Bidder to comply TS. Same shall be finalized during detailed engineering. |
| 124 | Vol. II, Part-B Appendix-I Pg. 1 of 1 | - Desktops of a durable, scratch resistant, non-reflecting finish of suitable thickness. | Points of clarification required: The material of the working surface shall be minimum 25 mm thick MDF with High-Pressure laminate. The proposed Control Desk’s life cycle should be assessed (from approved LCA consultant) for environmental impacts associated with all the stages of a product's life for cradle to grave analysis. Valid report/document from UL/Intertek to be submitted along with the technical bid. | Bidder to comply TS. Same shall be finalized during detailed engineering. |
| 125 | Vol. II, Part-B Appendix-I Pg. 1 of 1 | -Adequate space shall be provided on the desktop for writing area, to accommodate the operator workstation, mouse, telephone console/instruments and other miscellaneous items. | Points of clarification required: The front edge of consoles is the component which comes in frequent contact of the operator. The soft polyurethane edge is meant to prevent injury (accidental impact) to operator during emergency and it also reduces the contact stress. In case of damage to this edge the desk design shall permit quick & easy replacement within half an hour without taking any shutdowns or removal of the tabletops. Audit certified design feature of modular PU Edge: High-density poly-urethane foam moulded on industrial grade aluminum core to form 50mm deep tapered edge to be installed on worktop. In case of damage or wear, the edge shall be mechanically replaceable within 30 minutes without opening or removing the worktop. Valid UL audit certificate to be submitted along with the technical bid. Extruded PU edging/PVC T-beading shall be deemed unacceptable. Slat wall shall be made of approximately 2mm thick extruded aluminium (aluminium alloy). The proposed Control Desk shall be UL Listed and valid certificate to be submitted along with the technical bid. | Bidder to Comply TS. |
| 126 | Vol. II, Part-B Appendix-I Pg. 1 of 1 | -Drawers, shelves and miscellaneous fittings. | Points of clarification required: Front, and back shutters shall be of 18 mm Laminated MDF Board with premium finish. Side leg shall be of 25mm of the same finish. | Bidder to Comply TS. |
| 127 | Vol. II, Part-B Appendix-I Pg. 1 of 1 | - Support for Monitors shall be provided on the desk. Sufficient space shall be available so that Monitors shall be adjustable for tilt and angle by the operator. | Points of clarification required: The Console shall feature ergonomic display mounting arms. It shall enable quick & easy replacement of VESA mounts & arm extensions as per the ergonomic. UL audit certified design feature of monitor arm assembly shall have auto lock, push & remove feature for quick release of VESA mounts and modular arm extensions for ease in maintenance and fixing of monitor by one technician within 30 seconds without using any tools. Valid UL audit certificates to be submitted along with the technical bid. The proposed control desk shall be ANSI/BIFMA e3-2019 certified/tested at least for level 3 from UL/Intertek as per Furniture Sustainability Standard to identify the sustainability level of the furniture with respect to the environmental, health & wellness, and social impacts applicable to product(s). Valid certificate to be submitted along with the technical bid. | Bidder to Comply TS. |
| 128 | Vol. II, Part-B Appendix-I Pg. 1 of 1 | - Space for keeping the CPU of the workstation shall be available in the shelves. Power distribution units and Cables shall be neatly secured and accessible | Points of clarification required: The Console shall be designed with vertical and horizontal cable trays to allow for continuous cable management between the cabinets. Wire shall be routed into the cabinet through gland plate. The proposed console shall be RoHS Certified/tested from UL/Intertek. | Bidder to Comply TS. |
| 129 | Vol. II, Part-B Appendix-I Pg. 1 of 1 | - Access shall be allowed for maintenance to equipment mounted on or in the desk. Doors or removable panels shall be provided for this purpose. | Points of clarification required: To allow future extension and expansion, a weld-free system shall be proposed. Interconnecting joints shall not be visible. The structure shall be rigid enough to withstand BIFMA X5.5 tests. OEM shall have had BIFMA X5.5 certificate for at least six years prior to April 1st, 2022. The structure shall allow easy assembly of hinged shutters, slat wall, gland plate, and monitor arms in extremely rigid manner. Valid certificate of BIFMA X5.5 from authorized agencies to be submitted along with technical Bid. The EPD (Environmental product declaration) of Control Desk shall be verified in accordance with ISO 14025 (from UL/Intertek) for Impacts on Environment by Control Desk. Valid report/document from UL/Intertek to be submitted along with the technical bid. | Bidder to Comply TS. |
| 130 | Vol. II Part-B Appendix-K Pg. 2 of 2 | Appendix- K Typical Architecture of Control Centre: The detailed architecture of main, backup control centre and RTAMC shall be finalized during detailed Engineering, considering latest cyber security guidelines. | As the architecture is dependent on the BoQ, the offer and scope is based on the same as in the tender specification. As any additional items/equipment may have cost impact, request POWERGRID to consider the same accordingly. | Bidder to propose architecture during detail engineering as per requirement of TS. |
| 131 | Vol. II Part-B Appendix-M Pg. 1 of 2 | Appendix-M Operator Training Simulator (OTS) sample Test Cases: | As there the scope of NTAMC is only SCADA and no EMS functions are included, the power system network model, simulator load modelling, network simulation etc. are not applicable and possible without building the EMS network model. Hence, for only SCADA OTS is not applicable and request the same to be removed. | Refer Sr.no 53. |
| g 132 | Vol. II Part-B Appendix-P Pg. 1 of 27 | Application Communication and Other Servers: Processor: 2x8 core, Base Frequency - 3 GHz, X86 64-bit | Request for Changes: Processor: 2x8 core, Base Frequency - 3 GHz, X86 64-bit with 18MB L3 Cache Justification: Defined L3 Cache to have right processor for the solutions | Bidder to comply TS. |
| 133 | Vol. II Part-B Appendix-P Pg. 2 of 27 | Archive and Configuration Server: Processor: 2x8 core, Base Frequency - 3 GHz, X86 64-bit | Request for Changes: Processor: 2x8 core, Base Frequency - 3 GHz, X86 64-bit with 18MB L3 Cache Justification: Defined L3 Cache to have right processor for the solutions | Bidder to comply TS. |
| 134 | Vol. II Part-B Appendix-P Pg. 1 of 27 | Application Communication and Other Servers: 4, Processor 2x8 core, Base Frequency - 3 GHz, X86 64-bit | Change Required: 4, Processor 2x8 core, Base Frequency - 2.2 GHz, X86 64-bit Justification/Clarification: Request to align CPU frequency of DRS with specification mentioned in Vol 2, PartB, Section5 | Bidder to comply TS. |
| 135 | Vol. II Part-B Appendix-P Pg. 1 of 27 | Application Communication and Other Servers: 4, Processor 2x8 core, Base Frequency - 3 GHz, X86 64-bit | Justification/Clarification: In case of bidder offering virtual server, 2 x 8 core would be considered as virtual core or physical core. | Bidder to comply TS. |
| 136 | Vol. II Part-B Appendix-P Pg. 2 of 27 | Archive and Configuration Server: 4, Processor 2x8 core, Base Frequency - 3 GHz, X86 64-bit | Change Required: 4, Processor 2x8 core, Base Frequency - 2.2 GHz, X86 64-bit Justification/Clarification: Request to align CPU frequency of DRS with specification mentioned in Vol 2, PartB, Section5 | Bidder to comply TS. |
| 137 | Vol. II Part-B Appendix-P Pg. 2 of 27 | Archive and Configuration Server: 4, Processor 2x8 core, Base Frequency - 3 GHz, X86 64-bit | Justification/Clarification: In case of bidder offering virtual server, 2 x 8 core would be considered as virtual core or physical core. | Bidder to comply TS. |
| 138 | Vol Vol. II Part-B Appendix-P Pg. 3 of 27 | Common features in Control Centre Firewalls (Internal / External: Type-I, Type-II and Type-III) S.no 4 Support Active-Active/Active-Standby mode | We suggest that both Active-Active and Active-Standby mode operations should be supported on firewall for supporting different use case scenarios. Kindly amend the clause as below - Support Active-Active and Active-Standby mode | Bidder to comply TS. |
| 139 | Vol. II Part-B Appendix-P Pg. 3 of 27 | Common features in Control Centre Firewalls (Internal / External: Type-I, Type-II and Type-III) S.no 8 AT66, NAT64, NAT46/IPv4 over IPv6 | Type-I and Type-III firewall are external firewalls which are supposed to handle DNS traffic also. Hence we recommend to consider IPv6 feature of DNS64 in order to handle DNS communication between IPv4 and IPv6. Kindly amend the clause as below - Support IPv6 features like NAT66, NAT64, NAT46/IPv4 over IPv6, DNS64 | Bidder to comply TS. |
| 140 | Vol. II Part-B Appendix-P Pg. 4 of 27 | Common features in Control Centre Firewalls (Internal / External: Type-I, Type-II and Type-III) S.no 18 DNS sinkholing / DNS filtering against malware / redirect to block portal/ Malware DNS Trap & DNS guard/Reputation domain protection feature etc. | We understand that firewall must have capability to protect against & block malicious domains based on real time analysis with domain intelligence. DNS sinkholing / DNS filtering against malware / redirect to block portal/ Malware DNS Trap & DNS guard. Reputation intelligence based domain protection feature etc. | Bidder to Comply TS. |
| 141 | Vol. II Part-B Appendix-P Pg. 4 of 27 | Common features in Control Centre Firewalls (Internal / External: Type-I, Type-II and Type-III) S.no 29 Support for SSL/TLS encrypted traffic scanning: Yes, example (SSL stripping or HTTPS inspection) | There are multiple versions of SSL/TLS and some versions are already declared non suitable to be used because of serious security concerns/vulnerabilities in older versions. It is utmost important that firewall must support latest updated versions of SSL/TLS to ensure there is no security lapse. We understand that firewall must support updated released versions of SSL/TLS such as TLS1.1, TLS1.2, TLS1.3 and HTTPS inspection on HTTPv2, HTTPv3. Kindly confirm. | Confirmed |
| 142 | Vol. II Part-B Appendix-P Pg. 6 of 27 | Additional features in Control Centre Firewalls (Internal / External: Type-I, Type-II and Type-III) S.no 7 Additional 1no. Hardware Based (purpose-built appliance) shall be provided along with 1 pair of Firewall of same OEM at Main NTAMC & Back up NTAMC | We understand that additional hardware appliance asked in this clause is for Anti-APT Sandbox appliance. Kindly confirm. | Envisaged with Type-I & Type-III firewalls at Main and Back up NTAMC. |
| 143 | Vol. II Part-B Appendix-P Pg. 7 of 27 | b. Sizing parameters for Control Centre Firewalls | b. Sizing parameters for Control Centre Firewalls. Reference of Threat Prevention throughput must be available on Public Website/datasheets. Any letter head declaration on Next Generation Threat prevention performance and features are not acceptable Justification: - The Next Generation Threat Prevention features must be tested and available on public website/datasheet with performance numbers. this will ensure that all the functionalities are available publicly and used by customers to have transparent partnership. | Bidder to comply TS. |
|  |  |  | Please modify the clause to include following language: "b. Sizing parameters for Control Centre Firewalls. Reference of Threat Prevention throughput must be available on Public Website/datasheets. Self-Declarations should not be allowed." |  |
| 144 | Vol. II Part-B Appendix-P Pg. 7 of 27 | b. Sizing parameters for Control Centre Firewall Sr no 4 Minimum IPSEC VPN Throughput – (Type II and Type III (VPN not reqd.) | 4. Minimum IPSEC VPN throughput: - NTAMC/BNTAMC Type 2 and Type 3 (10Gbps), ER-RTAMC (10 Gbps) Proposed Firewalls must provide the Next Generation Firewall Throughput of 20Gbps with following features Firewall, Application and IPS from day 1. Justification: The performance numbers are not matching with industry standard requirements and moreover the sizing of NGFW must be done considering the Threat Prevention and Next Generation firewall features. The table partially address the Threat Prevention need but same time lot of performance requirements are missing in the table which enable lot of bidder to quote nonstandard NGFW OEM which may not provide the all threat prevention features and not even provide the effective security as per industry analysis reports (NSS< Gartner etc.) This clause is very generic and may even compromise the cyber security posture of NTAMC. On the other hand, all the appliances may require to enable the SSL inspection as well to provide the true positive security inline to Anti-APT devices hence such performance impact must be considered and defined the sizing carefully to ensure no bottleneck in network. Wherever Threat Prevention policy is not applicable or not compatible firewall must provide minimum protection by enabling the Next Generation Firewall Features ( FW + IPS + APP) from attacks hence its mandatory to define these parameters as well. | Bidder to comply TS. |
| 145 | Vol. II Part-B Appendix-P Pg. 16 of 27 | 7. Workstation/Remote Consoles | In substations, there are total 900 Workstations, kindly confirm how many workstations is envisaged for VMS at substations - 300 or 600? | 300nos. |
|  |  |  | In substations, kindly confirm which type of monitor is envisaged for VMS? Type 1 or Type 2 or Type 3? How many displays shall be connected per workstation in sub-stations? | Type-2 TFT for VMS system. Single display for each Workstation. |
|  |  |  | Please help us understand more on finger print sensor authentication (do you want a H/w Finger print reader (separately can be sourced from outside OR Inbuild in the keyboard (win compatible). Or only the support is required? | Please refer Vol-II Part-B Clause 1.7. Section-1. |
|  |  |  | Kindly specify number of display port required & which type? | Please refer Vol-II Part-B, Clause-5.2.8 of Section-5. |
| 146 | Vol. II Part-B Appendix-P Pg. 16 of 27 | 7.Workstation/Remote Consoles | Preinstalled OS shall be required. Kindly mention the same in the specifications. | Please refer Clause 4.1.2 of Vol-II Part-B, Section-4 |
| 147 | Vol. II Part-B Appendix-P Pg. 16 of 27 | 8. TFT Colour monitors Type-1 55” TFT with stand on wheels | Kindly confirm the height of the stand along with basic specifications | As per detailed Engineering. |
| 148 | Vol. II Part-B Appendix-P Pg. 16 of 27 | 7. Workstation/Remote Consoles Interfaces (For NTAMC) Interfaces (Back up NTAMC, ER-RTAMC & CR-RTAMC) | Based on the interfaces being asked under clause 10(a) & 10(b), model no of workstation will be different in NTAMC & in substations as per OEM design. Pls confirm | Confirmed. |
| 149 | Vol. II Part-B Appendix-P Pg. 16 of 27 | 7. Workstation/Remote Consoles | Parameters mentioned under this clause can be met by desktop grade machines as well, pls re confirm that requirement is of workstation & not desktop grade machines. | Refers to Workstation. |
| 150 | Vol. II Part-B Appendix-P Pg. 27 of 27 | FC Switch for SAN Storage Functions - FC Switch for SAN Storage | SAN Switch quantity is not mentioned in BoQ. We understand Bidder shall propose this sizing as per their design requirements. | SAN Switches are part of SAN Line item. |
| 151 | Vol. II Part-B Appendix-P | DRS of Workstation, Switch, Router, Firewall etc. Interface ports with Auto-Negotiation | Please note that Auto-Negotiation is not available on SFP/SFP+ ports. Hence this requirement should be deleted from all clauses where it is appearing in TS. | Auto negotiation is not applicable for SFP/SFP+ ports. |
| 152 | Vol. II Part-B Appendix-Q Pg. 1 of 1 | SIEM Operational Philosophy | Every OEM has different architecture of SIEM solution. We understand that the Operation Philosophy mentioned in Appendix-Q is an indicative framework which provides broader guideline for deployment of SIEM solution. However, bidder can propose SIEM architecture ensuring that - "The SIEM solution redundancy should be such that loss of any one hardware at Main NTAMC/BNTAMC/RTAMC should not result in loss of functionality or loss of log collection" | Bidder can propose own solution meeting the high availability requirements as per TS. |
| 153 | Vol. II Part-B Appendix-Q Pg. 1 of 1 | SIEM Operational Philosophy Sr.no 1 SIEM Correlation engine at Main and Back up NTAMC are in redundant configuration and are in Hot-Stand By Configuration. | HA across data center are not recommended considering high latency across wan , it is thus requested to relax the clause and propose HA in the same DC & Active - Active DC & Architecture. | HA across data centre is not envisaged. |
| 154 | Vol. II Part-B Appendix-Q Pg. 1 of 1 | SIEM Operational Philosophy Sr.no 2 The Connector Server -1 collects logs, compress and transmits to SIEM Correlation engine at Main NTAMC. Similarly, Connector Server -2 collects logs, compress and transmits to SIEM Correlation engine at Back up NTAMC. | Every OEM has their way of delivering HA solution, the prescribed method is tilting toward a single OEM. It thus requested allow flexibility on how replication for both sites will be done. | Bidder can propose own solution meeting the high availability requirements as per TS. |
| 155 | Vol. II Part-B Appendix-Q Pg. 1 of 1 | SIEM Operational Philosophy Sr.no 3 In case of disconnection of Connector Server and correlation engine, the Connector Server shall be capable of storing the logs locally and transporting the same to correlation engine once the connection is re-established. However, redundant connector server shall continue to send the logs to Back up NTAMC in case of link is healthy. | Every OEM has their way of delivering HA solution, the prescribed method is tilting toward a single OEM. It thus requested allow flexibility on how replication for both sites will be done. Redundant collector are in passive state and shall only be active in case of primary collector going down | Bidder can propose own solution meeting the high availability requirements as per TS. |
| 156 | Vol. II Part-B Appendix-Q Pg. 1 of 1 | SIEM Operational Philosophy Sr.no 4 In case of failure of Hot SIEM Correlation engine then Stand by SIEM Correlation engine shall take over without any delay and manual intervention | 4) In case of failure of Hot SIEM Correlation engine then Stand by SIEM Correlation engine shall take over without any delay and loss of features & logs. | No Manual Intervention envisaged for log collection. |
| 157 | Vol. II Part-B Appendix-Q Pg. 1 of 1 | SIEM Operational Philosophy Sr.no 4 In case of failure of Hot SIEM Correlation engine then Stand by SIEM Correlation engine shall take over without any delay and manual intervention | SIEM DR cannot be completely automated. There is a DR SOP that needs to be followed, and it may involve some manual steps. Please relax this point. | Refer above clarification. |
| 158 | Vol. II Part-B Appendix-Q Pg. 1 of 1 | SIEM Operational Philosophy Sr.no 5 The SIEM dashboard of Back up NTAMC shall be visible at Main NTAMC and vice versa. | The platform will support active-active deployment , dashboard created at one site can be exported and imported on the other site too, do confirm if the same meets your expectation. | Confirmed. |
| 159 | Vol. II Part-B Appendix-Q Pg. 1 of 1 | SIEM Operational Philosophy Sr.no 4 In case of failure of Hot SIEM Correlation engine then Stand by SIEM Correlation engine shall take over without any delay and manual intervention | The HA will proposed in active passive mode, in case the primary collector goes down the secondary will take over the primary collector. We hope this is in line with your expectation. | Bidder can propose own solution meeting the high availability requirements as per TS. |
| 160 | Vol. II Part-B Appendix-Q Pg. 1 of 1 | SIEM Operational Philosophy Sr.no 8 Storage of logs at Main NTAMC/BNTAMC shall be done considering the events sustained. | We understand the expectation is to propose storage considering average EPS equivalent to sustained EPS count. | Refer: Vol. II Part-B Appendix-P, Sr no 12 Pg. 15 of 27 |
| 161 | Vol. II Part-C Clause 1.0 Pg. 4 of 24 | 1.Introduction © Remote access of the Relays/IEDs in the Substation from Control centers (RTAMC and NTAMC) and substation Client PCs for collecting the relay parameters & settings, configuration files, internal logs, event lists etc. | This is part of Relay configuration software supplied by the employer. It is not scope of RAS software itself but providing the remote link only. Please confirm | Relay configuration software shall be provided by Employer. Bidder shall provide access to Relays using this software from Control Center in a secure manner. |
| 162 | Vol. II Part-C Clause 1.2 Pg. 5 of 24 | Control Centre architecture The Main Control Centre and Backup Control Centre RAS System shall have redundant servers for acquiring data from the various SDCs and AutoDR systems. | In the existing solution does AutoDR systems transfer DR files to the control center RAS servers in COMTRADE format? What is the protocol used for transfer of Auto DR files? | Yes, SFTP/HTTPS. Refer Amendent-1 |
| 163 | Vol. II Part-C Point 1.2 Pg. 5 of 24 | Control Centre architecture The Main Control Centre and Backup Control Centre RAS System shall have redundant servers for acquiring data from the various SDCs and AutoDR systems. | How does AutoDR systems transfer DR files to the control center RAS servers? Is there an SFTP client in each of the AutoDR system? Will the files be converted to COMTRADE before transferring? Will the DR files be renamed to IEEE naming structure before transfer? | Refer Amendment-1 for AutoDR System. |
| 164 | Vol. II Part-C Clause 3.0 Pg. 7 of 24 | 3 Functional Requirements for RAS System The Remote Accessibility System shall provide access to the remote device i.e. protection relays. These remote devices shall be having either serial port or Ethernet port. These devices shall be accessed from client PCs at control centers and substations through RAS servers using the existing RAS equipment at substation for relay parameterization, configuration changes, internal logs & database downloads, and diagnosis. Relay configuration software shall be installed in RAS client PC and these shall be used to access the devices from remote for configuration and settings changes. Relay configuration software shall be supplied by employer. | This is part of Relay configuration software supplied by the employer. It is not scope of RAS software itself but providing the remote link only. Please confirm | Relay configuration software shall be provided by Employer. Bidder shall provide access to Relays using this software from Control Center in a secure manner. |
| 165 | Vol. II Part-C Clause 3.0 Pg. 7 of 24 | 3: Functional Requirements for RAS System RAS system shall differentiate actual and spurious DR and shall have facility to automatically blocking the transfer of DRs in case of the number of DRs received from a particular relay is more than the user defined limits. An SMS and Email shall be generated for auto blocked relay. | Requirement to send SMS messages to indicate alarms are there in different parts of RAS specification. This is also there in AFAS specifications. Whether SMS function is needed? Will an SMS gateway be provided by the PGCIL. We request PGCIL to confirm | SMS gateway shall be provided by Employer. Bidder has to provide support for SMS integration through e-mail. |
| 166 | Vol. II Part-C Clause 6.0 Pg. 19 of 24 | 6.0: Dashboard Alerts shall be generated and sent to the respective user through email/SMS based on criteria customized and user configurable. |  |  |
| 167 | Vol. II Part-C Clause 3.1(2) Pg. 8 of 24 | 3.1: System and Device monitoring/ (2) System monitoring (b) No. of outages, duration of outages, no. of records received from each device, substation and region. | Outage and associated information may be more relevant to AFAS application than RAS. | Related to SDC and associated relays/IEDs. Bidder to comply TS. |
|  |  |  | No of outages and duration of outages can be arrived only based on breaker operations of each bay. RAS will not be aware of each and every breaker operation as analysis of the DR files will be done only by AFAS. Request to move this requirement to AFAS section. | Refers to devices installed in substations i.e. SDC and associated relays/IEDs. |
| 168 | Vol. II Part-C Clause 10.0 Pg. 22 of 24 | APIs, Device drivers and Software deliverables …These APIs and SOAP/REST web services shall be well documented and the source code for the same shall be supplied along with the system. API shall provide any data collected and generated after processing by RAS&AFAS…. | We understand it to be source code of API client application. Request to clarify /correct the clause as "source code of sample client application shall be supplied along with the system." | Source code of API required. Bidder to comply TS. |
| 169 | Vol.II Part-C Clause 8.3(e) Pg. 22 of 24 | Any failure/problem at the main NTAMC is to be attended immediately, whereas a period of 12 hours (from the time of reporting) shall be provided to attend failure/problem at Backup NTAMC and RTAMCs. This 12 hour period shall be considered as hold time and will not be part of the Availability calculation. | We request you to clarify this requirement. | Refer Amendment No-1. |
| 170 | Vol. II Part-D Clause 2.4(d) of Sec-2 Pg. 5 of 15 | The UPS shall provide 3-phase, four wire output plus ground. | The UPS output should be 240VAC single phase considering the setup required to be powered is single phase. Please amend the specification. | Bidder to comply TS. |
| 171 | Vol. II Part-D Clause 2.4.1(d) of Sec-2 Pg. 5 of 15 | Rectifier/Charger Unit: Capacity to recharge the batteries to 90% State of Charge from fully discharged state (i.e. ECV of 1.75 V) within 8 hrs while carrying full load where battery charging current shall be considered as at least 20% of Battery AH capacity. | It should be 10% of the Battery AH capacity instead of 20%. Even the manufacturer's don’t recommend for charging at 20% rate. | Bidder to comply TS. |
|  |  |  | We request to change this to 10% of the Battery AH capacity instead of 20%. Since the manufacturer's don’t recommend for charging at 20% rate. | Bidder to comply TS. |
| 172 | Vol. II Part-D Clause 2.4.2(k) of Sec-2 Pg. 6 of 15 | Inverter: The inverter shall include two winding / phase load transformer of one to one ratio with electrostatic shielding. This load transformer can be either internal or external to UPS panel. | Transformer should be External since in that case galvanic isolation will be provided in bypass mode as well. In case of inbuilt Isolation transformer there is no protection in the bypass path | Bidder to comply TS. |
| 173 | Vol. II Part-D Clause 2.5 of Sec-2 Pg. 8 of 15 | UPS Control/Monitoring | UPS shall be a standalone system and not integrated with SCADA. Please confirm. | Confirmed. |
| 174 | Vol. II Part-D Clause 4.1 of Sec-4 Pg. 3 of 7 | Power Cables: All external power cables shall be stranded Aluminium conductor, armoured XLPE/PVC insulated and sheathed, 1100V grade as per IS 1554 Part-I. The conductor for the Neutral connection from UPS to Output ACDB shall be sized 1.8 times the size of the Phase conductors to take care of the non-linear loads. However, the cable between UPS & Battery bank shall be of stranded copper conductor (armoured type). | Input & output power cable/DC Cable should be cu flexible instead armoured cables | As per Detailed Engineering. |
|  |  |  | Input & output power cable/DC Cable should be Cu flexible instead armoured cables as per feedabck from OEMs. Please confirm. |  |
| 175 | Vol. II Part-D Clause 4.4 of Sec-4 Pg. 4 of 7 | Enclosures/Panels design: The thickness of the structural frames and load bearing members shall be minimum 1.5 mm and for others shall be minimum 1.0 mm. | As per industry standards it should be 1.2 mm for load bearing members and 1 mm for others | Bidder to comply TS. |
| 176 | Vol. II Part-D Clause 4.6 of Sec-4 Pg. 5 of 7 | AC Distribution Boards Requirements | Please provide ACDB SLD with outgoing feeder details. | Bidder to comply TS. |
| 177 | Vol. II Part-D Appendix-A Pg. 1 of 2 | BOQ for Auxiliary Power Supply Equipment’s for NTAMC project | UPS qty as per Price schedule is not matching with Appendix-A BOQ for Auxiliary Power Supply Equipment. We understand Price Schedule qty shall be final. | Refer Amendemnt-1 |
| 178 | Vol. II Part-E Point 2.0 Pg. 03 of 28 | 2. Scope of the work The scope of works under this project includes design, supply, erect, test and commission to complete the successful upgradation of VMS system. The contractor shall ensure smooth migration of the settings, database, configuration, etc. of all the existing equipment available at various locations and shall successfully integrate them with new upgraded control center VMS software. Old and new system shall run in parallel for three month before final migration to new VMS after due diligence testing/validation. The Bidder shall submit the migration plan and parallel operation for the project along with the Bid. | Does it mean that SI has to run both systems (Existing and New) in parallel for few months and they need to deploy dedicated team till the existing settings like Presets, Map configuration, camera configuration and other settings are rebuilt in the new system. Please confirm. | System to be run in parallel. Bidder has to propose solution to meet TS requirement. |
|  |  |  | For running the system in parallel there might be a requirement of different streams from camera rather than one which is being used by existing system. Kindly confirm whether the same shall be available. Also there would be IP port requirements to connect workstations, servers etc. Kindly confirm same is available or not. Same is not being considered in current scope of works. | System to be run in parallel. Bidder has to propose solution to meet TS requirement. |
| 179 | Vol. II Part-E Clause 2 Pg. 3 of 28 | 2. Scope of the work The contractor shall evaluate the compatibility of new application with existing NVR hardware as mentioned in Appendix-A and submit the detailed report. The contractor shall provide detailed process for migrating to new VMS software. | Kindly confirm why this compatibility check is required? BOQ contains all new hardware which is envisaged to replace the existing hardware. Compatibility check cannot be done only on OS basis , other parameters are required too | Bidder to Comply TS. |
| 180 | Vol. II Part-E Clause 3.1 Pg. 5 of 28 | Functional Requirement shall have the capability/provision to support minimum 50 cameras in each NVR. | As we understand, 50 camera connection licenses and 50 video analytics licenses have to be considered at each substation location. Kindly confirm if our understanding is correct. | Refer Appendix A of Part E for details of existing Cameras. NVR shall have the capability as per required functional requirement. |
| 181 | Vol. II Part-E Clause 3.2 Fig 2 & 3 | Figure 2 & 3 | We understand that these are 2 separate systems/servers, etc. and integration of these 2-system are not in our Scope. | Confirmed. |
| 182 | Vol. II Part-E Clause-3.2 Page 6 of 28 | 3.2. Visual Monitoring System Architecture Level –I: National Transmission Asset Management Centre (NTAMC) / Back-up NTAMC There shall be dedicated client work stations for performing the functions of VMS system at NTAMC and BNTAMC, The Video wall installed for SCADA at NTAMC and BNTAMC shall also be used for performing the functions of VMS system. | How many workstations are envisaged in the NTAMC & BNTAMC for VMS alone? | NTAMC : 9nos ( 3no with Type-1 TFT & 6no with Type-2 TFT) Back up NTAMC : 5nos (1no with Type-1 TFT & 4no with Type-2 TFT) |
| 183 | Vol. II Part-E Clause-3.2 Page 6 of 28 | 3.2. Visual Monitoring System Architecture Level –II: Regional Transmission Asset Management Centers (RTAMCs) At RTAMC end, Failover NVR server shall serve as a back-up/failover hardware to the Network Video Recorders of the Substation Network Video Recorder (NVR) of a region. Along with Failover NVR there shall be dedicated client work stations for performing the functions of VMS system at RTAMCs. | How many workstations are envisaged in the RTAMC for VMS alone? | Each ER-RTAMC & CR-RTAMC : 5nos ( 1no with Type-1 TFT & 4no with Type-2 TFT) |
|  |  |  | Multiple servers shall have single failover server considering N:1 redundancy. Kindly confirm. More than 1 server failure cannot be tolerant | Bidder to Comply TS. |
|  |  |  | Kindly confirm if there would be any hot stand by server within the RTAMC for the failover server of substations? | Not Envisaged. |
| 184 | Vol. II Part-E Clause-3.2. Page 7 of 28 | Level-III: Substation Level At Substation end, Network Video Recorder (NVR) shall be installed to continuously record the video from the cameras installed at all the substations. One client PC shall be provided at these substations to perform all VMS functions. | Kindly confirm whether 600 WS is required or 300 for VMS? | 300nos Workstations Envisaged at Substation. |
| 185 | Vol. II Part-E Clause 3.3 Pg. 7 of 28 | System sizing and Expandability The Video Management System shall be sized such that they can accommodate 100% expansion of the present requirement in number of devices (Cameras, NVR, equipment) connected to it and 100% expansion in number of remote clients. The present requirement stands for 300 NVR, 3500 Cameras and 600 numbers clients (two clients at each substation). | - As we understand, proposed solution should be scalable to support up to 15000 cameras (considering to support minimum 50 cameras per location). Kindly confirm if our understanding is correct. - As per RFP reference from page 7, The VA quantities are not mentioned in the RFP. We request that you kindly confirm the video analytics quantity per location, so that compute power can be calculated and optimized accordingly. | - Not 15000, It shall be 7000nos cameras. However, NVR shall able to support minimum 50ns cameras. - Video Analytics are Envisaged for each camera as per Part-E, Appendix-A. |
|  |  |  | Does the software license should be consider with 7000 cameras, as its asked for 100% expansion. | Initial sizing of Software License shall be for 3500 Cameras. VMS system shall have capability to accommodate 100% expansion of present requirement. |
|  |  |  | This clause calls for 600 Workstations with 2 clients at each substation whereas above clause calls for 300 Workstations for VMS. Kindly confirm. | In present scope 300nos Workstations envisaged at Substation along with a provision for additional 300nos client which shall be provided by Employer. |
|  |  |  | Kindly correct the wordings for this clause. If we size for 100% expansion then 7000 licenses to be considered, servers capacity has to be doubled. System will support 100% expansion however procurement needs to be done for extra licenses & servers at later stage. Pls confirm | Refer Above. |
| 186 | Vol. II Part-E Clause 3.3 Pg. 8 of 28 | 3.3. System sizing and Expandability Online storage for VMS servers shall be considering storage of all alarm and event logs for a period of 3 months. It shall automatically overwrite after utilization of 70% of total memory. However, all the events and alarm logs shall be available in archive system for a period of 1 year. It shall be possible to export the data to off-line storage devices in a text format. | Where is the archive system planned? As a part of VMS is there any NAS Box required at NTAMC? Where these logs to be maintained? AT NTAMC, RTAMC or substations? | Online Storage is envisaged at Main & Back up NTAMC. SAN/NAS box is envisaged for this purpose. |
| 187 | Vol. II Part-E Clause 3.8 Pg. 9 of 28 | Technical Specifications for Visual Monitoring System, Control & Recording Software S.no 1 The VMS shall support integration of camera on different ONVIF profiles (S, G, T) with user selectable option available in dropdown menu. However, existing cameras integration shall be through SDK and API only in case of non-availability of ONVIF compliant cameras. Latest ONVIF profile shall be deployed in the system within 3 months from the release date of new ONVIF profile without any financial implication to Employer up to AMC period. | Its asked in your requirement that the VMS shall support integration of cameras on different ONVIF profile (S,G,T), also functionality mentioned in your RFP related to camera integration can be 100% achieved using ONVIF S,G T profiles, and no additional profile is required. Any additional profile added by ONVIF is basically to add some new features which is currently not mentioned in RFP. Hence the open statement " Latest ONVIF profile shall be deployed in the system within 3 months from the release date of new ONVIF profile without any financial implication to Employer up to AMC period" as it is very difficult for OEM/ SI to decide and act upon on ONVIF road map without knowing the effort and requirement. And no base to account this in commercial prices, So requesting you to remove above statement of Latest ONVIF profile shall be deployed in the system within 3 months from the release date of new ONVIF profile without any financial implication to Employer up to AMC period" | Bidder to comply TS. |
| 188 | Vol. II Part-E Clause 3.8. Pg. 9 of 28 | 3.8. Technical Specifications for Visual Monitoring System, Control & Recording Software Minimum features such as general camera settings (e.g. multicast streaming), recording profiles (including Codec, resolution, frames per second, bit rate), Audio profiles etc. shall be available in ONVIF profile configuration of VMS system. The software shall be capable of integrating cameras, NVR from any third-party system through published and configurable APIs without any major modification or programmers support in the system. | Post release of ONVIF profile, same is adopted by VMS OEMS after thorough R&D, this will take time where 3 months might not be enough. Also VMS upgrades are available at different intervals for different VMS OEMs. This clause may not be feasible in normal scenario. Kindly re-confirm | Bidder to Comply TS. |
|  |  |  | Does it mean that VMS should comply with ONVIF profile and it should support camera integration which is complying ONVIF profile (S,G,T) | Proposed VMS system shall also facilitates existing cameras integration through SDK and API, in case of non-availability of ONVIF compliant cameras. |
| 189 | Vol. II Part-E Clause 3.8 Pg. 9 of 28 | Technical Specifications for Visual Monitoring System, Control & Recording Software Sr.no 1 The software shall be capable of integrating cameras, NVR from any third-party system through published and configurable APIs without any major modification or programmers support in the system. | Need more clarification on this point. | Bidder to Comply TS. |
| 190 | Vol. II Part-E Clause 3.8 Pg. 9 of 28 | - | 2-factor authentication (offline, cell phone based) The VMS software should have increasing the security of the system by requiring the user to have a second authentication step besides only the user name and the password to prevent hacker to login and audit logs are specified to special person not to the user group. The VMS Software should have the following basis features: i. When user in the group tries to log in for the first time, the user is requested to use or install the 2-factor authentication client (e.g. Authy, Google authenticator, MS Authenticator) on user's mobile device. ii. The VMS and the authentication client will then synchronize the software with VMS. This will happen by transferring the "secret key" generated by the VMS to the authentication software via QR code first time. iii. Thereafter the authentication client generates automatically new one-time passwords. The passwords should change periodically for 30 seconds and should kept in sync as the clocks of the VMS and the authentication app have same time. | Bidder to Comply TS. |
| 191 | Vol. II Part-E Clause 3.8 Pg.. 9 of 28 | - | VMS Software should have Face blurring & Moving object blurring to fulfill GDPR guidelines. Request to add the clause in VMS Specs: 1) Privacy zones, 2) Facial blurring 3) Moving object blurring should be configured in the same UI under System configuration. 4) The privacy functionalities are available also in the exported clips. | Bidder to Comply TS. |
| 192 | Vol. II Part-E Clause 3.8. Sr.3.(f) Pg. 11 of 28 | System Requirements for Visual Monitoring System: (f) The software shall have inbuilt facility to store configuration of Network Video recorders and cameras So that in case of replacement of faulty NVR and camera the settings can be pushed directly from the central VMS application. | As we understand, NVR configuration data such as camera settings etc has to be restored, in case of replacement of a faulty NVR. Kindly confirm if our understanding is correct. | Bidder to Comply TS. |
| 193 | Vol. II Part-E Clause 3.8 Sr.no-3(2)(q) Pg. 13 of 28 | 3.8. Technical Specifications for Visual Monitoring System, Control & Recording Software 3. System Requirements for Visual Monitoring System: q. The VMS shall have built-in facility of to ensure tamper proof recording | Request to add the clause as below for better data security: q. The VMS shall have built-in facility of to ensure tamperproof recording and exporting of video in a tamper proof format. The media player provided in the software shall automatically notify if the video or audio has been modified. | Bidder to Comply TS.. |
| 194 | Vol. II Part-E Clause 3.8 Sr.no.3(2)(q) Pg. 13 of 28 | 3.8. Technical Specifications for Visual Monitoring System, Control & Recording Software (s) It shall be possible to have simultaneous display of video on the Console/monitor of the client workstation and the Video Wall at control centers. The client workstations shall have the necessary interfaces/ports to meet the above requirement. | Interfaces shall be as per specifications given in Hardware DRS. Pls confirm | Necessary Interfaces for integrating with Video wall is to be considered by Bidder. |
| 195 | Vol. II Part-E Clause 3.11 Pg. 20 of 28 | 3.11. Technical Specifications of Network Video Recorder (NVR) (13) GPU: NVIDIA RTX A4000/RTX A5000/ GTX 1080 Ti or Better compatible with VCA of VMS application | GPU is not required for VMS NVR, kindly remove the same. It will un-necessarily increase the cost quite a lot. Analytics cannot be run on GPU alone without using other compute like server cores, ram etc. Request you to consider separate server as per the above query. | Refer Amendement-1 |
| 196 | Vol. II Part-E Clause 3.11 Pg. 19 of 28 | 3.11. Technical Specifications of Network Video Recorder (NVR): (3) x86, 64-bit processor (8 cores or better) 3.0Ghz (min.), 16 MB Cache, 32 GB memory with 16 TB (minimum) storage capacity to store 15 days recording with Raid 5 or latest suitable configuration along with Colored TFT 22” High resolution monitor | Kindly confirm whether 22”-inch monitor is required with servers as well. | Confirmed. |
| 197 | Vol. II Part-E Clause 3.11 Page 19 of 28 | 3.11. Technical Specifications of Network Video Recorder (NVR): (7) The NVR/VMS shall be capable to integrate with digital I/O points either available in cameras or access controller. In case of alarm triggered by any Digital Alarm Input the NVR / VMS shall be capable to activate custom defined rule already programmed in the system without any manual intervention. Upon recognition of an alarm, the system shall be capable of displaying the video from the NVR/VMS that is associated with the alarm point. | In order to achieve this functionality OPC based IO modules shall be required. Same is not available in BOQ. Kindly confirm whether only capability is required or IO module needs to be considered. | Bidder to Comply TS. |
| 198 | Vol. II Part-E Clause 3.11 Pg. 19 of 28 | 3.11. Technical Specifications of Network Video Recorder (NVR): (8) Minimum 16 TB in RAID-5 Configuration or better to store minimum 15 days recording of cameras as at HD resolution & 25 FPS. The NVR storage shall have an additional camera integration capacity of 25 %. | Kindly confirm whether 25% extra is required after loading how many cameras? | Please refer Clause 3.11 of Part-E. 50 Cameras per Server is envisaged. |
| 199 | Vol. II Part-E Clause 3.11 Pg. 20 of 28 | Back-up /Fail-over Network Video Recorder: (1) The main purpose of Back-up/Fail over NVR is to serve as a back-up/failover hardware to the Network Video Recorders of the Substation. In case of failure of any NVR, the pre-defined number of cameras of failed substation NVR shall be automatically registered /recorded at the back-up/failover NVR as per scheme/jurisdiction defined. The frame rate and resolution for recording shall be changed to pre-defined values to optimize the bandwidth requirement. The recording at failover NVR shall start from the time of failover and previously recorded data in the NVR shall not be transferred to failover NVR. After recovery of NVR at the substation, the recording shall be stopped at failover NVR and shall switch over to NVR at substation without any manual intervention. | Kindly confirm whether back-up functionality is required, or failover is required? | Failover NVR functionality is envisaged. The pre-defined number of cameras of failed substation NVR shall be automatically registered /recorded at the back-up/failover NVR |
|  |  |  | Kindly confirm max how many cameras of 1 substation needs to be recorded in case of substation server failure. | The pre-defined number of cameras of failed substation NVR shall be automatically registered /recorded at the back-up/failover NVR which shall be finalized during detail engineering. |
|  |  |  | Kindly confirm if the qty per RTAMC shall be 1 no for such failover server | Bidder to Comply TS. |
|  |  |  | When substation server is failed & taken over by RTAMC server, recording will happen at RTAMC server, when the substation is up for recording, then let us know whether the recorded video of 1 day or 2 days at RTAMCs needs to be pushed back to substation server or not? This is critical functionality not available with ever VMS OEM | Please refer TS clause 3.11 page 20 of 28 “The recording at failover NVR shall start from the time of failover and previously recorded data in the NVR shall not be transferred to failover NVR” |
| 200 | Vol. II Part-E Clause 4 Pg. 22 of 28 | Video Content Analysis (VCA) requirements | Since the Video Analytics Server qty is not defined, we understand Bidder is free to size & scale this qty as per OEM recommendation to meet the TS for VMS system. Please confirm. | - Refer 2nd para of Clause 3.2 (VMS Architecture) in Vol II, Part-E, (pg. 05 of 28 ). - Refer Amendment No. 01 |
| 201 | Vol. II Part-E Clause 4 Pg. 22 of 28 | 4. Video Content Analysis (VCA) requirements: 4.1.2 Detection Zone | Kindly confirm how many analytics license per substation is required. This is needed to evaluate license cost along with computing requirements per substation. Analytics is not suitable for PTZ Camera, its ok for fixed cameras | Refer Sr.no 185. |
| 202 | Vol. II Part-E Clause 4 Pg. 22 of 28 | 4.1.3 Object Blocking zone | Kindly confirm how many analytics license per substation is required. This is needed to evaluate license cost along with computing requirements per substation. Analytics is not suitable for PTZ Camera, its ok for fixed cameras | Refer Sr.no 185. |
| 203 | Vol. II Part-E Clause 4 Pg. 22 of 28 | 4.1.4 Motion Detection Capability | Kindly confirm how many analytics license per substation is required. This is needed to evaluate license cost along with computing requirements per substation. | Refer Sr.no 185. |
| 204 | Vol. II Part-E Clause 4 Pg. 22 of 28 | 4.1.5 Intrusion Detection Solution | Kindly confirm how many analytics license per substation is required. This is needed to evaluate license cost along with computing requirements per substation. Analytics is not suitable for PTZ Camera, its ok for fixed cameras | Refer Sr.no 185. |
| 205 | Vol. II Part-E Clause 4 Pg. 22 of 28 | 4.1.6 Camera Sabotage Detection | Kindly confirm how many analytics license per substation is required. This is needed to evaluate license cost along with computing requirements per substation. | Refer Sr.no 185. |
| 206 | Vol. II Part-E Clause 4 Pg. 23 of 28 | 4.1.7 PTZ Tracking | Kindly confirm how many analytics license per substation is required. This is needed to evaluate license cost along with computing requirements per substation. | Refer Sr.no 185. |
| 207 | Vol. II Part-E Clause-4, Page 24 of 28 | 4.1.10 Smoke and Fire Detection: | Kindly confirm how many analytics license per substation is required. This is needed to evaluate license cost along with computing requirements per substation. Analytics is not suitable for PTZ Camera, its ok for fixed cameras | Kindly refer Amendement-1 |
| 208 | Vol. II Part-E Clause 4 Pg. 24 of 28 | 4.1.11 Personal protective equipment (PPE) Violation Detector | Kindly confirm how many analytics license per substation is required. This is needed to evaluate license cost along with computing requirements per substation. Analytics is not suitable for PTZ Camera, its ok for fixed cameras | Kindly refer Amendement-1 |
| 209 | Vol. II Part-E Clause 4 Pg. 24 of 28 | 4.1.11 -Gloves and shoe detection | This is highly compute intensive analytics algorithm & shall need continuous training on ground . Also depending on the colors & size of gloves & shoes, model shall be trained differently which is practically not possible to do for 300 substations if the used PPE is of different types. Kindly check & confirm | Kindly refer Amendement-1 |
| 210 | Vol. II Part-E Clause 4 Pg. 24 of 28 | - | It Is recommended to run one or max 2 analytics per camera depending on the compute requirement of the analytics. Kindly provide the substation qty for analytics accordingly differentiating between different analytics. Kindly use the attached format for qty decision | Bidder to Comply TS. |
| 211 | Vol. II Part-E Clause 4 Pg. 24 of 28 | - | There is no Analytics server being asked in the BOQ. Kindly add minimum 1 Analytics Server qty per substation with below compute requirement: Intel Xeon Processor Silver 4216 x 2 , 64GB RAM, Dual RTXA4000, Redundant PSU, 2x480GB SSD, RAID 1, 6TB Storage RAID 5 | Refer Amendement-1 |
| 212 | Vol. II Part-E Clause 3.8(5) Pg. 16 of 28 | Live Video h) Modify Video Analytic settings and tuning for: · Video motion detection · Object Tracking · Object classification | Does object tracking mean that the PTZ has to follow a moving object in its FOV. | Confirmed. |
| 213 | Vol. II Part-E Clause 3.8(7) Pg. 17 of 28 | 3.8. Technical Specifications for Visual Monitoring System, Control & Recording Software: 7. Recording User Activated: The users shall be able to configure. · Pre-Record Duration: The amount of prerecorded video that will be associated with a user request for recorded video. | Request you to amend the clause as below for better functionality: Pre & Post Record Duration: The amount of prerecorded and post recorded video of alarms of up to 60 minutes that will be associated with a user request for recorded video. | Bidder to Comply TS. |
| 214 | Vol. II Part-E Clause 3.8 Pg. 9 of 28 | - | 3.8. Technical Specifications for Visual Monitoring System, Control & Recording Software Additional features: In today's scenario data security is a major concern in any video application . So, the Proposed Video Monitoring and recording Software must comply the industry standard encryption algorithm as per below clause. So, request you to add the below clause: "The software should comply that all client to server and server to server communications and encryption during export are compressed and encrypted and connection specific key should be 256-bit AES and data encryption should be 256-bit AES. VMS software should have the Encryption algorithm of 4096-bit RSA and hashing of SHA -384 from 3rd party DigiCert trusted G4 for tamper proof data. The exported video should be saved in Secure Export Format for secure non tamper file system with Password key which can be set to 24 Characters. The Client application should support dual password mode for each user. | Bidder to Comply TS. |
| 215 | Vol. II Part-E Clause 3.8 Pg. 13 of 28 | - | Additional features: As there is no video export formats given in the specification. So, we request you to add the below clause for some industry standard common export formats: "The Visual monitoring and recording software The VMS shall provide file export tool for export of single frame of video in BMP, GIF, TIF, JPG and PNG formats and export of video files in SEF, SEF2, ASF, AVI, MP4 and MKV format." | Bidder to Comply TS. |
| 216 | Vol. II Part-E Clause 3.8 Pg. 9 of 28 | - | Additional features: The Visual monitoring and recording software must support the technologies like multi-streaming, multi casting and thru cast streaming. With the help of feature Thru Cast we can directly stream video from camera which will optimize bandwidth and network optimization. | Bidder to Comply TS. |
| 217 | Vol. II Part-E Clause 3.8(13) Pg. 18 of 28 | 13.Digital Sensor Interface: The software solution shall be capable of interfacing with other digital sensors (motion detectors, smoke detectors, electronic fence, etc.). The software solution shall be capable of managing alarm conditions for sensors. The software will be capable of activating and deactivating detection rules on inputs from digital sensors. | Is there any application which reads the sensor data and which can be integrated with VMS? | The software delivered shall have the capabilities to meet said TS requirement. |
| 218 | Vol. II Part-E Clause 4 Pg. 21 of 28 | Video Content Analysis (VCA) requirements | How many cameras (per substation) are relevant for Video Analytics? And how many are relevant only for Monitoring? | - Refer Sr.no 185 Refer Amendment No.1 |
|  |  |  | There is no quantity and bifurcation given in the tender for Video Analytics licenses. For E.g. In substation A :- 5 cameras requires PPE Helmet, Jacket and Smoke detection use case. 2. Analytics on PTZ camera is very limited and preset dependent. In case of PTZ camera, analytics may only be applied on a fixed preset/fixed field of view. 3. No. of rules required per camera(identified for analytics) should be typically 3-4 rules. Please confirm. We request you to kindly mention the total count of cameras for Video analytics per substation and bifurcation of VA use cases required per camera to size the hardware capacity required properly. |  |
|  |  |  | In the BOQ, the Video content analytics Qty. is not defined. Specially the analytics asked like 4.1.10 Smoke and Fire Detection & 4.1.11 Personal protective equipment (PPE) Violation Detector which require GPU servers for processing. Pls clarify the Video analytics qty. |  |
| 219 | Vol. II Part-E Clause 4.1.9 Pg. 23 of 28 | 4.1.9 Reporting tool: The video content analysis system shall include a reporting tool that shall allow the user to generate interactive reports of event counts presented as tables or charts. The report formats shall include text, PDF and Excel data. It shall include a report scheduler, which will periodically generate event count reports in a format specified by the user. | The reporting tool should have some basic features for formal recording of facts related to an incident. The video content analysis system shall include a reporting tool that shall allow the user to generate interactive reports of event counts presented as tables or charts. The report formats shall include text, PDF and Excel data. It shall include a report scheduler, which will periodically generate event count reports in a format specified by the user. The VMS & Video content analytics should support this features of Incident Reporting inbuilt to export Incident reports, Images and video clips. The retention time for Data should be unlimited, and it should export in a dedicated storage drive so that incase storage is burnt/damage/corrupt, we can keep the incident report data safe in dedicated storage of incident report. Adding evidence to the incident report by add image, video clips and camera audit reports must be there. | Bidder to Comply TS. |
| 220 | Vol. II Part-E Clause 5 Pg. 24 of 28 | Integration with CCTV system and other Security System: VMS solution shall provide a unified device interface to devices, including different kinds of third-party devices. The VMS Solution shall be capable for seamless integration with the third-party systems, in future, particularly the following systems using the interfaces defined by ONVIF and PSIA standards: - CCTV system for new substations not covered under the present scope - Intrusion Detection and Prevention System - Access Control System - Attendance System/Card Reader - SCADA Alarm system - Thermo Vision Cameras - Any other security system application | - Access Control System - Attendance System/Card Reader - SCADA Alarm system | The VMS Solution shall be capable for seamless integration with the third-party systems, in future. |
|  |  |  | For integration of CCTV-VMS system with 3rd party systems it should be mandatory that VMS OEM must comply below certifications: a) VMS OEM must be ONVIF Profile S, G & T conformant as per ONVIF website and must be either contributor level/ full level member as per ONVIF website. b) Certificate from GPU/VPU leading technology OEM like Intel/Nvidia. c) The VMS Application should have undergone that Security Audit Certificate as per the OWASP Guidelines to Mitigate Cyber Security Attacks. The Software model proposed should be same as certified. | Bidder to Comply TS. |
|  |  |  | Integrations are possible however cost of integration need not be considered from day. Pls confirm | The VMS Solution shall be capable for seamless integration with the third-party systems, in future. |
| 221 | Vol. II Part-E Clause 5 Pg. 25 of 28 | Integration with CCTV system and other Security System: Last Para - The contractor must extend its full cooperation in this regard. VMS system shall be able to exchange information through published API as well as web services in Simple Object Access Protocol (SOAP) and Representational State Transfer (REST) architectural style using high-level programming languages (preferably Python). These APIs along with SOAP & REST web services shall be well documented and the source code for the same shall be supplied along with the system | We understand that as part of the project scope, we need to integrate VMS systems with third-party systems. Further, these integrations can be done via API, REST/SOAP API, or another way to integrate the systems, and it is not mandatory to integrate only the systems via SOAP and REST. we request you to Kindly amend this clause as “VMS system shall be able to exchange information through published API as well as web services in Simple Object Access Protocol (SOAP)/ Representational State Transfer (REST) architectural style using high-level programming languages (preferably Python). These APIs along with SOAP/REST web services shall be well documented and the source code for the same shall be supplied along with the system". | Bidder to comply TS. |
| 222 | Vol. II Part-E Clause 6.1 Pg. 25 of 28 | 6.1. Factory Acceptance test 5 NVRs representing 5 substations, and with at least 2 cameras connected with each NVR. Cameras are to be arranged by The contractor during FAT at their cost. | Kindly confirm which type of camera to be arranged for this activity? Any particular make or specifications? | Bidder to Comply TS. |
| 223 | Vol. II Part-E Clause 6.2(b) Pg. 27 of 28 | b)UTILISATION Server Processor & Memory utilization at National Control Centre (Less than 30%) | Kindly confirm whether this 30% utilization being asked is after loading how many cameras per server at substation? | 30% Utilization of VMS Server is envisaged for present requirement. |
| 224 | Vol. II Part-E Clause 6.2(b) Pg. 27 of 28 | b)UTILISATION Server Processor & Memory utilization at National Control Centre (Less than 30%) | This clause is usually applicable for SCADA or other low compute requirement systems. If we talk about 30% utilization post 50 cameras loading, then compute has to be planned for at least 150 cameras which will lead to higher specifications of at least 20 cores & 128 GB RAM. Kindly correct | Bidder to Comply TS. |
| 225 | Vol. II Part-E Clause 6.2(b) Pg. 27 of 28 | b)UTILISATION (1) Server Processor & Memory utilization at National Control Centre (2) NVR Processor & Memory utilization at each Substation (Less than 30%) | This clause is usually applicable for SCADA or other low compute requirement systems. If we talk about 30% utilization post 50 cameras loading, then compute has to be planned for at least 150 cameras which will lead to higher specifications of at least 20 cores requires & 128 GB RAM. Kindly correct | - Bidder to Comply TS. - Refer Amendment-1 |
| 226 | Vol. II Part-E Clause 6.2(b) Page 27 of 28 | b)UTILISATION Server Processor & Memory utilization at National Control Centre (Less than 30%) | Kindly make the acceptable utilization to 90% at least | Refer Sr.no-223. |
| 227 | Vol. II Part-E Appendix-A Pg. 7 of 14 | Appendix-A: List Of Make And Models Of Cameras | There are few models which are not ONVIF compliant & obsolete, even the brand itself is not existing anymore, kindly confirm how the support on API or SDK is expected on those cameras? | Bidder to Comply TS. |
|  |  |  | Kindly confirm if any of the camera is not working or down due to network issue, rectification of the same is not under current scope of works. Pls confirm | Preliminary troubleshooting needs to be done by Contractor. Rectification works due to telecom issue is not in Contractor Scope. |
| 228 | Vol. II Part-E Appendix-A Pg. 12 of 14 | LIST OF NVRs TO BE EVALUATED | Please elaborate meaning of "Evaluated" and time duration for the same. | - To asses use of existing NVRs with proposed VMS. - Refer clause 1.8 of Section-I, Part A |
| 229 | Vol. II Part-E | - | VISUAL MONITORING SYSTEM (VMS): General Kindly confirm whether any type of Active, Passive Networking, Poles, Mounting, Power Cabling, Conduiting, rack solution for Visual monitoring system is not under current scope of works. Only servers, workstations, displays, & Software is under current scope of works for VMS | Please refer Vol-II Part-A, Clause-1.6 point(d). |
| 230 | General |  | Please confirm number of PSTN lines & types of PSTN lines to be connected to newly offered VoIP system. | Shall be finalized during Detailed Engineering. PSTN line of Operator desk is Envisaged. |
| 231 | General |  | Please confirm if any Analog sets/phones to be managed by newly offered VoIP system. | Refer above, |
| 232 | General |  | Please confirm if newly offered system should be integrated with any existing communication system. If yes please share make and model of system and expected type of connectivity between two systems. | Bidder to Comply TS. |
| 233 | General |  | Please confirm if PSTN Connectivity is required for VOIP System? Please confirm the Number of PRI / SIP Trunks. | Refer Sr.no 230. |
| 234 | Vol. II, Part A, Section-4 | General | The Defect Liability period of individual control center shall start after its acceptance and shall not be linked with overall project. Please confirm. | Refer clause 1.10.3(h) of Vol-II, Part-A, Section-I & 3.2.2 of Vol-II, Part A, Section-3. |
| 235 | Vol. II, Part A, Section-4 | General | Batteries shall be treated a consumable. Please confirm. | Refer last para of clause 4.13 Vol-II, Part-A, Section-4 |
| 236 | General |  | We understand the material can be stored at PGCIL premises/installation site after dispatch. Please confirm | Refer clause 4.14 Vol-II, Part-A, Section-4 |
| 237 | General |  | Corporate historian functionality & corresponding server is not envisaged in the BOQ. Please confirm. | Refer Amendment No 1 |
| 238 | General |  | NMS servers at ER-RTAMC's are not envisaged in the BOQ. We request to include the same in Price Schedule and BoQ. Please also confirm the total NMS sizing. | Refer Amendment No 1 Bidder to Comply TS for NMS sizing. |
| 239 | General |  | Anti-Virus servers at Main-NTAMC, B-NTAMC and ER-RTAMC's are not envisaged in the BOQ. We request to include the same in Price Schedule and BoQ | Centralized HIDS server envisaged in Main & Backup Control Centres. |
| 240 | General | UPS | Since the Auxiliary Power Supply/UPS systems including Batteries are presently in good condition, we recommend to remove the same from the scope of this project along with its annual AMC to reduce a monopolistic situation. The AMC for same may be directly purchased by PGCIL since there is a high likelihood of exorbitant AMC charges being quoted by incumbent OEM due to monopoly. If this is not possible, then please treat this request as withdrawn. Please confirm accordingly. | Bidder to Comply TS. |
| 241 | General |  | Mostly hardware and network devices are with mixed specification, May be few point can be non-complied or partial complied during detailed engineering. Hence we recommend that the selection of any make n model will be based upon sizing and performance criteria mentioned in the TS and DRS. kindly confirm | Bidder to Comply TS. |
| 242 | General |  | We understand SMS gateway and bulk messaging services are beyond the scope of this project. Please confirm. | Confirmed |
| 243 | General |  | General We request clearance to implement new RAS system inclusive of Data Concentrator/Software based system at the substations along with the servers and UI/workstation required in the present scope of work. | Bidder to Comply TS. |
| 244 | General | General | General As software market upgrades very fast, considering the Cyber security scenario we propose the system should be upgraded to the latest OS, DB, SCADA software and other periphery software. Request PGCIL to include the requirement as this will improve the system security from Cyber security point of view. | Bidder to comply TS |
| 245 | General | No cap on penalty | There is no cap on penalty. We request PGCIL to cap the penalty on quarterly bill to 20% in each category. | Bidder to Comply TS. |
| 246 | 02 Price Schedule NTAMC Sch-1 | Price Schedule Sch1, Line item 3,4, 5 & 6 and corresponding TS reference: "*In general, number of SFP/SFP+ for fiber optic and Cu Ethernet type has been given in the BOQ for indicative purpose. Number of SFP/SFP+ shall be finalized during detailed Engineering. The minimum hardware configuration of shall be as per appendix-P of Part-B" | We understand, 1. 1G CU network is specified in the server and workstation DRS for Client RTAMCs but SFP base ports are mentioned in the switches specification. There is no requirement to have 1G/10G fibre switches with 1G SFP+ for client RTAMCs as network is 1G copper only, request you to update the specification. Please confirm. | Bidder to Comply TS. |
| 247 | 02 Price Schedule NTAMC Sch-1 S.No.37 to S.No.40 | Price schedule | Kindly confirm how many monitors belongs to VMS. Which type of monitors are envisaged for VMS out of three types. Kindly confirm whether workstation shall be connected to 2 displays or 1? | Type-1 & Type-2 Monitors are envisaged for VMS system along with 1(Single) display. |
| 248 | 02 Price Schedule NTAMC Sch-1 S.No.127 to S.No.130 | Price schedule | Kindly confirm how many workstations belongs to VMS out of 26 in B-NTAMC? | Qty of Workstations shall be equal to no.of Type-1 & Type-2 TFTs mentioned in Price Schedule. |
| 249 | 02 Price Schedule NTAMC Sch-1 S.No.127 to S.No.130 | Price schedule | Kindly confirm how many monitors belongs to VMS. Which type of monitors are envisaged for VMS out of three types. Kindly confirm whether workstation shall be connected to 2 displays or 1? | Type-1 & Type-2 Monitors are envisaged for VMS system along with 1(Single) display. |
| 250 | 02 Price Schedule NTAMC Sch-1 S.No.37 to S.No.40 | Price schedule | Kindly confirm how many workstations belongs to VMS out of 52? | Type-1 & Type-2 Monitors are envisaged for VMS system along with 1(Single) display. Workstation quantity shall be in line with Type-1 & Type-2 TFTs requirement. |
| 251 | Price Schedule |  | Please share the line item for Mandatory spares in the Price Schedule along with a control center wise BoQ. | Bidder to Comply TS |
| 252 | Price Schedule | Power & Communication cables | Please specify the exact quantity and detailed specifications of cables so that all bidders are at par. | Refer Clause 1.8 in Vol-II, Part-A, Section-1. |
| 253 | General | Hardware | All required Hardware i:e NVR,Switches,routers etc is in MSI scope | Bidder to Comply TS |
| 254 | General | NMS | Please clarify NMS architecture and Nodes count. We understand that substation devices are excluded from NMS purview and node count for NMS are considered for Control Center only. Please confirm. | Refer 2nd para of Clause 1.10 (NMS Operational Philosophy) in Vol II, Part-B, Section-1 (pg. 11 of 11) & Clause 4.4 (c) of Section-4, Part-B. |
| 255 | Vol. II Part A Clause 1.6(t) of Sec-1 Pg. 14 of 32 | 1.6 Scope of Work t) Development of complete database including the power system database | We understand that power system database means SCADA database only as EMS applications are not envisaged in the project scope. Kindly confirm | Bidder to Comply TS |
| 256 | Vol. II Part A Clause 1.9 of Sec-1 Pg. 24 of 32 | 1.9. Development System during migration at contractor works: "The substation level activity will be done by Employer during Point to point validation testing of SCADA signals. The contractor to ensure support from control center end only." | We understand that this sentence related to point to point testing is for information and actual point to point testing can be done at employer's location not on development system at contractor works Kindly confirm | Bidder to Comply TS |
| 257 | Vol. II Part A Clause 1.10.3(b) of Sec-1 Pg. 26 of 32 | 1.10.3 Availability of spares and service support for the system: (b) The contractor shall ensure the availability of all spare parts, beside the mandatory spares | Spare inventory and mandatory spare inventory are the same thing or Contractor has to maintain separate spare inventory apart from mandatory spare? | Bidder to Comply TS |
| 258 | Vol. II Part A Clause 4.14 of Sec-4 Pg. 14 of 25 | 4.14. Spares inventory The Contractor shall maintain an inventory of spares at his own cost to meet the spare availability requirements of the system. | If not ,what does "contractor shall ensure " means here? | Bidder to Comply TS |
| 259 | Vol. II Part A Clause 1.10.3(h) of Sec-1 Pg. 27 of 32 | 1.10.3 Availability of spares and service support for the system (h)-Irrespective to of commissioning of system in progressive manner, entire the Defect Liability Period (DLP)…. | We understand that contractor libality to ensure uninterrupted service & functional requirement of delivered system shall strat only after DLP starts Kindly confirm | Bidder to Comply TS |
| 260 | Vol. II Part A Clause 2.2 of Sec-2 Pg. 12 of 12 | 2.2. Testing and Certification Table 2.1 Training Requirements | No. of trainees to be considered in single batch ? If not ,kindly specify max no. of batches | Bidder to Comply TS |
| 261 | Vol. II Part A Clause 2.2 of Sec-2 Pg. 12 of 12 | Table 2.1 Training Requirements *Training also needs to be provided during AMC period in each year as per table given above. | Apart from execution phase , training also need to be considered for 6 years of AMC or 7 years including DLP? We request 7 or 8 sets ( depending on DLP year) may be reduced to total 4 sets as one during execution and 3 during 7 years of DLP & AMC | Bidder to Comply TS |
| 262 | Vol. II Part A Clause 4.2 of Sec-4 Pg. 5 of 25 | 4.2. Support in case of End of Life or End of Support | Kindly review EOL & EOS which is earlier clause, this clause may satisfy sooner but support may continue | Refer Sr.no 17. |
| 263 | Vol. II Part B Clause 2.1.1(ii) of Sec-4 Pg. 6 of 52 | ii) The following functions are classified as Non-Critical functions: | OTS & PDS environment are mentioned as non-critical and usually not supported by redundancy however in BOQ there are 2 quality of each in both Main and Backup NTAMC Could you pls clarify the requirement ? | Bidder to Comply TS |
| 264 | Vol. II Part B Clause 2.3.1 of Sec-2 Pg. 33 of 52 | 2.3.1 Configuration of the data historian at Main and Backup NTAMC | We understand that historian will receive data from Main NTAMC, Backup NTAMCs (Main and Backup NTAMC has data for all RTAMC) .Why the individual connections are shown directly from Substations & RTAMCs? Could you please clarify the same? | RTAMC users Shall use the Data Historian at Main & Back up NTAMC. Substations users shall use the Corporate Data Historian. Refer Amendment-1 for Corporate Historian. |
| 265 | Vol. II Part B Clause 2.4.1(a) of Sec-2 Pg. 39 of 52 | 2.4.1 NTAMC SCADA Operator Training Simulator a) Dedicated hardware & software setup | Could you pls clarify what additional hardware’s envisaged beyond the scope of BOQ/Servers ? | Bidder to Comply TS |
| 266 | Vol. II Part B Clause 3.6.2 of Sec-3 Pg. 16 of 28 | 3.6.2 Alarm Priority levels Each alarm shall be assigned to an alarm priority level. Up to 8 alarm priority levels shall be supported | Request you pls update/confirm alarm priority as 8 at both the places | Refer Sr.no 44 |
| 267 | Vol. II Part B Appendix-C Pg. 7 of 8 | TABLE 3 - DESIGN PARAMETERS FOR USER INTERFACE Alarm priority levels=10 | Request you pls update/confirm alarm priority as 8 at both the places | Refer Sr.no 44 |
| 268 | Vol. II Part B Clause 5.2.1 of Sec-5 Pg. 6 of 41 | 5.2.1Servers/Processors Bidder can shall offer blade servers…... In general, blade server will be preferred at main and backup NTAMC to cater most….... | We understand that blade servers are optional and bidder may propose rack servers for Man and Backup NTAMC Kindly confirm | Refer Amendment-1 |
| 269 | Vol. II Part B Clause 5.2.1 of Sec-5 Pg. 6 of 41 | 5.2.1 Servers/Processors Bidder can shall offer blade servers…... In general, blade server will be preferred at main and backup NTAMC to cater most….... | In case bidder offer rack servers ,specifications related to blade servers mentioned in this section shall not be applicable to bidder's offered servers Kindly confirm | Refer Amendment-1 |
| 270 | Vol. II Part B Clause 5.2.1 of Sec-5 Pg. 6 of 41 | 5.2.1 Servers/Processors Bidder can shall offer blade servers…... In general, blade server will be preferred at main and backup NTAMC to cater most….... | In case bidder offer rack servers ,specifications mentioned in Appendix-P, Vol.II Part-B shall be applicable Kindly confirm | Refer Amendment-1 |
| 271 | Vol. II Part B Appendix-D Pg. 3 of 7 | (b)UTILISATION AUXILIARY MEMORY Access & Transfer capacity | Could you pls clarify how to establish Access & Transfer capacity of auxaliry memory in terms of percentage? | Bidder to Comply TS |
| 272 | Vol. II Part A Clause 16 of Sec-1 Pg. 13 of 32 | g) Establishment of 01 new ER-RTAMC at NR-3. h) Establishment of CR-RTAMCs | Could you please clarify the establishment of ER & CR RTAMC include civil work also.? | Bidder to Comply TS |
| 273 | Vol. II Part-A Clause 3.7.8 of Sec-3 Pg. 17 of 18 | Training Documentation: The schedule for submission/approval of documents shall be in line with the overall project schedule. Completion schedule of the project is 15 months from the date of agreement. | We understand that 15 months is not sufficient time for project completion. Request you to increase the project duration from 15 months to 24 months. | Bidder to Comply TS |
| 274 | General | FAT of Network devices | Please note that as per feedback received from major OEMs, due to the semiconductor supply chain issue currently the networking component (Switch, Router etc.) delivey timelines are experiencing substantial delays. We request PGCIL confirmation, that if any hardware delivery lead times are impacted, then bidder should be allowed to demonstrate its functionality during FAT/staging with an equivalent/similar hardware and FAT may be approved without the said HW, while the actual approved device may be directly supplied to site to meet overall project timelines. In any case, its testing would be covered in SAT. Please confirm. | Bidder to comply T.S. |
| 275 | General | - | We understand that node calculation for Backup software covers only Control Center Servers. Substation devices are excluded from purview of backup software. Please confirm. Further, please clarify if each CC has their own Backup server for their respective devices. | - Refer 4th para of Clause 5.2.2 (Archive & Configuration Server) in Vol II, Part-B, Section-5 (pg. 10 of 41 ). - Refer Clause 5.2.2 for 2nd query. |
| 276 | Vol. II Part-E Clause 3.7 Pg. 8 of 28 | 3.7.Technical Requirements / Specifications Minimal technical specifications of the VMS Application are provided here, the contractor has to ensure a fully functional system. All necessary interfaces and accessories required to complete the system functions shall be supplied | If any server hardware required in addition to mentioned in RFP BOQ for fully functional system for VMS solution than the said server hardware will be supplied as per VMS OEM recommendation and corresponding certification will be provided from VMS OEM. Hope our understanding is correct! | Bidder to comply T.S. |
| 277 | Vol. II Part-A Clause 1.9 of Sec-1 Pg 24 of 32 | 1.9. Development System during migration at contractor works A development system shall be provided by the contractor for building of databases, displays and reports for NTAMC systems (SCADA, RAS, AFAS, VMS, VoIP, VPS, Data Historian, NMS and Cybersecurity system etc.) which shall be reviewed by Employer/Owner. This development system shall not be part of the delivery. | We understand that development system will not be part of delivery and will be retained at contractor's place during project tenure till end of AMC period. Please confirm our understanding. | Development system during migration at Contractor Works is not part of deliver. However, Bidder shall supply Development System as per BOQ. |
| 278 | Vol. II Part-B Clause 3.9 of Sec-3 Pg. 21 of 28 | 3.9. Dynamic Data Presentation (h) Select indicator- The select indicator shall be an optional graphic symbol, which will be used to indicate conditions associated with a dynamic field on a display. The select indicator shall identify the ‘point selected’, ‘control –in –progress’, and function/process active notes. | Please elaborate the requirements in terms of functionality expected with the use case. | “Select Indicator” shall provide a warning message incase of equipment is already selected by other user. |
| 279 | Vol. II Part-B Appendix-G Pg. 2 of 16 | BOQ FOR SUPPLY FOR UPGRADATION OF NTAMC SYSTEM STORAGE SERVER SAN | Please provide capacity of SAN storage which will be mandatory to all bidders. | Refer Vol-II Part-B, Appendix-P Pg 26 of 27. |
| 280 | Vol. II Part-A Clause 4.7 Sec-4 Pg 70 of 102 | 4.7. Call Tracking System | Please include call tracking tool in BoQ. | Bidder to Comply TS. |
| 281 | Vol. II Part-B Clause 7.7 of Sec-7 Pg 9 of 15 | 7.7. Factory Test Requirements | Considering project delivery timeline, we request you to conduct sample testing on Main, Backup and One Regional CC during FAT and rest of RTAMC can tested during SAT. | Bidder to Comply TS. |
| 282 | Vol.II Part-A Clause 4.5 of Sec-4 Pg 7 of 25 | b) BYOD Policy The contractor shall provide the tool (e.g. degaussing) to clear all the data and configurations for the defective equipment | Please include degaussing tool in BoQ | Bidder to Comply TS. |
| 283 | Vol.II Part-B Clause 2.3.2 of Sec-2 Page 34 of 52 | 2.3.2 Features required with the Data Historian c) Real-time data interfaces The data historian shall provide real-time, fault-tolerant, high-speed links from any industrial automated real-time data sources through interfaces such as multiple OPC industry standards, OPC DA, OPC UA and OPC HDA, connector. Also, it shall have interfaces compatible with DAS (1.0a and 2.0) compliant servers, SQL, ODBC, OLEDB, Modbus, ASCII, and text. | We understand that OPC UA/HDA connector is required at ISR or Historian system to exchange real time and historical data respectively. In addition, other interface compatibility like ODBC is also required at ISR / Historian system. In that please confirm if instead of OPC HDA connector, historical data over ODBC is accepted? | OPC HDA is preferable. |
| 284 | Vol. II Part-B Appendix-B Page 4 of 23 | B-5 Switching Reports Circuit breaker switching details including no. of operations, current interrupted in the present operations, cumulative no. of operations, cumulative current interrupted, the reason for trip operations i.e. testing, manual, protection (some values are to be entered manually). These shall be available per shift and on daily basis. These reports will be retained online for 60 months. | Please elaborate the requirements for switching reports and how current interrupted in present operations and cumulative current interrupted expected to be calculated. | Current interruption information shall be obtained from RAS/AFAS System. |
| 285 | Vol. II Part-E Clause 4.1.10 Page 24 of 28 | 4.1.10 Smoke and Fire Detection: 4.1.10 Smoke and Fire Detection: | 1. We would like to inform that - Smoke Detection & PPE Analytics are high compute analytics and shall require separate high compute servers. however other use cases of Analytics can still be there as a part RFP. We request you to consider the other use case analytics on edge (camera) rather than on server. the tender should have provision that all Camera models (installed) which supports these analytics on edge & relevant ONVIF profile shall be configured in VMS. Rest of the analytics shall not be required if camera doesn't support the same on edge. 2. If (PGCIL) would like to have rest of the use cases of Analytics as server based analytics then we request PGCIL to include one more server machine per substation, also to provide qty of analytics license per type of Analytics required. | Refer Amendment-1 |
| 286 | Vol. II Part-E Clause 4.1.11 Page 24 of 28 | 4.1.11 Personal protective equipment (PPE) Violation Detector 4.1.11 Personal protective equipment (PPE) Violation Detector |  | Refer Amendment-1 |
| 287 | Vol. II Part-E Clause 6.2 Page 27 of 28 | b) UTILISATION b) UTILISATION | We understand from tender that PGCIL require 30% utilization post loading 50 cameras per server which is not applicable for IT equipment's like these. This memory/ processor utilization criteria will increase the no of cores, ram, memory by 3 times. We request PGCIL to either increase the compute or stress on 30% utilization clause in server specifications itself so that no bidder shall make mistake while quoting as this would lead to doubling up server NVR cost. | Refer Amendment-1 |
| 288 | Vol. II Part-E Clause 4.1.7 Page 23 of 28 | 4.1.7 PTZ Tracking 4.1.7 PTZ Tracking | On PTZ camera Since it keeps rotating, the analytics can only work on pre-set position apart from PTZ tracking analytics. Please confirm | Bidder to Comply TS. |
| 289 | Price Schedule | Price Schedule Price Schedule | We understand that at site the client PC's -900 Nos and the NVRs - 300 are one to one replacement of existing hardware. We envisages that no power cabling and networking cabling scope is required at site and existing will be used. Incase power cabling and network cabling is to be done then please provide a tentative quantity. So that variation in quantity is acceptable during execution. | New Cables to be used. Bidder to Comply TS. |
| 290 | Vol.II Part-A Clause 3.7.8 of Sect-3 Page 17 of 18 | Completion schedule of the project is 15 months from the date of agreement. | The project is site intensive (13 Control centres + 300 Substations) and huge volume of hardware needs to be procured, installed, tested, inspected, dispatched and commissioned. It would be very challenging. We proposed that critical milestones be defined to be met in 15 months whereas the overall project can be allowed to be delivered in 24 months without an Liquidated damages being imposed on the suppliers. We request your concurrence. | Bidder to Comply TS. |
| 291 | Vol-I 06-Sec-V 3/19 | 5. Replacing Sub-Clause GCC 3.3 b) The contractor shall ensure the availability of all spare parts, beside the mandatory spares, required for the operation and maintenance of the facilities and service support for all items supplied by the Contractor for a period of 7 years from Operational Acceptance by the Employer. | From the date of PO we envisaged that we need to consider 8.5 years of support would be mandatorily required to meet the project execution + AMC schedule. Based on experience another 2 years of AMC extension maybe desired. Considering this we need to consider 10 years of support from major OEMs of server, workstation, switches, firewall, etc. OEMs are not willing to commit for 10 years duration product support and spare support. Request you to kindly amend the clause from (10) years from the end of Defect Liability Period to (5) years from the end of Defect Liability Period | Bidder to Comply TS. |
| 292 | Vol.II Part-A Clause 4.12 of Sec-4 Page 12 of 25 | Clause 4.12. Video Projection system / Video Wall says Any dead pixel or LED module defect observed shall be considered under severity level 1. | One module of VPS failure won’t hamper the system by any means. Please classify the issue as Severity level 3 | Refer Amendment-1 |
|  |  |  | Since VPS maintenance and module replacement requires expertise of OEM, we request you to remove Dead Pixel criteria from Severity Level 1 to Severity Level 3 |  |
| 293 | Vol.II Part-B Appendix-P Clause-1, Sr.no-16 in Table, Pg. 1 of 27. | Server Specification | Please clarify which server shall host FC card, and clarify SAN switch port & quantity. | FC card is envisaged for Connecting Servers to SAN Switches for Archival & Back up. |
| 294 | Appendix-G (BoQ) /Price Schedule | UPS | Please clarify the UPS sizing requirement for CR/ER RTAMC. | Refer Amendment-1 |
| 295 | General | The security management system for supervising and configuring the firewalls and IPS/IDS shall be connected to these components through a dedicated security management network, which shall be a separate non-routed screened subnet. | Request to kindly provide the rough architecture diagram | Refer Vol-II, Part-B Appendix-K. |
| 296 | Vol.II Part-E Pg 6 of 28 | Block diagram in reference clause and also Figure 2/3 National Transmission Asset Management Centre (NTAMC)/ Back-up NTAMC VISUAL MONITORING SYSTEM (VMS) shows VMS/ACS system. | We understand that these are 2 separate systems/servers, etc. and integration of these 2-system are not in our Scope. | Confirmed. |
| 297 | Vol.II Part-E | VMS means Video Management system which integrates all the cameras and shows videowalls | Will VMS system be at substation level ? | VMS meant for Visual Monitoring System. Integration of existing cameras at Substation with VMS system is in present scope. Supply of NVR is also under present scope. |
| 298 | Vol.II Part-A Clause-1.6, Pg 18 of 32. | All IT products procured /supplied shall have a valid Certificate of Common Criteria as per ISO/IEC 15408 issued by signatories of the Common Criteria Recognition Agreement (CCRA). Acceptance of such tests shall be in line with directions of MoP and MeitY. | This certification is not followed by IT products suppliers and has not confirmed for the same. This needs to be discussed. | Bidder to Comply TS. |