| S N | Clause | Provision of Bidding Documents | Bidder’s Query | POWERGRID's Reply |
| --- | --- | --- | --- | --- |
| A | TS (Volume-II) |  |  |  |
| 1 | Vol. II Part-A Clause 1.10.3(d) of Sec-1Pg. 27 of 32 & Vol. II Part-A Clause 4.2 of Sec-4 Pg. 5 of 25 | The contractor has to ensure with OEM for maintenance and services support for the hardware and software delivered under this project till the completion of AMC period. In case, any hardware / software / equipment /component items of the systems supplied under the contract shall reach its End-of-Life (EOL) or End-of-Support (EOS) whichever is earlier, the contractor shall replace such item with new Hardware or Software without any financial implication to employer. The contractor shall have to submit the documentary evidence certified by OEM for the validity of End-of Life/End-of-Support along with quarterly invoice. & Support in case of End of Life or End of Support | All OEMs have a product refresh cycle of up to a year now and new products are introduced on ongoing basis to keep up with changing technology landscape. While we appreciate PGCIL's intent, this criteria is strenuous and complicating considering the mix of technologies and vendors required at NTAMC. Considering the above, we request to delete this clause as we may not be in position to bid if this remains. As an alternate we suggest following: Earlier Clarification: The Contractor shall replace the EOL and EOS Hardware / software if it has become either non-functional or the patches/updates have been discontinued from the OEM. Bidder’s Query dtd 16.03.23: This is not supported by any OEM and hence request to Omit the clause OR Otherwise employer should explicitly ask for mandatory hardware/software replacement within AMC phase & extended AMC and include in BOM for fair estimation and evaluation by all bidders. | Bidder to Comply TS. |
| 2 | Vol.II Part-B Section-5, Clause- 5.2.6 | 5.2.6 Security Information and Event Management (SIEM) 1. The SIEM solution shall be capable of performing correlation on the events with more than 6000 EPS events per second (sustainable). The contractor shall provide flexibility to increase the EPS in case of any further extension in sources or types of logs required for enhancing cyber security and 2.The SIEM shall support multi-device, multi event and multi-site correlation across the system (including Control Centre and substations). | 1. SIEM Event Sizing as per TS is 6000 EPS(sustained) which corresponds with Control center devices, however TS mentions "contractor shall provide flexibility to increase the EPS in case of any further extension in sources or types of log." This is an open ended statement. We request PGCIL to limit the number of EPS to be considered with the SIEM solution. 2. This statement should be deleted and devices should be restricted to Control Center only or else PGCIL to clearly specify the device types and count of each device for clarity of all bidders since in this case EPS count shall be much higher than 6000EPS. | Bidder to Comply TS. |
| 3 | Vol.II Part-B Section-5, Clause- 5.2.3.1 & Appendix-P | Firewall DRS 3. Common features in Control Centre Firewalls (Internal / External: Type-I, Type-II and Type-III) DNS attack prevention features- DNS sinkholing / DNS filtering against malware / redirect to block portal/ Malware DNS Trap & DNS guard/ Reputation domain protection feature etc. | DNS Filtering feature has been asked as common feature on all types of firewalls whereas as per our understanding it should be provisioned only on those firewalls which are directly terminated with Internet Links/Connectivity to optimize the overall budget Kindly confirm DNS rating filtering is required on which type of firewall? | Bidder to Comply TS. |
| 4 | Vol.II Part-B Section-5, Clause- 5.2.3.2 & Appendix-P | Additional features in Control Centre Firewalls (Internal / External: Type-I, Type-II and Type-III) Sandboxing (on premises, no public cloud), URL filtering and behavior analysis to detect and deal with threats such as malware, ransomware and SQL injection | URL Filtering feature has been asked as additional feature on all types of firewalls whereas as per our understanding it should be provisioned only on those firewalls which are directly terminated with Internet Links/Connectivity. Kindly confirm. | Bidder to Comply TS. |
| 5 | Vol. II Part-B 5.2.6 of Sec-5 & Appendix-P Vol. II Part-B | 5.2.6 Security Information and Event Management (SIEM) SIEM shall be integrated with SOAR or another SOC in future and provision of bidirectional message exchange in SYSLOG, CEF and LEEF format shall be provided along with the supplied SIEM system. Necessary support for integration shall be provided by Contractor. | The formats asked in this clause include syslog, CEF and LEEF. Syslog and CEF are mostly commonly used open standard formats whereas LEEF was originally developed by a specific OEM as a proprietary log format and was released to the public at later stage. Currently, LEEF is not supported by all SIEM/SOAR OEMs and hence restricting healthy participation. Integration is supported on syslog and CEF by all leading OEMs. Hence, request you to amend the clause as follows - SIEM shall be integrated with SOAR or another SOC in future and provision of bidirectional message exchange in SYSLOG, CEF/LEEF format shall be provided along with the supplied SIEM system | SIEM shall support SYSLOG, CEF format for bidirectional message exchange. LEEF format is optional. |
| 6 | Vol. II Part-A 4.5 of Sec-4 | 4.5. Hours of Cover and Manpower -One SCADA software engineer round the clock shall always be available at the Main Control centre i.e. 24 X7 hours for all days. -One cybersecurity engineer round the clock shall always be available at the Main Control centre i.e. 24 X7 hours for all days. He shall also be able to handle the networking and hardware maintenance -One SCADA software/hardware engineer shall be available at each Regional Control centre i.e. 8 office hours (Monday to Saturday) -One engineer of RAS/AFAS shall always be available at Main Control centre i.e. 8 office hours (Monday to Saturday) -One engineer of VMS shall always be available at Main Control centre i.e. 8 office hours (Monday to Saturday). | Clarification-1: Replace with 4.5. Hours of Cover and Manpower • One SCADA software engineer round the clock shall always be available at the Main Control centre i.e. 24 X7 hours for all days .• One cybersecurity engineer round the clock shall always be available at the Main Control centre i.e. 24 X7 hours for all days. He shall also be able to handle the networking and hardware maintenance. • One SCADA software/hardware engineer shall be available Regional Control centre (Back up NTAMC & ER-RTAMC) i.e. 8 office hours (Monday to Saturday). • One engineer of RAS/AFAS shall always be available at Main Control centre i.e. 8 office hours (Monday to Saturday). • One engineer of VMS shall always be available at Main Control centre i.e. 8 office hours (Monday to Saturday) .• One cybersecurity engineer shall always be available at Back up Control Centre i.e. 8 office hours (Monday to Saturday). The Cybersecurity engineer shall also be able to handle the networking and hardware maintenance. Bidder’s Query dtd 16.03.23: As per TS & Amendment, 1 full time resource is required from Monday to Saturday for 8 hours for AFAS, but to meet the SLA requirements, 8-hour shift (Mon-Sat) may not be sufficient, so kindly allow relaxed SLA terms to accommodate the shift timing of deployed resource for RAS/AFAS. Further, this associated SLA for RAS/AFAS shall not be applicable for Backup control center since RAS/AFAS manpower deployment is not envisaged. | Bidder to Comply TS. |
| 7 | General |  | At Gajshield, we are one of reputed “Make in India” OEM for Manufacturing of Next Generation Firewall having presence in this business from last 20+ years taking pride of India to global countries. Our innovative technology and solution offering have been recognised and accepted across globe for its uniqueness, solution performance and after sales support. Recognized in Gartner’s 2018 & 19 Asia/Pacific Context: ‘Magic Quadrant for Enterprise Network Firewalls’ & GajShield is also a global group ISO 9001 certified company (ISO 27001:2013 and ISO 9001:2015) to have met all the ISO standards required for the certification. We are very keen to participate in this tender as we have multiple past successful engagement with PGCIL in various projects. The Government of India is encouraging Indian OEMs to manufacture robust products through Make in India campaign. As per Public Procurement Order by Meity, preference must be given to Make in India Cyber Security Products. ICSA Lab Certification as well as EAL certification both provides assurance of the IT product by thorough security testing. ICSA Lab is well known for testing of networking products specially security products. We would like to bring to your attentions that GajShield has already provided 50+ Next Generation Firewall appliances for the various projects of PGCIL itself. We would like you to consider Indian OEM GajShield as key participants in this project. We would be glad if ICSA Lab Certificate is also considered as an option to common criteria or EAL certificate with necessary arrangements in the tender. We would appreciate, if you consider our sincere request to be part of PGCIL Project once again. | Bidder to Comply TS. |
| B | Commercial (Volume-I) |  |  |  |
| 8. | Annexure-B to BDS | e-Reverse Auction | Due to the fact that this is not a typical commodity package and involves cutting edge technologies requiring significant expertise, we request that PGCIL omit reverse auctions from its proposal. | Provisions of Bidding Documents shall remain unaltered. |